## Summary
Steam Network — Live Summary
Total Generation (t/h) |  | Total Consumption (t/h) |  | Total Vents (t/h) |  | Net Balance (t/h) |  | Turbine Power (kW)
947.5 |  | 469 |  | 0 |  | 478.5 |  | 24943
Per-Header Balance
Header | Rank | P (bar) | Inflow (t/h) | Outflow (t/h) | Imbalance (t/h) | Status | Mixed h (kJ/kg) | Energy In (kW) | Energy Out (kW) | Energy Δ (kW)
VHP | 1 | 110 | 560 | 250 | 310 | SURPLUS | 3388.9 | 527160 | 235339.3 | 291820.7
HP | 2 | 42 | 396 | 276 | 120 | SURPLUS | 3194.1 | 351348.3 | 246166.3 | 105182
MP | 3 | 16 | 170 | 194 | -24 | DEFICIT | 3005.7 | 141936.3 | 161138.8 | -19202.5
LP | 4 | 4.5 | 119 | 90.5 | 28.5 | SURPLUS | 2813.3 | 92995 | 70780.3 | 22214.6
LLP | 5 | 1.4 | 34.5 | 40.5 | -6 | DEFICIT | 2690.9 | 25787.5 | 30397.5 | -4610
BFW | 9 | 8 | 34.5 | 0 | 34.5 | SURPLUS | 440.7 | 4223.5 | 0 | 4223.5
CONDENSATE | 10 | 3 | 174.8 | 0 | 174.8 | SURPLUS | 333.4 | 16187.1 | 0 | 16187.1

## Inputs - Headers
Edit values below; save the file to refresh outputs.
name | pressure_bar | temperature_c | rank | enthalpy_kj_kg | description
VHP | 110 | 510 | 1 |  | Very-high-pressure superheated steam
HP | 42 | 400 | 2 |  | High-pressure header
MP | 16 | 280 | 3 |  | Medium-pressure header
LP | 4.5 | 180 | 4 |  | Low-pressure header
LLP | 1.4 | 115 | 5 |  | Very-low-pressure / utility steam header
BFW | 8 | 110 | 9 |  | Boiler feed-water rail (water side; no steam decision vars)
CONDENSATE | 3 | 90 | 10 |  | Condensate return rail

## Inputs - Elements
Edit values below; save the file to refresh outputs.
name | kind | enabled | header | source_header | from_header | to_header | inlet_header | outlet_header | extraction_header | return_header | dsh_water_header | flow_tph | inlet_flow_tph | extraction_flow_tph | dsh_water_tph | pressure_bar | temperature_c | enthalpy_kj_kg | isentropic_efficiency | mechanical_efficiency | return_fraction | return_temperature_c | dsh_water_temperature_c | max_flow_tph | fuel_input_kw | subtype | condenser_pressure_bar | condensate_return_header
VHP_FuelFired_Boiler_1 | generator | TRUE | VHP | [8 empty] | 178 | [13 empty] | fuel_fired_boiler
VHP_FuelFired_Boiler_2 | generator | TRUE | VHP | [8 empty] | 158 | [13 empty] | fuel_fired_boiler
VHP_HRSG | generator | TRUE | VHP | [8 empty] | 118 | [13 empty] | heat_recovery_steam_generator
VHP_WasteHeat_Boiler | generator | TRUE | VHP | [8 empty] | 68 | [13 empty] | waste_heat_boiler
VHP_Reactor_SteamDrum | generator | TRUE | VHP | [8 empty] | 38 | [13 empty] | reactor_steam_drum
HP_FuelFired_Boiler | generator | TRUE | HP | [8 empty] | 78 | [13 empty] | fuel_fired_boiler
HP_HRSG | generator | TRUE | HP | [8 empty] | 89 | [13 empty] | heat_recovery_steam_generator
HP_WasteHeat_Boiler | generator | TRUE | HP | [8 empty] | 49 | [13 empty] | waste_heat_boiler
HP_Reactor_SteamDrum | generator | TRUE | HP | [8 empty] | 30 | [13 empty] | reactor_steam_drum
MP_FuelFired_Boiler | generator | TRUE | MP | [8 empty] | 38 | [13 empty] | fuel_fired_boiler
MP_HRSG | generator | TRUE | MP | [8 empty] | 29 | [13 empty] | heat_recovery_steam_generator
MP_WasteHeat_Boiler | generator | TRUE | MP | [8 empty] | 25 | [13 empty] | waste_heat_boiler
LP_FuelFired_Boiler | generator | TRUE | LP | [8 empty] | 19 | [13 empty] | fuel_fired_boiler
LP_HRSG | generator | TRUE | LP | [8 empty] | 15 | [13 empty] | heat_recovery_steam_generator
LP_WasteHeat_Boiler | generator | TRUE | LP | [8 empty] | 10 | [13 empty] | waste_heat_boiler
CBD_Flash_Drum | generator | TRUE | LLP | [8 empty] | 5.5 | [13 empty] | cbd_flash_drum
HP_Cooler | consumer | TRUE |  | HP | [7 empty] | 35 | [8 empty] | 0 | 90 |  |  |  | cooler
HP_Heater | consumer | TRUE |  | HP | [5 empty] | CONDENSATE |  | 50 | [8 empty] | 0.7 | 95 |  |  |  | heater
HP_Reactor_Heating | consumer | TRUE |  | HP | [7 empty] | 72 | [8 empty] | 0 | 90 |  |  |  | process_heater
HP_Process_Tracing | consumer | TRUE |  | HP | [7 empty] | 24 | [8 empty] | 0 | 90 |  |  |  | tracing_system
MP_Cooler | consumer | TRUE |  | MP | [7 empty] | 20 | [8 empty] | 0 | 90 |  |  |  | cooler
MP_Heater | consumer | TRUE |  | MP | [5 empty] | CONDENSATE |  | 30 | [8 empty] | 0.7 | 90 |  |  |  | heater
MP_Stripper_Reboiler | consumer | TRUE |  | MP | [5 empty] | CONDENSATE |  | 82 | [8 empty] | 0.6 | 95 |  |  |  | reboiler
MP_Saturator | consumer | TRUE |  | MP | [7 empty] | 15 | [8 empty] | 0 | 90 |  |  |  | saturator
MP_Decoke_Steam | consumer | FALSE |  | MP | [7 empty] | 18 | [8 empty] | 0 | 90 |  |  |  | decoke_steam
MP_Evaporator_Effect_1 | consumer | TRUE |  | MP | [7 empty] | 22 | [8 empty] | 0 | 90 |  |  |  | evaporator_effect
LP_Cooler | consumer | TRUE |  | LP | [7 empty] | 12 | [8 empty] | 0 | 90 |  |  |  | cooler
LP_Heater | consumer | TRUE |  | LP | [5 empty] | CONDENSATE |  | 18 | [8 empty] | 0.7 | 90 |  |  |  | heater
LP_Evaporator_Effect_2 | consumer | TRUE |  | LP | [7 empty] | 14 | [8 empty] | 0 | 90 |  |  |  | evaporator_effect
LP_Deaerator | consumer | TRUE |  | LP | [5 empty] | BFW |  | 34.5 | [8 empty] | 1 | 105 |  |  |  | deaerator
LLP_Process_Heater | consumer | TRUE |  | LLP | [7 empty] | 12.5 | [8 empty] | 0 | 90 |  |  |  | process_heater
LLP_Reboiler | consumer | TRUE |  | LLP | [5 empty] | CONDENSATE |  | 14 | [8 empty] | 0.5 | 90 |  |  |  | reboiler
LLP_Tracing_System | consumer | TRUE |  | LLP | [7 empty] | 8 | [8 empty] | 0 | 90 |  |  |  | tracing_system
LLP_Dump_Condenser | consumer | TRUE |  | LLP | [7 empty] | 6 | [8 empty] | 0 | 90 |  |  |  | dump_condenser
VHP_BackPressure_to_HP | turbine | TRUE |  |  |  |  | VHP | HP |  |  |  |  | 120 | 0 |  |  |  |  | 0.78 | 0.98 | [5 empty] | backpressure_turbine
VHP_Extraction_HP_LP | turbine | TRUE |  |  |  |  | VHP | LP | HP |  |  |  | 80 | 30 |  |  |  |  | 0.75 | 0.98 | [5 empty] | extraction_turbine
VHP_Condensing_Turbine | condensingturbine | TRUE |  |  |  |  | VHP | [5 empty] | 50 | [5 empty] | 0.8 | 0.98 | [5 empty] | condensing_turbine | 0.1 | CONDENSATE
HP_BackPressure_to_MP | turbine | TRUE |  |  |  |  | HP | MP |  |  |  |  | 60 | 0 |  |  |  |  | 0.74 | 0.98 | [5 empty] | backpressure_turbine
HP_Extraction_MP_LLP | turbine | TRUE |  |  |  |  | HP | LLP | MP |  |  |  | 35 | 18 |  |  |  |  | 0.72 | 0.98 | [5 empty] | extraction_turbine
MP_BackPressure_to_LP | turbine | TRUE |  |  |  |  | MP | LP |  |  |  |  | 25 | 0 |  |  |  |  | 0.7 | 0.98 | [5 empty] | backpressure_turbine
LP_BackPressure_to_LLP | turbine | TRUE |  |  |  |  | LP | LLP |  |  |  |  | 12 | 0 |  |  |  |  | 0.66 | 0.98 | [5 empty] | backpressure_turbine
VHP_to_HP_PRV | letdown | TRUE |  |  | VHP | HP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
VHP_to_MP_PRV | letdown | TRUE |  |  | VHP | MP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
VHP_to_LP_PRV | letdown | TRUE |  |  | VHP | LP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
VHP_to_LLP_PRV | letdown | TRUE |  |  | VHP | LLP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
HP_to_MP_PRV | letdown | TRUE |  |  | HP | MP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
HP_to_LP_PRV | letdown | TRUE |  |  | HP | LP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
HP_to_LLP_PRV | letdown | TRUE |  |  | HP | LLP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
MP_to_LP_PRV | letdown | TRUE |  |  | MP | LP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
MP_to_LLP_PRV | letdown | TRUE |  |  | MP | LLP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
LP_to_LLP_PRV | letdown | TRUE |  |  | LP | LLP |  |  |  |  | BFW | 0 |  |  | 0 | [7 empty] | 105 |  |  | letdown
VHP_Steam_Import | import | TRUE | VHP | [8 empty] | 0 | [13 empty] | import
HP_Steam_Import | import | TRUE | HP | [8 empty] | 0 | [13 empty] | import
MP_Steam_Import | import | TRUE | MP | [8 empty] | 0 | [13 empty] | import
LP_Steam_Import | import | TRUE | LP | [8 empty] | 0 | [13 empty] | import
LLP_Steam_Import | import | TRUE | LLP | [8 empty] | 0 | [13 empty] | import
VHP_Steam_Export | export | TRUE | VHP | [8 empty] | 0 | [13 empty] | export
HP_Steam_Export | export | TRUE | HP | [8 empty] | 0 | [13 empty] | export
MP_Steam_Export | export | TRUE | MP | [8 empty] | 0 | [13 empty] | export
LP_Steam_Export | export | TRUE | LP | [8 empty] | 0 | [13 empty] | export
LLP_Steam_Export | export | TRUE | LLP | [8 empty] | 0 | [13 empty] | export
VHP_Vent | vent | TRUE | VHP | [8 empty] | 0 | [11 empty] | 1000000 |  | vent
HP_Vent | vent | TRUE | HP | [8 empty] | 0 | [11 empty] | 1000000 |  | vent
MP_Vent | vent | TRUE | MP | [8 empty] | 0 | [11 empty] | 1000000 |  | vent
LP_Vent | vent | TRUE | LP | [8 empty] | 0 | [11 empty] | 1000000 |  | vent
LLP_Vent | vent | TRUE | LLP | [8 empty] | 0 | [11 empty] | 1000000 |  | vent

## Output - Headers
Header | Rank | P (bar) | Inflow (t/h) | Outflow (t/h) | Imbalance (t/h) | Status | Mixed h (kJ/kg) | Energy In (kW) | Energy Out (kW) | Energy Δ (kW)
VHP | 1 | 110 | 560 | 250 | 310 | SURPLUS | 3388.9 | 527160 | 235339.3 | 291820.7
HP | 2 | 42 | 396 | 276 | 120 | SURPLUS | 3194.1 | 351348.3 | 246166.3 | 105182
MP | 3 | 16 | 170 | 194 | -24 | DEFICIT | 3005.7 | 141936.3 | 161138.8 | -19202.5
LP | 4 | 4.5 | 119 | 90.5 | 28.5 | SURPLUS | 2813.3 | 92995 | 70780.3 | 22214.6
LLP | 5 | 1.4 | 34.5 | 40.5 | -6 | DEFICIT | 2690.9 | 25787.5 | 30397.5 | -4610
BFW | 9 | 8 | 34.5 | 0 | 34.5 | SURPLUS | 440.7 | 4223.5 | 0 | 4223.5
CONDENSATE | 10 | 3 | 174.8 | 0 | 174.8 | SURPLUS | 333.4 | 16187.1 | 0 | 16187.1

## Output - Elements
Name | Kind | Enabled | Primary Flow (t/h) | Inflows | Outflows | Power (kW)
VHP_FuelFired_Boiler_1 | Generator | TRUE | 178 | VHP:178.00@3389
VHP_FuelFired_Boiler_2 | Generator | TRUE | 158 | VHP:158.00@3389
VHP_HRSG | Generator | TRUE | 118 | VHP:118.00@3389
VHP_WasteHeat_Boiler | Generator | TRUE | 68 | VHP:68.00@3389
VHP_Reactor_SteamDrum | Generator | TRUE | 38 | VHP:38.00@3389
HP_FuelFired_Boiler | Generator | TRUE | 78 | HP:78.00@3211
HP_HRSG | Generator | TRUE | 89 | HP:89.00@3211
HP_WasteHeat_Boiler | Generator | TRUE | 49 | HP:49.00@3211
HP_Reactor_SteamDrum | Generator | TRUE | 30 | HP:30.00@3211
MP_FuelFired_Boiler | Generator | TRUE | 38 | MP:38.00@2990
MP_HRSG | Generator | TRUE | 29 | MP:29.00@2990
MP_WasteHeat_Boiler | Generator | TRUE | 25 | MP:25.00@2990
LP_FuelFired_Boiler | Generator | TRUE | 19 | LP:19.00@2816
LP_HRSG | Generator | TRUE | 15 | LP:15.00@2816
LP_WasteHeat_Boiler | Generator | TRUE | 10 | LP:10.00@2816
CBD_Flash_Drum | Generator | TRUE | 5.5 | LLP:5.50@2702
HP_Cooler | Consumer | TRUE | 35 |  | HP:35.00@3211
HP_Heater | Consumer | TRUE | 50 | CONDENSATE:35.00@398 | HP:50.00@3211
HP_Reactor_Heating | Consumer | TRUE | 72 |  | HP:72.00@3211
HP_Process_Tracing | Consumer | TRUE | 24 |  | HP:24.00@3211
MP_Cooler | Consumer | TRUE | 20 |  | MP:20.00@2990
MP_Heater | Consumer | TRUE | 30 | CONDENSATE:21.00@377 | MP:30.00@2990
MP_Stripper_Reboiler | Consumer | TRUE | 82 | CONDENSATE:49.20@398 | MP:82.00@2990
MP_Saturator | Consumer | TRUE | 15 |  | MP:15.00@2990
MP_Decoke_Steam | Consumer | FALSE | 18
MP_Evaporator_Effect_1 | Consumer | TRUE | 22 |  | MP:22.00@2990
LP_Cooler | Consumer | TRUE | 12 |  | LP:12.00@2816
LP_Heater | Consumer | TRUE | 18 | CONDENSATE:12.60@377 | LP:18.00@2816
LP_Evaporator_Effect_2 | Consumer | TRUE | 14 |  | LP:14.00@2816
LP_Deaerator | Consumer | TRUE | 34.5 | BFW:34.50@441 | LP:34.50@2816
LLP_Process_Heater | Consumer | TRUE | 12.5 |  | LLP:12.50@2702
LLP_Reboiler | Consumer | TRUE | 14 | CONDENSATE:7.00@377 | LLP:14.00@2702
LLP_Tracing_System | Consumer | TRUE | 8 |  | LLP:8.00@2702
LLP_Dump_Condenser | Consumer | TRUE | 6 |  | LLP:6.00@2702
VHP_BackPressure_to_HP | Turbine | TRUE | 120 | HP:120.00@3165 | VHP:120.00@3389 | 7319.6
VHP_Extraction_HP_LP | Turbine | TRUE | 80 | LP:50.00@2817, HP:30.00@3173 | VHP:80.00@3389 | 9549.2
VHP_Condensing_Turbine | CondensingTurbine | TRUE | 50 | CONDENSATE:50.00@189 | VHP:50.00@3389 | 14225.8
HP_BackPressure_to_MP | Turbine | TRUE | 60 | MP:60.00@3023 | HP:60.00@3211 | 3071.3
HP_Extraction_MP_LLP | Turbine | TRUE | 35 | LLP:17.00@2698, MP:18.00@3028 | HP:35.00@3211 | 3270.8
MP_BackPressure_to_LP | Turbine | TRUE | 25 | LP:25.00@2803 | MP:25.00@2990 | 1276
LP_BackPressure_to_LLP | Turbine | TRUE | 12 | LLP:12.00@2676 | LP:12.00@2816 | 456.1
VHP_to_HP_PRV | Letdown | TRUE | 0 | HP:0.00@3389 | VHP:0.00@3389
VHP_to_MP_PRV | Letdown | TRUE | 0 | MP:0.00@3389 | VHP:0.00@3389
VHP_to_LP_PRV | Letdown | TRUE | 0 | LP:0.00@3389 | VHP:0.00@3389
VHP_to_LLP_PRV | Letdown | TRUE | 0 | LLP:0.00@3389 | VHP:0.00@3389
HP_to_MP_PRV | Letdown | TRUE | 0 | MP:0.00@3211 | HP:0.00@3211
HP_to_LP_PRV | Letdown | TRUE | 0 | LP:0.00@3211 | HP:0.00@3211
HP_to_LLP_PRV | Letdown | TRUE | 0 | LLP:0.00@3211 | HP:0.00@3211
MP_to_LP_PRV | Letdown | TRUE | 0 | LP:0.00@2990 | MP:0.00@2990
MP_to_LLP_PRV | Letdown | TRUE | 0 | LLP:0.00@2990 | MP:0.00@2990
LP_to_LLP_PRV | Letdown | TRUE | 0 | LLP:0.00@2816 | LP:0.00@2816
VHP_Steam_Import | Import | TRUE | 0 | VHP:0.00@3389
HP_Steam_Import | Import | TRUE | 0 | HP:0.00@3211
MP_Steam_Import | Import | TRUE | 0 | MP:0.00@2990
LP_Steam_Import | Import | TRUE | 0 | LP:0.00@2816
LLP_Steam_Import | Import | TRUE | 0 | LLP:0.00@2702
VHP_Steam_Export | Export | TRUE | 0 |  | VHP:0.00@3389
HP_Steam_Export | Export | TRUE | 0 |  | HP:0.00@3211
MP_Steam_Export | Export | TRUE | 0 |  | MP:0.00@2990
LP_Steam_Export | Export | TRUE | 0 |  | LP:0.00@2816
LLP_Steam_Export | Export | TRUE | 0 |  | LLP:0.00@2702
VHP_Vent | Vent | TRUE | 0
HP_Vent | Vent | TRUE | 0
MP_Vent | Vent | TRUE | 0
LP_Vent | Vent | TRUE | 0
LLP_Vent | Vent | TRUE | 0

## Output - Totals
Metric | Value
Total Generation (t/h) | 947.5
Total Imports (t/h) | 0
Total Consumption (t/h) | 469
Total Exports (t/h) | 0
Total Vents (t/h) | 0
Net Plant Balance (t/h) | 478.5
Total Turbine Power (kW) | 24943

## Output - Optimizer
Element | Kind | Recommended (t/h)
VHP_FuelFired_Boiler_1 | Generator | 178
VHP_FuelFired_Boiler_2 | Generator | 28
VHP_HRSG | Generator | 0
VHP_WasteHeat_Boiler | Generator | 68
VHP_Reactor_SteamDrum | Generator | 0
HP_FuelFired_Boiler | Generator | 78
HP_HRSG | Generator | 0
HP_WasteHeat_Boiler | Generator | 20.5
HP_Reactor_SteamDrum | Generator | 30
MP_FuelFired_Boiler | Generator | 38
MP_HRSG | Generator | 29
MP_WasteHeat_Boiler | Generator | 25
LP_FuelFired_Boiler | Generator | 19
LP_HRSG | Generator | 0
LP_WasteHeat_Boiler | Generator | 0
CBD_Flash_Drum | Generator | 5.5
VHP_to_HP_PRV | Letdown | 0
VHP_to_MP_PRV | Letdown | 24
VHP_to_LP_PRV | Letdown | 0
VHP_to_LLP_PRV | Letdown | 0
HP_to_MP_PRV | Letdown | 0
HP_to_LP_PRV | Letdown | 0
HP_to_LLP_PRV | Letdown | 2.5
MP_to_LP_PRV | Letdown | 0
MP_to_LLP_PRV | Letdown | 0
LP_to_LLP_PRV | Letdown | 3.5
VHP_Vent | Vent | 0
HP_Vent | Vent | 0
MP_Vent | Vent | 0
LP_Vent | Vent | 0
LLP_Vent | Vent | 0