## intantiated_attributes
element_path | element_code | element_name | level | attribute | default_uom | formula | constant_value
| 09296cd9-0970-5623-bb92-e0140a2ea5cb | United | Plant | BOILER_LHV | KCAL/KG |  | 10000
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | AMBIENT_TEMPERATURE | DEGC
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | RELATIVE_HUMIDITY | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | HP_STEAM_PRESSURE | BARG
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | DESUPERHEATER_OUTLET_TEMP | C
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | STEAM_FLOW_RAW | KG/HR
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FLUE_GAS_OXYGEN | MOLE%
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_C1 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_C2 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_C3 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_CO2 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_FLOW | KG/HR
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_IC4 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_IC5 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_N2 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_NC4 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | FUEL_GAS_NC5 | %
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | EXCESS_O2 | MOLE%
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | RATED_STEAM_KGH | KG/HR |  | 150000
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | MIN_LOAD_PCT | % |  | 25
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | STEAM_TEMP_ON_THRESH | C |  | 370
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | STEAM_PRESS_ON_THRESH | BARG |  | 40
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | CO2_KG_PER_GJ | KG/GJ |  | 56.1
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | SEC_OPT_A |  |  | 8e-06
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | SEC_OPT_B |  |  | -0.0017
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | BLR_1 | Boiler | SEC_OPT_C |  |  | 3.0167

## Sensors_Mapping
element_path | element_code | level | attribute | sensor_code | sensor_name | sensor_uom | sip_min | sip_max | sip_default_value | sip_policy
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | AMBIENT_TEMPERATURE | blr_1_ambient_temperature | UN.UO.86XI6024.PV | DEGC |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | RELATIVE_HUMIDITY | blr_1_relative_humidity | UN.UO.86XI6025.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | HP_STEAM_PRESSURE | blr_1_hp_steam_pressure | UN.UO.71PI1113.PV | BARG | 40 | 49 |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | DESUPERHEATER_OUTLET_TEMP | blr_1_desuperheater_outlet_temp | UN.UO.71TC1111.PV | C | 370 | 440 |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | STEAM_FLOW_RAW | blr_1_steam_flow_raw | UN.UO.71FI1101.PV | KG/HR | 40000 | 175000 |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FLUE_GAS_OXYGEN | blr_1_flue_gas_oxygen | UN.UO.71AC1104.PV | MOLE% | 1 | 4 |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_C1 | blr_1_fuel_gas_c1 | AR.AR5.DCS.Process.AI51211.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_C2 | blr_1_fuel_gas_c2 | AR.AR5.DCS.Process.AI51212.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_C3 | blr_1_fuel_gas_c3 | AR.AR5.DCS.Process.AI51213.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_CO2 | blr_1_fuel_gas_co2 | AR.AR5.DCS.Process.AI51213.PV,AR.AR5.DCS.Process.AI51217.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_FLOW | blr_1_fuel_gas_flow | UN.UO.71FC1104.PV | KG/HR |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_IC4 | blr_1_fuel_gas_ic4 | AR.AR5.DCS.Process.AI51215.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_IC5 | blr_1_fuel_gas_ic5 | AR.AR5.DCS.Process.AI51215.PV,AR.AR5.DCS.Process.AI512111.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_N2 | blr_1_fuel_gas_n2 | AR.AR5.DCS.Process.AI51219.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_NC4 | blr_1_fuel_gas_nc4 | AR.AR5.DCS.Process.AI51214.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | FUEL_GAS_NC5 | blr_1_fuel_gas_nc5 | AR.AR5.DCS.Process.AI512110.PV | % |  |  |  | last_good_value
BLR_1 | 57db313d-bba0-598e-8f03-0af6d096a157 | Boiler | EXCESS_O2 | blr_1_excess_o2 | UN.UO.71AC1104.PV | MOLE% | 1 | 4 |  | last_good_value