# Implementing Boiler Balance Diagnostics

To help detect faulty measurement tags in the DCS, we have implemented strict Material and Energy balance validations directly inside the core boiler mathematical logic.

## 1. Configurable Validation Thresholds

In BoilerInput, two new configuration parameters were added:
- mass_balance_threshold_pct
- energy_balance_threshold_pct

By default, the code protects these checks using a 1.0% threshold if not explicitly set in the input CSV. If your specific meters have lower accuracy (e.g., ±3%), you can easily override this per boiler inside your CSV file.

## 2. Mass Balance Check

The logic actively compares total mass entering the boiler drum against mass leaving.

mass_in_t_h = m_in_bfw + m_in_spray
mass_out_t_h = m_out_steam + m_out_cbd
mass_balance_dev = (mass_in - mass_out) / mass_out * 100.0

## 3. Absolute Enthalpy Energy Balance Check

The code calculates the exact GJ/h of absolute heat enthalpy moving through the system to detect if the expected heat release matches the steam generation.

heat_in_total_gj_h = fuel_input_gj_h + heat_in_bfw + heat_in_spray
heat_out_total_gj_h = heat_out_steam + heat_out_cbd + stack_loss_gj_h + rad_loss_gj_h
energy_balance_dev = (heat_in - heat_out) / heat_out * 100.0

## 4. Execution Warning Example

During testing, our dummy data purposefully had an imbalance (124.0 t/h of feedwater producing only 120.0 t/h of steam with 2.5 t/h of blowdown).

The execution script (run_boilerhouse.py) automatically threw the following constraints during evaluation, precisely as intended:

[WARNING]
- [BLR-1] Mass balance deviation (1.22%) exceeds threshold (±1.0%)
- [BLR-1] Energy balance deviation (-7.50%) exceeds threshold (±1.0%)

This functionality is now live and will automatically flag any poorly calibrated flow or temperature meters moving forward!