## tag
tag_name | pi_name | tag_type | data_type
BLR_1_HPS_Gen_raw | YOUR.DCS.BLR1.STEAM_FLOW | pi | kg/hr
BLR_1_Fuel_raw | YOUR.DCS.BLR1.FUEL_FLOW | pi | kg/hr
BLR_1_FD_Fan_Steam_raw | YOUR.DCS.BLR1.FDF_STEAM | pi | kg/hr
BLR_1_Flue_O2_pct | YOUR.DCS.BLR1.FLUE_O2 | pi | %
BLR_1_Stack_Temp_C | YOUR.DCS.BLR1.STACK_TEMP | pi | C
BLR_1_FW_Temp_C | YOUR.DCS.BLR1.FW_TEMP | pi | C
BLR_1_Ambient_Temp_C | YOUR.DCS.AMBIENT_TEMP | pi | C
BLR_1_Flue_O2_flag | YOUR.DCS.BLR1.O2_FLAG | pi
BLR_2_HPS_Gen_raw | YOUR.DCS.BLR2.STEAM_FLOW | pi | kg/hr
BLR_2_Fuel_raw | YOUR.DCS.BLR2.FUEL_FLOW | pi | kg/hr
BLR_2_FD_Fan_Steam_raw | YOUR.DCS.BLR2.FDF_STEAM | pi | kg/hr
BLR_2_Flue_O2_pct | YOUR.DCS.BLR2.FLUE_O2 | pi | %
BLR_2_Stack_Temp_C | YOUR.DCS.BLR2.STACK_TEMP | pi | C
BLR_2_FW_Temp_C | YOUR.DCS.BLR2.FW_TEMP | pi | C
BLR_2_Ambient_Temp_C | YOUR.DCS.AMBIENT_TEMP | pi | C
BLR_2_Flue_O2_flag | YOUR.DCS.BLR2.O2_FLAG | pi
BLR_1_HPS_Gen |  | inferred
BLR_1_Fuel_Flow |  | inferred
BLR_1_Status |  | inferred
BLR_1_Capacity |  | inferred
BLR_1_Spec_En_Cons |  | inferred
BLR_1_HPS_Gen_warmup |  | inferred
BLR_1_FD_Fan_Steam_reg |  | inferred
BLR_1_FD_Fan_Steam_warmup |  | inferred
BLR_1_FD_Fan_Steam |  | inferred
BLR_1_useful_heat_gj_h |  | inferred
BLR_1_fuel_input_gj_h |  | inferred
BLR_1_efficiency_pct |  | inferred
BLR_1_excess_air_pct |  | inferred
BLR_1_stack_loss_pct |  | inferred
BLR_1_indirect_efficiency_pct |  | inferred
BLR_1_sec_gj_per_t_steam |  | inferred
BLR_1_co2_t_per_h |  | inferred
BLR_1_fuel_cost_per_hr |  | inferred
BLR_2_HPS_Gen |  | inferred
BLR_2_Fuel_Flow |  | inferred
BLR_2_Status |  | inferred
BLR_2_Capacity |  | inferred
BLR_2_Spec_En_Cons |  | inferred
BLR_2_HPS_Gen_warmup |  | inferred
BLR_2_FD_Fan_Steam_reg |  | inferred
BLR_2_FD_Fan_Steam_warmup |  | inferred
BLR_2_FD_Fan_Steam |  | inferred
BLR_2_useful_heat_gj_h |  | inferred
BLR_2_fuel_input_gj_h |  | inferred
BLR_2_efficiency_pct |  | inferred
BLR_2_excess_air_pct |  | inferred
BLR_2_stack_loss_pct |  | inferred
BLR_2_indirect_efficiency_pct |  | inferred
BLR_2_sec_gj_per_t_steam |  | inferred
BLR_2_co2_t_per_h |  | inferred
BLR_2_fuel_cost_per_hr |  | inferred
Buffer_Steam_in_Boilers |  | inferred
Total_Boilers_Running |  | inferred
Total_HPS_Generation |  | inferred
Total_Fuel_for_Boilers |  | inferred
Boilers_Total_Fuel_Input_GJ_h |  | inferred
Boilers_Total_CO2_t_h |  | inferred
Boilers_Average_Efficiency_pct |  | inferred
Boilers_Specific_Energy_GJ_per_t |  | inferred
BLR_1_Status |  | inferred
BLR_1_HPS_Gen |  | inferred
BLR_1_Fuel_Flow |  | inferred
BLR_1_FD_Fan_Steam |  | inferred
BLR_2_Status |  | inferred
BLR_2_HPS_Gen |  | inferred
BLR_2_Fuel_Flow |  | inferred
BLR_2_FD_Fan_Steam |  | inferred
Total_Boilers_Running |  | inferred
Total_HPS_Generation |  | inferred
Total_Fuel_for_Boilers |  | inferred

## master_pi_data
time_stamp | BLR_1_HPS_Gen_raw | BLR_1_Fuel_raw | BLR_1_FD_Fan_Steam_raw | BLR_1_Flue_O2_pct | BLR_1_Stack_Temp_C | BLR_1_FW_Temp_C | BLR_1_Ambient_Temp_C | BLR_1_Flue_O2_flag | BLR_2_HPS_Gen_raw | BLR_2_Fuel_raw | BLR_2_FD_Fan_Steam_raw | BLR_2_Flue_O2_pct | BLR_2_Stack_Temp_C | BLR_2_FW_Temp_C | BLR_2_Ambient_Temp_C | BLR_2_Flue_O2_flag
2026-05-06 19:06

## inferred
tag_name | formula_expression
BLR_1_HPS_Gen | if([BLR_1_HPS_Gen_raw]<0,0,[BLR_1_HPS_Gen_raw]/1000)
BLR_1_Fuel_Flow | [BLR_1_Fuel_raw]*[BLR_1_Status]/1000
BLR_1_Status | if([BLR_1_HPS_Gen]>=50,1,0)
BLR_1_Capacity | 150
BLR_1_Spec_En_Cons | if([BLR_1_HPS_Gen]==0,0,[BLR_1_Fuel_Flow]*[LHV]/[BLR_1_HPS_Gen])
BLR_1_HPS_Gen_warmup | if([BLR_1_Status]==0,[BLR_1_HPS_Gen],0)
BLR_1_FD_Fan_Steam_reg | ((4378.1-32.667*[BLR_1_HPS_Gen]+0.4255*[BLR_1_HPS_Gen]^2)/1000)
BLR_1_FD_Fan_Steam_warmup | if([BLR_1_FD_Fan_Steam_raw]>100 && [BLR_1_FD_Fan_Steam_raw]<8000 && [BLR_1_Status]==0,[BLR_1_FD_Fan_Steam_raw]/1000,0)
BLR_1_FD_Fan_Steam | if([BLR_1_FD_Fan_Steam_raw]<500,0,[BLR_1_FD_Fan_Steam_raw]/1000)
BLR_1_useful_heat_gj_h | [BLR_1_HPS_Gen]*2.7
BLR_1_fuel_input_gj_h | [BLR_1_Fuel_Flow]*[LHV]
BLR_1_efficiency_pct | if([BLR_1_fuel_input_gj_h]==0,0,[BLR_1_useful_heat_gj_h]/[BLR_1_fuel_input_gj_h]*100)
BLR_1_excess_air_pct | if([BLR_1_Flue_O2_pct]>=21,0,[BLR_1_Flue_O2_pct]/(21-[BLR_1_Flue_O2_pct])*100)
BLR_1_stack_loss_pct | if([BLR_1_Flue_O2_pct]>=21,0,0.55*([BLR_1_Stack_Temp_C]-[BLR_1_Ambient_Temp_C])/(21-[BLR_1_Flue_O2_pct]))
BLR_1_indirect_efficiency_pct | 100-[BLR_1_stack_loss_pct]-1
BLR_1_sec_gj_per_t_steam | if([BLR_1_HPS_Gen]==0,0,[BLR_1_fuel_input_gj_h]/[BLR_1_HPS_Gen])
BLR_1_co2_t_per_h | [BLR_1_fuel_input_gj_h]*56.1/1000
BLR_1_fuel_cost_per_hr | [BLR_1_Fuel_Flow]*[LHV]*[Fuel_Cost_in_MMBTU]
BLR_2_HPS_Gen | if([BLR_2_HPS_Gen_raw]<0,0,[BLR_2_HPS_Gen_raw]/1000)
BLR_2_Fuel_Flow | [BLR_2_Fuel_raw]*[BLR_2_Status]/1000
BLR_2_Status | if([BLR_2_HPS_Gen]>=50,1,0)
BLR_2_Capacity | 150
BLR_2_Spec_En_Cons | if([BLR_2_HPS_Gen]==0,0,[BLR_2_Fuel_Flow]*[LHV]/[BLR_2_HPS_Gen])
BLR_2_HPS_Gen_warmup | if([BLR_2_Status]==0,[BLR_2_HPS_Gen],0)
BLR_2_FD_Fan_Steam_reg | ((4711.7-39.276*[BLR_2_HPS_Gen]+0.4601*[BLR_2_HPS_Gen]^2)/1000)
BLR_2_FD_Fan_Steam_warmup | if([BLR_2_FD_Fan_Steam_raw]>100 && [BLR_2_FD_Fan_Steam_raw]<8000 && [BLR_2_Status]==0,[BLR_2_FD_Fan_Steam_raw]/1000,0)
BLR_2_FD_Fan_Steam | if([BLR_2_FD_Fan_Steam_raw]<500,0,[BLR_2_FD_Fan_Steam_raw]/1000)
BLR_2_useful_heat_gj_h | [BLR_2_HPS_Gen]*2.7
BLR_2_fuel_input_gj_h | [BLR_2_Fuel_Flow]*[LHV]
BLR_2_efficiency_pct | if([BLR_2_fuel_input_gj_h]==0,0,[BLR_2_useful_heat_gj_h]/[BLR_2_fuel_input_gj_h]*100)
BLR_2_excess_air_pct | if([BLR_2_Flue_O2_pct]>=21,0,[BLR_2_Flue_O2_pct]/(21-[BLR_2_Flue_O2_pct])*100)
BLR_2_stack_loss_pct | if([BLR_2_Flue_O2_pct]>=21,0,0.55*([BLR_2_Stack_Temp_C]-[BLR_2_Ambient_Temp_C])/(21-[BLR_2_Flue_O2_pct]))
BLR_2_indirect_efficiency_pct | 100-[BLR_2_stack_loss_pct]-1
BLR_2_sec_gj_per_t_steam | if([BLR_2_HPS_Gen]==0,0,[BLR_2_fuel_input_gj_h]/[BLR_2_HPS_Gen])
BLR_2_co2_t_per_h | [BLR_2_fuel_input_gj_h]*56.1/1000
BLR_2_fuel_cost_per_hr | [BLR_2_Fuel_Flow]*[LHV]*[Fuel_Cost_in_MMBTU]
Buffer_Steam_in_Boilers | 100
Total_Boilers_Running | [BLR_1_Status] + [BLR_2_Status]
Total_HPS_Generation | [BLR_1_HPS_Gen] + [BLR_2_HPS_Gen]
Total_Fuel_for_Boilers | [BLR_1_Fuel_Flow] + [BLR_2_Fuel_Flow]
Boilers_Total_Fuel_Input_GJ_h | [BLR_1_fuel_input_gj_h] + [BLR_2_fuel_input_gj_h]
Boilers_Total_CO2_t_h | [BLR_1_co2_t_per_h] + [BLR_2_co2_t_per_h]
Boilers_Average_Efficiency_pct | if([Total_HPS_Generation]==0,0,[BLR_1_HPS_Gen]*[BLR_1_efficiency_pct] + [BLR_2_HPS_Gen]*[BLR_2_efficiency_pct]/[Total_HPS_Generation])
Boilers_Specific_Energy_GJ_per_t | if([Total_HPS_Generation]==0,0,[Boilers_Total_Fuel_Input_GJ_h]/[Total_HPS_Generation])

## variables
tag_name | lower_bound_value | lower_bound_expression | upper_bound_value | upper_bound_expression | flag_integer | source_flag
BLR_1_Status | 0 | 0 | 1 | [BLR_1_Status] | 1 | GENERIC_TEMPLATE
BLR_1_HPS_Gen | 0 | [BLR_1_Status]*50 | 150 | [BLR_1_Status]*150 | 0 | GENERIC_TEMPLATE
BLR_1_Fuel_Flow | 0 | 0 | 12 | max(12,[BLR_1_Fuel_Flow]) | 0 | GENERIC_TEMPLATE
BLR_1_FD_Fan_Steam | 0 | 0 | 8 | max([BLR_1_FD_Fan_Steam],8) | 0 | GENERIC_TEMPLATE
BLR_2_Status | 0 | 0 | 1 | [BLR_2_Status] | 1 | GENERIC_TEMPLATE
BLR_2_HPS_Gen | 0 | [BLR_2_Status]*50 | 150 | [BLR_2_Status]*150 | 0 | GENERIC_TEMPLATE
BLR_2_Fuel_Flow | 0 | 0 | 12 | max(12,[BLR_2_Fuel_Flow]) | 0 | GENERIC_TEMPLATE
BLR_2_FD_Fan_Steam | 0 | 0 | 8 | max([BLR_2_FD_Fan_Steam],8) | 0 | GENERIC_TEMPLATE
Total_Boilers_Running | 0 | 0 | 2 | 2 | 1 | GENERIC_TEMPLATE
Total_HPS_Generation | 0 | 0 | 300 | 300 | 0 | GENERIC_TEMPLATE
Total_Fuel_for_Boilers | 0 | 0 | 24 | 24 | 0 | GENERIC_TEMPLATE

## derived_equations
tag_name | formula_expression | active | source_flag
BLR_1_HPS_Gen | [BLR_1_Fuel_Flow]*[LHV]/[BLR_1_Spec_En_Cons]*[BLR_1_Status]+(1-[BLR_1_Status])*[BLR_1_HPS_Gen_warmup] | 1 | GENERIC_TEMPLATE
BLR_1_Fuel_Flow | [BLR_1_Fuel_Flow]*[BLR_1_Status] | 1 | GENERIC_TEMPLATE
BLR_1_FD_Fan_Steam | if([BLR_1_FD_Fan_Steam_raw]<500,0,[BLR_1_FD_Fan_Steam_raw]/1000) | 1 | GENERIC_TEMPLATE
BLR_2_HPS_Gen | [BLR_2_Fuel_Flow]*[LHV]/[BLR_2_Spec_En_Cons]*[BLR_2_Status]+(1-[BLR_2_Status])*[BLR_2_HPS_Gen_warmup] | 1 | GENERIC_TEMPLATE
BLR_2_Fuel_Flow | [BLR_2_Fuel_Flow]*[BLR_2_Status] | 1 | GENERIC_TEMPLATE
BLR_2_FD_Fan_Steam | if([BLR_2_FD_Fan_Steam_raw]<500,0,[BLR_2_FD_Fan_Steam_raw]/1000) | 1 | GENERIC_TEMPLATE
Total_Boilers_Running | [BLR_1_Status] + [BLR_2_Status] | 1 | GENERIC_TEMPLATE
Total_HPS_Generation | [BLR_1_HPS_Gen] + [BLR_2_HPS_Gen] | 1 | GENERIC_TEMPLATE
Total_Fuel_for_Boilers | [BLR_1_Fuel_Flow] + [BLR_2_Fuel_Flow] | 1 | GENERIC_TEMPLATE

## derived_equation_post_optimizer
tag_name | formula_expression | active
BLR_1_Stack_Temp_C_clipped | if([BLR_1_Flue_O2_flag]==0,[BLR_1_Stack_Temp_C],min([BLR_1_Stack_Temp_C],(0.369*[BLR_1_HPS_Gen]+0.357*[BLR_1_Flue_O2_pct]+117.1))*[BLR_1_Status]) | 1
BLR_2_Stack_Temp_C_clipped | if([BLR_2_Flue_O2_flag]==0,[BLR_2_Stack_Temp_C],min([BLR_2_Stack_Temp_C],(0.446*[BLR_2_HPS_Gen]+0.31*[BLR_2_Flue_O2_pct]+110.2))*[BLR_2_Status]) | 1

## constraints
system | expression | active | source_flag
Boilers | [BLR_1_HPS_Gen] >= 50*[BLR_1_Status] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_1_Fuel_Flow] >= 0.000001*[BLR_1_Status] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_2_HPS_Gen] >= 50*[BLR_2_Status] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_2_Fuel_Flow] >= 0.000001*[BLR_2_Status] | 1 | GENERIC_TEMPLATE
Boilers | [Buffer_Steam_in_Boilers]+[Total_HPS_Generation] <= [BLR_1_Status]*[BLR_1_Capacity] + [BLR_2_Status]*[BLR_2_Capacity] | 1 | GENERIC_TEMPLATE

## inferred_tag_rm_block_mapping
model_id | tag_name | data_enrichment_inferred_calculation | post_optimizer_inferred_calculation | pre_optimizer_iterative_inferred | data_ingestion_seu_seec_inferred_calc | data_enrichment_peeo_adjusted_inferred | whatif_inferred
1 | BLR_1_HPS_Gen | 1
1 | BLR_1_Fuel_Flow | 1
1 | BLR_1_Status | 1
1 | BLR_1_Capacity | 1
1 | BLR_1_Spec_En_Cons | 1
1 | BLR_1_HPS_Gen_warmup | 1
1 | BLR_1_FD_Fan_Steam_reg | 1
1 | BLR_1_FD_Fan_Steam_warmup | 1
1 | BLR_1_FD_Fan_Steam | 1
1 | BLR_1_useful_heat_gj_h | 1
1 | BLR_1_fuel_input_gj_h | 1
1 | BLR_1_efficiency_pct | 1
1 | BLR_1_excess_air_pct | 1
1 | BLR_1_stack_loss_pct | 1
1 | BLR_1_indirect_efficiency_pct | 1
1 | BLR_1_sec_gj_per_t_steam | 1
1 | BLR_1_co2_t_per_h | 1
1 | BLR_1_fuel_cost_per_hr | 1
1 | BLR_2_HPS_Gen | 1
1 | BLR_2_Fuel_Flow | 1
1 | BLR_2_Status | 1
1 | BLR_2_Capacity | 1
1 | BLR_2_Spec_En_Cons | 1
1 | BLR_2_HPS_Gen_warmup | 1
1 | BLR_2_FD_Fan_Steam_reg | 1
1 | BLR_2_FD_Fan_Steam_warmup | 1
1 | BLR_2_FD_Fan_Steam | 1
1 | BLR_2_useful_heat_gj_h | 1
1 | BLR_2_fuel_input_gj_h | 1
1 | BLR_2_efficiency_pct | 1
1 | BLR_2_excess_air_pct | 1
1 | BLR_2_stack_loss_pct | 1
1 | BLR_2_indirect_efficiency_pct | 1
1 | BLR_2_sec_gj_per_t_steam | 1
1 | BLR_2_co2_t_per_h | 1
1 | BLR_2_fuel_cost_per_hr | 1
1 | Buffer_Steam_in_Boilers | 1
1 | Total_Boilers_Running | 1
1 | Total_HPS_Generation | 1
1 | Total_Fuel_for_Boilers | 1
1 | Boilers_Total_Fuel_Input_GJ_h | 1
1 | Boilers_Total_CO2_t_h | 1
1 | Boilers_Average_Efficiency_pct | 1
1 | Boilers_Specific_Energy_GJ_per_t | 1