## tag
tag_name | pi_name | tag_type | data_type
BLR_1_HPS_Gen_raw | UN.UO.71FI1101.PV | pi | kg/hr
Fuel_BLR_1_raw | UN.UO.BO-7101A.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | kg/hr
FD_Fan_BLR_1_Steam_raw | UN.UO.71FI1108.PV | pi | kg/hr
BLR_1_Flue_O2_pct | UN.UO.BO-71011.FLUE_O2_PCT | pi | %
BLR_1_Stack_Temp_C | UN.UO.BO-71011.STACK_TEMP | pi | C
BLR_1_HPS_Pressure_bar | UN.UO.BO-71011.STEAM_P | pi | bar
BLR_1_HPS_Temp_C | UN.UO.BO-71011.STEAM_T | pi | C
BLR_1_FW_Temp_C | UN.UO.BO-71011.FW_TEMP | pi | C
BLR_1_Ambient_Temp_C | UN.UO.AMBIENT_TEMP | pi | C
BLR_1_Flue_O2_flag | UN.UO.BO-71011.O2_FLAG | pi
BLR_2_HPS_Gen_raw | UN.UO.71FI1201.PV | pi | kg/hr
Fuel_BLR_2_raw | UN.UO.BO-7101B.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | kg/hr
FD_Fan_BLR_2_Steam_raw | UN.UO.71FI1208.PV | pi | kg/hr
BLR_2_Flue_O2_pct | UN.UO.BO-71012.FLUE_O2_PCT | pi | %
BLR_2_Stack_Temp_C | UN.UO.BO-71012.STACK_TEMP | pi | C
BLR_2_HPS_Pressure_bar | UN.UO.BO-71012.STEAM_P | pi | bar
BLR_2_HPS_Temp_C | UN.UO.BO-71012.STEAM_T | pi | C
BLR_2_FW_Temp_C | UN.UO.BO-71012.FW_TEMP | pi | C
BLR_2_Ambient_Temp_C | UN.UO.AMBIENT_TEMP | pi | C
BLR_2_Flue_O2_flag | UN.UO.BO-71012.O2_FLAG | pi
BLR_3_HPS_Gen_raw | UN.UO.71FI1301.PV | pi | kg/hr
Fuel_BLR_3_raw | UN.UO.BO-7101C.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | kg/hr
FD_Fan_BLR_3_Steam_raw | UN.UO.71FI1308.PV | pi | kg/hr
BLR_3_Flue_O2_pct | UN.UO.BO-71013.FLUE_O2_PCT | pi | %
BLR_3_Stack_Temp_C | UN.UO.BO-71013.STACK_TEMP | pi | C
BLR_3_HPS_Pressure_bar | UN.UO.BO-71013.STEAM_P | pi | bar
BLR_3_HPS_Temp_C | UN.UO.BO-71013.STEAM_T | pi | C
BLR_3_FW_Temp_C | UN.UO.BO-71013.FW_TEMP | pi | C
BLR_3_Ambient_Temp_C | UN.UO.AMBIENT_TEMP | pi | C
BLR_3_Flue_O2_flag | UN.UO.BO-71013.O2_FLAG | pi
BLR_4_HPS_Gen_raw | UN.UO.71FI1401.PV | pi | kg/hr
Fuel_BLR_4_raw | UN.UO.BO-7101D.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | kg/hr
FD_Fan_BLR_4_Steam_raw | UN.UO.71FI1408.PV | pi | kg/hr
BLR_4_Flue_O2_pct | UN.UO.BO-71014.FLUE_O2_PCT | pi | %
BLR_4_Stack_Temp_C | UN.UO.BO-71014.STACK_TEMP | pi | C
BLR_4_HPS_Pressure_bar | UN.UO.BO-71014.STEAM_P | pi | bar
BLR_4_HPS_Temp_C | UN.UO.BO-71014.STEAM_T | pi | C
BLR_4_FW_Temp_C | UN.UO.BO-71014.FW_TEMP | pi | C
BLR_4_Ambient_Temp_C | UN.UO.AMBIENT_TEMP | pi | C
BLR_4_Flue_O2_flag | UN.UO.BO-71014.O2_FLAG | pi
BLR_5_HPS_Gen_raw | UN.UO.71FI1501A.PV | pi | kg/hr
Fuel_BLR_5_raw | UN.UO.PK-7104E.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | kg/hr
FD_Fan_BLR_5_Steam_raw | UN.UO.71FI1508.PV | pi | kg/hr
BLR_5_Flue_O2_pct | UN.UO.BO-71015.FLUE_O2_PCT | pi | %
BLR_5_Stack_Temp_C | UN.UO.BO-71015.STACK_TEMP | pi | C
BLR_5_HPS_Pressure_bar | UN.UO.BO-71015.STEAM_P | pi | bar
BLR_5_HPS_Temp_C | UN.UO.BO-71015.STEAM_T | pi | C
BLR_5_FW_Temp_C | UN.UO.BO-71015.FW_TEMP | pi | C
BLR_5_Ambient_Temp_C | UN.UO.AMBIENT_TEMP | pi | C
BLR_5_Flue_O2_flag | UN.UO.BO-71015.O2_FLAG | pi
BLR_1_HPS_Gen |  | inferred
Fuel_BLR_1 |  | inferred
BLR_1_Status |  | inferred
BLR_1_Capacity |  | inferred
Spec_En_Cons_BLR_1 |  | inferred
BLR_1_HPS_Gen_warmup |  | inferred
FD_Fan_BLR_1_Steam_reg |  | inferred
FD_Fan_BLR_1_Steam_warmup |  | inferred
FD_Fan_BLR_1_Steam |  | inferred
BLR_1_useful_heat_gj_h |  | inferred
BLR_1_fuel_input_gj_h |  | inferred
BLR_1_efficiency_pct |  | inferred
BLR_1_excess_air_pct |  | inferred
BLR_1_stack_loss_pct |  | inferred
BLR_1_indirect_efficiency_pct |  | inferred
BLR_1_sec_gj_per_t_steam |  | inferred
BLR_1_co2_t_per_h |  | inferred
BLR_1_fuel_cost_per_hr |  | inferred
BLR_2_HPS_Gen |  | inferred
Fuel_BLR_2 |  | inferred
BLR_2_Status |  | inferred
BLR_2_Capacity |  | inferred
Spec_En_Cons_BLR_2 |  | inferred
BLR_2_HPS_Gen_warmup |  | inferred
FD_Fan_BLR_2_Steam_reg |  | inferred
FD_Fan_BLR_2_Steam_warmup |  | inferred
FD_Fan_BLR_2_Steam |  | inferred
BLR_2_useful_heat_gj_h |  | inferred
BLR_2_fuel_input_gj_h |  | inferred
BLR_2_efficiency_pct |  | inferred
BLR_2_excess_air_pct |  | inferred
BLR_2_stack_loss_pct |  | inferred
BLR_2_indirect_efficiency_pct |  | inferred
BLR_2_sec_gj_per_t_steam |  | inferred
BLR_2_co2_t_per_h |  | inferred
BLR_2_fuel_cost_per_hr |  | inferred
BLR_3_HPS_Gen |  | inferred
Fuel_BLR_3 |  | inferred
BLR_3_Status |  | inferred
BLR_3_Capacity |  | inferred
Spec_En_Cons_BLR_3 |  | inferred
BLR_3_HPS_Gen_warmup |  | inferred
FD_Fan_BLR_3_Steam_reg |  | inferred
FD_Fan_BLR_3_Steam_warmup |  | inferred
FD_Fan_BLR_3_Steam |  | inferred
BLR_3_useful_heat_gj_h |  | inferred
BLR_3_fuel_input_gj_h |  | inferred
BLR_3_efficiency_pct |  | inferred
BLR_3_excess_air_pct |  | inferred
BLR_3_stack_loss_pct |  | inferred
BLR_3_indirect_efficiency_pct |  | inferred
BLR_3_sec_gj_per_t_steam |  | inferred
BLR_3_co2_t_per_h |  | inferred
BLR_3_fuel_cost_per_hr |  | inferred
BLR_4_HPS_Gen |  | inferred
Fuel_BLR_4 |  | inferred
BLR_4_Status |  | inferred
BLR_4_Capacity |  | inferred
Spec_En_Cons_BLR_4 |  | inferred
BLR_4_HPS_Gen_warmup |  | inferred
FD_Fan_BLR_4_Steam_reg |  | inferred
FD_Fan_BLR_4_Steam_warmup |  | inferred
FD_Fan_BLR_4_Steam |  | inferred
BLR_4_useful_heat_gj_h |  | inferred
BLR_4_fuel_input_gj_h |  | inferred
BLR_4_efficiency_pct |  | inferred
BLR_4_excess_air_pct |  | inferred
BLR_4_stack_loss_pct |  | inferred
BLR_4_indirect_efficiency_pct |  | inferred
BLR_4_sec_gj_per_t_steam |  | inferred
BLR_4_co2_t_per_h |  | inferred
BLR_4_fuel_cost_per_hr |  | inferred
BLR_5_HPS_Gen |  | inferred
Fuel_BLR_5 |  | inferred
BLR_5_Status |  | inferred
BLR_5_Capacity |  | inferred
Spec_En_Cons_BLR_5 |  | inferred
BLR_5_HPS_Gen_warmup |  | inferred
FD_Fan_BLR_5_Steam_reg |  | inferred
FD_Fan_BLR_5_Steam_warmup |  | inferred
FD_Fan_BLR_5_Steam |  | inferred
BLR_5_useful_heat_gj_h |  | inferred
BLR_5_fuel_input_gj_h |  | inferred
BLR_5_efficiency_pct |  | inferred
BLR_5_excess_air_pct |  | inferred
BLR_5_stack_loss_pct |  | inferred
BLR_5_indirect_efficiency_pct |  | inferred
BLR_5_sec_gj_per_t_steam |  | inferred
BLR_5_co2_t_per_h |  | inferred
BLR_5_fuel_cost_per_hr |  | inferred
Buffer_Steam_in_Boilers |  | inferred
Total_Boilers_Running |  | inferred
Total_BLR_HPS_Generation |  | inferred
Total_Fuel_for_Boilers |  | inferred
Boilers_Total_Fuel_Input_GJ_h |  | inferred
Boilers_Total_CO2_t_h |  | inferred
Boilers_Average_Efficiency_pct |  | inferred
Boilers_Specific_Energy_GJ_per_t |  | inferred
BLR_1_Status |  | inferred
BLR_1_HPS_Gen |  | inferred
Fuel_BLR_1 |  | inferred
FD_Fan_BLR_1_Steam |  | inferred
BLR_2_Status |  | inferred
BLR_2_HPS_Gen |  | inferred
Fuel_BLR_2 |  | inferred
FD_Fan_BLR_2_Steam |  | inferred
BLR_3_Status |  | inferred
BLR_3_HPS_Gen |  | inferred
Fuel_BLR_3 |  | inferred
FD_Fan_BLR_3_Steam |  | inferred
BLR_4_Status |  | inferred
BLR_4_HPS_Gen |  | inferred
Fuel_BLR_4 |  | inferred
FD_Fan_BLR_4_Steam |  | inferred
BLR_5_Status |  | inferred
BLR_5_HPS_Gen |  | inferred
Fuel_BLR_5 |  | inferred
FD_Fan_BLR_5_Steam |  | inferred
Total_Boilers_Running |  | inferred
Total_BLR_HPS_Generation |  | inferred
Total_Fuel_for_Boilers |  | inferred

## master_pi_data
time_stamp | BLR_1_HPS_Gen_raw | Fuel_BLR_1_raw | FD_Fan_BLR_1_Steam_raw | BLR_1_Flue_O2_pct | BLR_1_Stack_Temp_C | BLR_1_HPS_Pressure_bar | BLR_1_HPS_Temp_C | BLR_1_FW_Temp_C | BLR_1_Ambient_Temp_C | BLR_1_Flue_O2_flag | BLR_2_HPS_Gen_raw | Fuel_BLR_2_raw | FD_Fan_BLR_2_Steam_raw | BLR_2_Flue_O2_pct | BLR_2_Stack_Temp_C | BLR_2_HPS_Pressure_bar | BLR_2_HPS_Temp_C | BLR_2_FW_Temp_C | BLR_2_Ambient_Temp_C | BLR_2_Flue_O2_flag | BLR_3_HPS_Gen_raw | Fuel_BLR_3_raw | FD_Fan_BLR_3_Steam_raw | BLR_3_Flue_O2_pct | BLR_3_Stack_Temp_C | BLR_3_HPS_Pressure_bar | BLR_3_HPS_Temp_C | BLR_3_FW_Temp_C | BLR_3_Ambient_Temp_C | BLR_3_Flue_O2_flag | BLR_4_HPS_Gen_raw | Fuel_BLR_4_raw | FD_Fan_BLR_4_Steam_raw | BLR_4_Flue_O2_pct | BLR_4_Stack_Temp_C | BLR_4_HPS_Pressure_bar | BLR_4_HPS_Temp_C | BLR_4_FW_Temp_C | BLR_4_Ambient_Temp_C | BLR_4_Flue_O2_flag | BLR_5_HPS_Gen_raw | Fuel_BLR_5_raw | FD_Fan_BLR_5_Steam_raw | BLR_5_Flue_O2_pct | BLR_5_Stack_Temp_C | BLR_5_HPS_Pressure_bar | BLR_5_HPS_Temp_C | BLR_5_FW_Temp_C | BLR_5_Ambient_Temp_C | BLR_5_Flue_O2_flag
2026-05-06 21:17

## inferred
tag_name | formula_expression
BLR_1_HPS_Gen | if([BLR_1_HPS_Gen_raw]<0,0,[BLR_1_HPS_Gen_raw]/1000)
Fuel_BLR_1 | [Fuel_BLR_1_raw]*[BLR_1_Status]/1000
BLR_1_Status | if([BLR_1_HPS_Gen]>=50,1,0)
BLR_1_Capacity | 150
Spec_En_Cons_BLR_1 | if([BLR_1_HPS_Gen]==0,0,[Fuel_BLR_1]*[LHV]/[BLR_1_HPS_Gen])
BLR_1_HPS_Gen_warmup | if([BLR_1_Status]==0,[BLR_1_HPS_Gen],0)
FD_Fan_BLR_1_Steam_reg | ((4378.1-32.667*[BLR_1_HPS_Gen]+0.4255*[BLR_1_HPS_Gen]^2)/1000)
FD_Fan_BLR_1_Steam_warmup | if([FD_Fan_BLR_1_Steam_raw]>100 && [FD_Fan_BLR_1_Steam_raw]<8000 && [BLR_1_Status]==0,[FD_Fan_BLR_1_Steam_raw]/1000,0)
FD_Fan_BLR_1_Steam | if([FD_Fan_BLR_1_Steam_raw]<500,0,[FD_Fan_BLR_1_Steam_raw]/1000)
BLR_1_useful_heat_gj_h | [BLR_1_HPS_Gen]*2.7
BLR_1_fuel_input_gj_h | [Fuel_BLR_1]*[LHV]
BLR_1_efficiency_pct | if([BLR_1_fuel_input_gj_h]==0,0,[BLR_1_useful_heat_gj_h]/[BLR_1_fuel_input_gj_h]*100)
BLR_1_excess_air_pct | if([BLR_1_Flue_O2_pct]>=21,0,[BLR_1_Flue_O2_pct]/(21-[BLR_1_Flue_O2_pct])*100)
BLR_1_stack_loss_pct | if([BLR_1_Flue_O2_pct]>=21,0,0.55*([BLR_1_Stack_Temp_C]-[BLR_1_Ambient_Temp_C])/(21-[BLR_1_Flue_O2_pct]))
BLR_1_indirect_efficiency_pct | 100-[BLR_1_stack_loss_pct]-1
BLR_1_sec_gj_per_t_steam | if([BLR_1_HPS_Gen]==0,0,[BLR_1_fuel_input_gj_h]/[BLR_1_HPS_Gen])
BLR_1_co2_t_per_h | [BLR_1_fuel_input_gj_h]*56.1/1000
BLR_1_fuel_cost_per_hr | [Fuel_BLR_1]*[LHV]*[Fuel_Cost_in_MMBTU]
BLR_2_HPS_Gen | if([BLR_2_HPS_Gen_raw]<0,0,[BLR_2_HPS_Gen_raw]/1000)
Fuel_BLR_2 | [Fuel_BLR_2_raw]*[BLR_2_Status]/1000
BLR_2_Status | if([BLR_2_HPS_Gen]>=50,1,0)
BLR_2_Capacity | 150
Spec_En_Cons_BLR_2 | if([BLR_2_HPS_Gen]==0,0,[Fuel_BLR_2]*[LHV]/[BLR_2_HPS_Gen])
BLR_2_HPS_Gen_warmup | if([BLR_2_Status]==0,[BLR_2_HPS_Gen],0)
FD_Fan_BLR_2_Steam_reg | ((4711.7-39.276*[BLR_2_HPS_Gen]+0.4601*[BLR_2_HPS_Gen]^2)/1000)
FD_Fan_BLR_2_Steam_warmup | if([FD_Fan_BLR_2_Steam_raw]>100 && [FD_Fan_BLR_2_Steam_raw]<8000 && [BLR_2_Status]==0,[FD_Fan_BLR_2_Steam_raw]/1000,0)
FD_Fan_BLR_2_Steam | if([FD_Fan_BLR_2_Steam_raw]<500,0,[FD_Fan_BLR_2_Steam_raw]/1000)
BLR_2_useful_heat_gj_h | [BLR_2_HPS_Gen]*2.7
BLR_2_fuel_input_gj_h | [Fuel_BLR_2]*[LHV]
BLR_2_efficiency_pct | if([BLR_2_fuel_input_gj_h]==0,0,[BLR_2_useful_heat_gj_h]/[BLR_2_fuel_input_gj_h]*100)
BLR_2_excess_air_pct | if([BLR_2_Flue_O2_pct]>=21,0,[BLR_2_Flue_O2_pct]/(21-[BLR_2_Flue_O2_pct])*100)
BLR_2_stack_loss_pct | if([BLR_2_Flue_O2_pct]>=21,0,0.55*([BLR_2_Stack_Temp_C]-[BLR_2_Ambient_Temp_C])/(21-[BLR_2_Flue_O2_pct]))
BLR_2_indirect_efficiency_pct | 100-[BLR_2_stack_loss_pct]-1
BLR_2_sec_gj_per_t_steam | if([BLR_2_HPS_Gen]==0,0,[BLR_2_fuel_input_gj_h]/[BLR_2_HPS_Gen])
BLR_2_co2_t_per_h | [BLR_2_fuel_input_gj_h]*56.1/1000
BLR_2_fuel_cost_per_hr | [Fuel_BLR_2]*[LHV]*[Fuel_Cost_in_MMBTU]
BLR_3_HPS_Gen | if([BLR_3_HPS_Gen_raw]<0,0,[BLR_3_HPS_Gen_raw]/1000)
Fuel_BLR_3 | [Fuel_BLR_3_raw]*[BLR_3_Status]/1000
BLR_3_Status | if([BLR_3_HPS_Gen]>=50,1,0)
BLR_3_Capacity | 150
Spec_En_Cons_BLR_3 | if([BLR_3_HPS_Gen]==0,0,[Fuel_BLR_3]*[LHV]/[BLR_3_HPS_Gen])
BLR_3_HPS_Gen_warmup | if([BLR_3_Status]==0,[BLR_3_HPS_Gen],0)
FD_Fan_BLR_3_Steam_reg | ((4701.3-35.004*[BLR_3_HPS_Gen]+0.4481*[BLR_3_HPS_Gen]^2)/1000)
FD_Fan_BLR_3_Steam_warmup | if([FD_Fan_BLR_3_Steam_raw]>100 && [FD_Fan_BLR_3_Steam_raw]<8000 && [BLR_3_Status]==0,[FD_Fan_BLR_3_Steam_raw]/1000,0)
FD_Fan_BLR_3_Steam | if([FD_Fan_BLR_3_Steam_raw]<500,0,[FD_Fan_BLR_3_Steam_raw]/1000)
BLR_3_useful_heat_gj_h | [BLR_3_HPS_Gen]*2.7
BLR_3_fuel_input_gj_h | [Fuel_BLR_3]*[LHV]
BLR_3_efficiency_pct | if([BLR_3_fuel_input_gj_h]==0,0,[BLR_3_useful_heat_gj_h]/[BLR_3_fuel_input_gj_h]*100)
BLR_3_excess_air_pct | if([BLR_3_Flue_O2_pct]>=21,0,[BLR_3_Flue_O2_pct]/(21-[BLR_3_Flue_O2_pct])*100)
BLR_3_stack_loss_pct | if([BLR_3_Flue_O2_pct]>=21,0,0.55*([BLR_3_Stack_Temp_C]-[BLR_3_Ambient_Temp_C])/(21-[BLR_3_Flue_O2_pct]))
BLR_3_indirect_efficiency_pct | 100-[BLR_3_stack_loss_pct]-1
BLR_3_sec_gj_per_t_steam | if([BLR_3_HPS_Gen]==0,0,[BLR_3_fuel_input_gj_h]/[BLR_3_HPS_Gen])
BLR_3_co2_t_per_h | [BLR_3_fuel_input_gj_h]*56.1/1000
BLR_3_fuel_cost_per_hr | [Fuel_BLR_3]*[LHV]*[Fuel_Cost_in_MMBTU]
BLR_4_HPS_Gen | if([BLR_4_HPS_Gen_raw]<0,0,[BLR_4_HPS_Gen_raw]/1000)
Fuel_BLR_4 | [Fuel_BLR_4_raw]*[BLR_4_Status]/1000
BLR_4_Status | if([BLR_4_HPS_Gen]>=50,1,0)
BLR_4_Capacity | 150
Spec_En_Cons_BLR_4 | if([BLR_4_HPS_Gen]==0,0,[Fuel_BLR_4]*[LHV]/[BLR_4_HPS_Gen])
BLR_4_HPS_Gen_warmup | if([BLR_4_Status]==0,[BLR_4_HPS_Gen],0)
FD_Fan_BLR_4_Steam_reg | ((5015.5-46.088*[BLR_4_HPS_Gen]+0.4828*[BLR_4_HPS_Gen]^2)/1000)
FD_Fan_BLR_4_Steam_warmup | if([FD_Fan_BLR_4_Steam_raw]>100 && [FD_Fan_BLR_4_Steam_raw]<8000 && [BLR_4_Status]==0,[FD_Fan_BLR_4_Steam_raw]/1000,0)
FD_Fan_BLR_4_Steam | if([FD_Fan_BLR_4_Steam_raw]<500,0,[FD_Fan_BLR_4_Steam_raw]/1000)
BLR_4_useful_heat_gj_h | [BLR_4_HPS_Gen]*2.7
BLR_4_fuel_input_gj_h | [Fuel_BLR_4]*[LHV]
BLR_4_efficiency_pct | if([BLR_4_fuel_input_gj_h]==0,0,[BLR_4_useful_heat_gj_h]/[BLR_4_fuel_input_gj_h]*100)
BLR_4_excess_air_pct | if([BLR_4_Flue_O2_pct]>=21,0,[BLR_4_Flue_O2_pct]/(21-[BLR_4_Flue_O2_pct])*100)
BLR_4_stack_loss_pct | if([BLR_4_Flue_O2_pct]>=21,0,0.55*([BLR_4_Stack_Temp_C]-[BLR_4_Ambient_Temp_C])/(21-[BLR_4_Flue_O2_pct]))
BLR_4_indirect_efficiency_pct | 100-[BLR_4_stack_loss_pct]-1
BLR_4_sec_gj_per_t_steam | if([BLR_4_HPS_Gen]==0,0,[BLR_4_fuel_input_gj_h]/[BLR_4_HPS_Gen])
BLR_4_co2_t_per_h | [BLR_4_fuel_input_gj_h]*56.1/1000
BLR_4_fuel_cost_per_hr | [Fuel_BLR_4]*[LHV]*[Fuel_Cost_in_MMBTU]
BLR_5_HPS_Gen | if([BLR_5_HPS_Gen_raw]<0,0,[BLR_5_HPS_Gen_raw]/1000)
Fuel_BLR_5 | [Fuel_BLR_5_raw]*[BLR_5_Status]/1000
BLR_5_Status | if([BLR_5_HPS_Gen]>=50,1,0)
BLR_5_Capacity | 150
Spec_En_Cons_BLR_5 | if([BLR_5_HPS_Gen]==0,0,[Fuel_BLR_5]*[LHV]/[BLR_5_HPS_Gen])
BLR_5_HPS_Gen_warmup | if([BLR_5_Status]==0,[BLR_5_HPS_Gen],0)
FD_Fan_BLR_5_Steam_reg | ((4772.4+9.2624*[BLR_5_HPS_Gen]+0.0843*[BLR_5_HPS_Gen]^2)/1000)
FD_Fan_BLR_5_Steam_warmup | if([FD_Fan_BLR_5_Steam_raw]>100 && [FD_Fan_BLR_5_Steam_raw]<8000 && [BLR_5_Status]==0,[FD_Fan_BLR_5_Steam_raw]/1000,0)
FD_Fan_BLR_5_Steam | if([FD_Fan_BLR_5_Steam_raw]<500,0,[FD_Fan_BLR_5_Steam_raw]/1000)
BLR_5_useful_heat_gj_h | [BLR_5_HPS_Gen]*2.7
BLR_5_fuel_input_gj_h | [Fuel_BLR_5]*[LHV]
BLR_5_efficiency_pct | if([BLR_5_fuel_input_gj_h]==0,0,[BLR_5_useful_heat_gj_h]/[BLR_5_fuel_input_gj_h]*100)
BLR_5_excess_air_pct | if([BLR_5_Flue_O2_pct]>=21,0,[BLR_5_Flue_O2_pct]/(21-[BLR_5_Flue_O2_pct])*100)
BLR_5_stack_loss_pct | if([BLR_5_Flue_O2_pct]>=21,0,0.55*([BLR_5_Stack_Temp_C]-[BLR_5_Ambient_Temp_C])/(21-[BLR_5_Flue_O2_pct]))
BLR_5_indirect_efficiency_pct | 100-[BLR_5_stack_loss_pct]-1
BLR_5_sec_gj_per_t_steam | if([BLR_5_HPS_Gen]==0,0,[BLR_5_fuel_input_gj_h]/[BLR_5_HPS_Gen])
BLR_5_co2_t_per_h | [BLR_5_fuel_input_gj_h]*56.1/1000
BLR_5_fuel_cost_per_hr | [Fuel_BLR_5]*[LHV]*[Fuel_Cost_in_MMBTU]
Buffer_Steam_in_Boilers | 100
Total_Boilers_Running | [BLR_1_Status] + [BLR_2_Status] + [BLR_3_Status] + [BLR_4_Status] + [BLR_5_Status]
Total_BLR_HPS_Generation | [BLR_1_HPS_Gen] + [BLR_2_HPS_Gen] + [BLR_3_HPS_Gen] + [BLR_4_HPS_Gen] + [BLR_5_HPS_Gen]
Total_Fuel_for_Boilers | [Fuel_BLR_1] + [Fuel_BLR_2] + [Fuel_BLR_3] + [Fuel_BLR_4] + [Fuel_BLR_5]
Boilers_Total_Fuel_Input_GJ_h | [BLR_1_fuel_input_gj_h] + [BLR_2_fuel_input_gj_h] + [BLR_3_fuel_input_gj_h] + [BLR_4_fuel_input_gj_h] + [BLR_5_fuel_input_gj_h]
Boilers_Total_CO2_t_h | [BLR_1_co2_t_per_h] + [BLR_2_co2_t_per_h] + [BLR_3_co2_t_per_h] + [BLR_4_co2_t_per_h] + [BLR_5_co2_t_per_h]
Boilers_Average_Efficiency_pct | if([Total_BLR_HPS_Generation]==0,0,[BLR_1_HPS_Gen]*[BLR_1_efficiency_pct] + [BLR_2_HPS_Gen]*[BLR_2_efficiency_pct] + [BLR_3_HPS_Gen]*[BLR_3_efficiency_pct] + [BLR_4_HPS_Gen]*[BLR_4_efficiency_pct] + [BLR_5_HPS_Gen]*[BLR_5_efficiency_pct]/[Total_BLR_HPS_Generation])
Boilers_Specific_Energy_GJ_per_t | if([Total_BLR_HPS_Generation]==0,0,[Boilers_Total_Fuel_Input_GJ_h]/[Total_BLR_HPS_Generation])

## variables
tag_name | lower_bound_value | lower_bound_expression | upper_bound_value | upper_bound_expression | flag_integer | source_flag
BLR_1_Status | 0 | 0 | 1 | [BLR_1_Status] | 1 | GENERIC_TEMPLATE
BLR_1_HPS_Gen | 0 | [BLR_1_Status]*50 | 150 | [BLR_1_Status]*150 | 0 | GENERIC_TEMPLATE
Fuel_BLR_1 | 0 | 0 | 12 | max(12,[Fuel_BLR_1]) | 0 | GENERIC_TEMPLATE
FD_Fan_BLR_1_Steam | 0 | 0 | 8 | max([FD_Fan_BLR_1_Steam],8) | 0 | GENERIC_TEMPLATE
BLR_2_Status | 0 | 0 | 1 | [BLR_2_Status] | 1 | GENERIC_TEMPLATE
BLR_2_HPS_Gen | 0 | [BLR_2_Status]*50 | 150 | [BLR_2_Status]*150 | 0 | GENERIC_TEMPLATE
Fuel_BLR_2 | 0 | 0 | 12 | max(12,[Fuel_BLR_2]) | 0 | GENERIC_TEMPLATE
FD_Fan_BLR_2_Steam | 0 | 0 | 8 | max([FD_Fan_BLR_2_Steam],8) | 0 | GENERIC_TEMPLATE
BLR_3_Status | 0 | 0 | 1 | [BLR_3_Status] | 1 | GENERIC_TEMPLATE
BLR_3_HPS_Gen | 0 | [BLR_3_Status]*50 | 150 | [BLR_3_Status]*150 | 0 | GENERIC_TEMPLATE
Fuel_BLR_3 | 0 | 0 | 12 | max(12,[Fuel_BLR_3]) | 0 | GENERIC_TEMPLATE
FD_Fan_BLR_3_Steam | 0 | 0 | 8 | max([FD_Fan_BLR_3_Steam],8) | 0 | GENERIC_TEMPLATE
BLR_4_Status | 0 | 0 | 1 | [BLR_4_Status] | 1 | GENERIC_TEMPLATE
BLR_4_HPS_Gen | 0 | [BLR_4_Status]*50 | 150 | [BLR_4_Status]*150 | 0 | GENERIC_TEMPLATE
Fuel_BLR_4 | 0 | 0 | 12 | max(12,[Fuel_BLR_4]) | 0 | GENERIC_TEMPLATE
FD_Fan_BLR_4_Steam | 0 | 0 | 8 | max([FD_Fan_BLR_4_Steam],8) | 0 | GENERIC_TEMPLATE
BLR_5_Status | 0 | 0 | 1 | [BLR_5_Status] | 1 | GENERIC_TEMPLATE
BLR_5_HPS_Gen | 0 | [BLR_5_Status]*50 | 150 | [BLR_5_Status]*150 | 0 | GENERIC_TEMPLATE
Fuel_BLR_5 | 0 | 0 | 12 | max(12,[Fuel_BLR_5]) | 0 | GENERIC_TEMPLATE
FD_Fan_BLR_5_Steam | 0 | 0 | 8 | max([FD_Fan_BLR_5_Steam],8) | 0 | GENERIC_TEMPLATE
Total_Boilers_Running | 0 | 0 | 5 | 5 | 1 | GENERIC_TEMPLATE
Total_BLR_HPS_Generation | 0 | 0 | 750 | 750 | 0 | GENERIC_TEMPLATE
Total_Fuel_for_Boilers | 0 | 0 | 60 | 60 | 0 | GENERIC_TEMPLATE

## derived_equations
tag_name | formula_expression | active | source_flag
BLR_1_HPS_Gen | [Fuel_BLR_1]*[LHV]/[Spec_En_Cons_BLR_1]*[BLR_1_Status]+(1-[BLR_1_Status])*[BLR_1_HPS_Gen_warmup] | 1 | GENERIC_TEMPLATE
Fuel_BLR_1 | [Fuel_BLR_1]*[BLR_1_Status] | 1 | GENERIC_TEMPLATE
FD_Fan_BLR_1_Steam | if([FD_Fan_BLR_1_Steam_raw]<500,0,[FD_Fan_BLR_1_Steam_raw]/1000) | 1 | GENERIC_TEMPLATE
BLR_2_HPS_Gen | [Fuel_BLR_2]*[LHV]/[Spec_En_Cons_BLR_2]*[BLR_2_Status]+(1-[BLR_2_Status])*[BLR_2_HPS_Gen_warmup] | 1 | GENERIC_TEMPLATE
Fuel_BLR_2 | [Fuel_BLR_2]*[BLR_2_Status] | 1 | GENERIC_TEMPLATE
FD_Fan_BLR_2_Steam | if([FD_Fan_BLR_2_Steam_raw]<500,0,[FD_Fan_BLR_2_Steam_raw]/1000) | 1 | GENERIC_TEMPLATE
BLR_3_HPS_Gen | [Fuel_BLR_3]*[LHV]/[Spec_En_Cons_BLR_3]*[BLR_3_Status]+(1-[BLR_3_Status])*[BLR_3_HPS_Gen_warmup] | 1 | GENERIC_TEMPLATE
Fuel_BLR_3 | [Fuel_BLR_3]*[BLR_3_Status] | 1 | GENERIC_TEMPLATE
FD_Fan_BLR_3_Steam | if([FD_Fan_BLR_3_Steam_raw]<500,0,[FD_Fan_BLR_3_Steam_raw]/1000) | 1 | GENERIC_TEMPLATE
BLR_4_HPS_Gen | [Fuel_BLR_4]*[LHV]/[Spec_En_Cons_BLR_4]*[BLR_4_Status]+(1-[BLR_4_Status])*[BLR_4_HPS_Gen_warmup] | 1 | GENERIC_TEMPLATE
Fuel_BLR_4 | [Fuel_BLR_4]*[BLR_4_Status] | 1 | GENERIC_TEMPLATE
FD_Fan_BLR_4_Steam | if([FD_Fan_BLR_4_Steam_raw]<500,0,[FD_Fan_BLR_4_Steam_raw]/1000) | 1 | GENERIC_TEMPLATE
BLR_5_HPS_Gen | [Fuel_BLR_5]*[LHV]/[Spec_En_Cons_BLR_5]*[BLR_5_Status]+(1-[BLR_5_Status])*[BLR_5_HPS_Gen_warmup] | 1 | GENERIC_TEMPLATE
Fuel_BLR_5 | [Fuel_BLR_5]*[BLR_5_Status] | 1 | GENERIC_TEMPLATE
FD_Fan_BLR_5_Steam | if([FD_Fan_BLR_5_Steam_raw]<500,0,[FD_Fan_BLR_5_Steam_raw]/1000) | 1 | GENERIC_TEMPLATE
Total_Boilers_Running | [BLR_1_Status] + [BLR_2_Status] + [BLR_3_Status] + [BLR_4_Status] + [BLR_5_Status] | 1 | GENERIC_TEMPLATE
Total_BLR_HPS_Generation | [BLR_1_HPS_Gen] + [BLR_2_HPS_Gen] + [BLR_3_HPS_Gen] + [BLR_4_HPS_Gen] + [BLR_5_HPS_Gen] | 1 | GENERIC_TEMPLATE
Total_Fuel_for_Boilers | [Fuel_BLR_1] + [Fuel_BLR_2] + [Fuel_BLR_3] + [Fuel_BLR_4] + [Fuel_BLR_5] | 1 | GENERIC_TEMPLATE

## derived_equation_post_optimizer
tag_name | formula_expression | active
BLR_1_Stack_Temp_C_clipped | if([BLR_1_Flue_O2_flag]==0,[BLR_1_Stack_Temp_C],min([BLR_1_Stack_Temp_C],(0.368798*[BLR_1_HPS_Gen]+0.356735*[BLR_1_Flue_O2_pct]+117.092))*[BLR_1_Status]) | 1
BLR_2_Stack_Temp_C_clipped | if([BLR_2_Flue_O2_flag]==0,[BLR_2_Stack_Temp_C],min([BLR_2_Stack_Temp_C],(0.446276*[BLR_2_HPS_Gen]+0.310062*[BLR_2_Flue_O2_pct]+110.239))*[BLR_2_Status]) | 1
BLR_3_Stack_Temp_C_clipped | if([BLR_3_Flue_O2_flag]==0,[BLR_3_Stack_Temp_C],min([BLR_3_Stack_Temp_C],(0.399051*[BLR_3_HPS_Gen]-0.176072*[BLR_3_Flue_O2_pct]+116.397))*[BLR_3_Status]) | 1
BLR_4_Stack_Temp_C_clipped | if([BLR_4_Flue_O2_flag]==0,[BLR_4_Stack_Temp_C],min([BLR_4_Stack_Temp_C],(0.39909*[BLR_4_HPS_Gen]-0.482676*[BLR_4_Flue_O2_pct]+114.659))*[BLR_4_Status]) | 1
BLR_5_Stack_Temp_C_clipped | if([BLR_5_Flue_O2_flag]==0,[BLR_5_Stack_Temp_C],min([BLR_5_Stack_Temp_C],(0.313556*[BLR_5_HPS_Gen]+0.475168*[BLR_5_Flue_O2_pct]+132.57))*[BLR_5_Status]) | 1

## constraints
system | expression | active | source_flag
Boilers | [BLR_1_HPS_Gen] >= 50*[BLR_1_Status] | 1 | GENERIC_TEMPLATE
Boilers | [Fuel_BLR_1] >= 0.000001*[BLR_1_Status] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_2_HPS_Gen] >= 50*[BLR_2_Status] | 1 | GENERIC_TEMPLATE
Boilers | [Fuel_BLR_2] >= 0.000001*[BLR_2_Status] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_3_HPS_Gen] >= 50*[BLR_3_Status] | 1 | GENERIC_TEMPLATE
Boilers | [Fuel_BLR_3] >= 0.000001*[BLR_3_Status] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_4_HPS_Gen] >= 50*[BLR_4_Status] | 1 | GENERIC_TEMPLATE
Boilers | [Fuel_BLR_4] >= 0.000001*[BLR_4_Status] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_5_HPS_Gen] >= 50*[BLR_5_Status] | 1 | GENERIC_TEMPLATE
Boilers | [Fuel_BLR_5] >= 0.000001*[BLR_5_Status] | 1 | GENERIC_TEMPLATE
Boilers | [Buffer_Steam_in_Boilers]+[Total_BLR_HPS_Generation] <= [BLR_1_Status]*[BLR_1_Capacity] + [BLR_2_Status]*[BLR_2_Capacity] + [BLR_3_Status]*[BLR_3_Capacity] + [BLR_4_Status]*[BLR_4_Capacity] + [BLR_5_Status]*[BLR_5_Capacity] | 1 | GENERIC_TEMPLATE
HP Steam | [Total_BLR_HPS_Generation]==[HP_Steam_Imbalance]+[HP_Steam_Consumption] | 1 | GENERIC_TEMPLATE

## inferred_tag_rm_block_mapping
model_id | tag_name | data_enrichment_inferred_calculation | post_optimizer_inferred_calculation | pre_optimizer_iterative_inferred | data_ingestion_seu_seec_inferred_calc | data_enrichment_peeo_adjusted_inferred | whatif_inferred
1 | BLR_1_HPS_Gen | 1
1 | Fuel_BLR_1 | 1
1 | BLR_1_Status | 1
1 | BLR_1_Capacity | 1
1 | Spec_En_Cons_BLR_1 | 1
1 | BLR_1_HPS_Gen_warmup | 1
1 | FD_Fan_BLR_1_Steam_reg | 1
1 | FD_Fan_BLR_1_Steam_warmup | 1
1 | FD_Fan_BLR_1_Steam | 1
1 | BLR_1_useful_heat_gj_h | 1
1 | BLR_1_fuel_input_gj_h | 1
1 | BLR_1_efficiency_pct | 1
1 | BLR_1_excess_air_pct | 1
1 | BLR_1_stack_loss_pct | 1
1 | BLR_1_indirect_efficiency_pct | 1
1 | BLR_1_sec_gj_per_t_steam | 1
1 | BLR_1_co2_t_per_h | 1
1 | BLR_1_fuel_cost_per_hr | 1
1 | BLR_2_HPS_Gen | 1
1 | Fuel_BLR_2 | 1
1 | BLR_2_Status | 1
1 | BLR_2_Capacity | 1
1 | Spec_En_Cons_BLR_2 | 1
1 | BLR_2_HPS_Gen_warmup | 1
1 | FD_Fan_BLR_2_Steam_reg | 1
1 | FD_Fan_BLR_2_Steam_warmup | 1
1 | FD_Fan_BLR_2_Steam | 1
1 | BLR_2_useful_heat_gj_h | 1
1 | BLR_2_fuel_input_gj_h | 1
1 | BLR_2_efficiency_pct | 1
1 | BLR_2_excess_air_pct | 1
1 | BLR_2_stack_loss_pct | 1
1 | BLR_2_indirect_efficiency_pct | 1
1 | BLR_2_sec_gj_per_t_steam | 1
1 | BLR_2_co2_t_per_h | 1
1 | BLR_2_fuel_cost_per_hr | 1
1 | BLR_3_HPS_Gen | 1
1 | Fuel_BLR_3 | 1
1 | BLR_3_Status | 1
1 | BLR_3_Capacity | 1
1 | Spec_En_Cons_BLR_3 | 1
1 | BLR_3_HPS_Gen_warmup | 1
1 | FD_Fan_BLR_3_Steam_reg | 1
1 | FD_Fan_BLR_3_Steam_warmup | 1
1 | FD_Fan_BLR_3_Steam | 1
1 | BLR_3_useful_heat_gj_h | 1
1 | BLR_3_fuel_input_gj_h | 1
1 | BLR_3_efficiency_pct | 1
1 | BLR_3_excess_air_pct | 1
1 | BLR_3_stack_loss_pct | 1
1 | BLR_3_indirect_efficiency_pct | 1
1 | BLR_3_sec_gj_per_t_steam | 1
1 | BLR_3_co2_t_per_h | 1
1 | BLR_3_fuel_cost_per_hr | 1
1 | BLR_4_HPS_Gen | 1
1 | Fuel_BLR_4 | 1
1 | BLR_4_Status | 1
1 | BLR_4_Capacity | 1
1 | Spec_En_Cons_BLR_4 | 1
1 | BLR_4_HPS_Gen_warmup | 1
1 | FD_Fan_BLR_4_Steam_reg | 1
1 | FD_Fan_BLR_4_Steam_warmup | 1
1 | FD_Fan_BLR_4_Steam | 1
1 | BLR_4_useful_heat_gj_h | 1
1 | BLR_4_fuel_input_gj_h | 1
1 | BLR_4_efficiency_pct | 1
1 | BLR_4_excess_air_pct | 1
1 | BLR_4_stack_loss_pct | 1
1 | BLR_4_indirect_efficiency_pct | 1
1 | BLR_4_sec_gj_per_t_steam | 1
1 | BLR_4_co2_t_per_h | 1
1 | BLR_4_fuel_cost_per_hr | 1
1 | BLR_5_HPS_Gen | 1
1 | Fuel_BLR_5 | 1
1 | BLR_5_Status | 1
1 | BLR_5_Capacity | 1
1 | Spec_En_Cons_BLR_5 | 1
1 | BLR_5_HPS_Gen_warmup | 1
1 | FD_Fan_BLR_5_Steam_reg | 1
1 | FD_Fan_BLR_5_Steam_warmup | 1
1 | FD_Fan_BLR_5_Steam | 1
1 | BLR_5_useful_heat_gj_h | 1
1 | BLR_5_fuel_input_gj_h | 1
1 | BLR_5_efficiency_pct | 1
1 | BLR_5_excess_air_pct | 1
1 | BLR_5_stack_loss_pct | 1
1 | BLR_5_indirect_efficiency_pct | 1
1 | BLR_5_sec_gj_per_t_steam | 1
1 | BLR_5_co2_t_per_h | 1
1 | BLR_5_fuel_cost_per_hr | 1
1 | Buffer_Steam_in_Boilers | 1
1 | Total_Boilers_Running | 1
1 | Total_BLR_HPS_Generation | 1
1 | Total_Fuel_for_Boilers | 1
1 | Boilers_Total_Fuel_Input_GJ_h | 1
1 | Boilers_Total_CO2_t_h | 1
1 | Boilers_Average_Efficiency_pct | 1
1 | Boilers_Specific_Energy_GJ_per_t | 1