## tag
tag_name | pi_name | tag_type | data_type
BLR_1_STEAM_FLOW_RAW | UN.UO.71FI1101.PV | pi | KG/HR
BLR_1_FUEL_GAS_FLOW | UN.UO.BO-7101A.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | KG/HR
BLR_1_FD_FAN_STEAM_RAW | UN.UO.71FI1108.PV | pi | KG/HR
BLR_1_STEAM_DRUM_PRESSURE | UN.UO.BO-71011.STEAM_DRUM_PRESSURE | pi | BARG
BLR_1_BFW_TO_ECONOMIZER | UN.UO.BO-71011.BFW_TO_ECONOMIZER | pi | KG/HR
BLR_1_BFW_TO_DESUPERHEATER | UN.UO.BO-71011.BFW_TO_DESUPERHEATER | pi | KG/HR
BLR_1_ECONOMIZER_OUTLET_TEMP | UN.UO.BO-71011.ECONOMIZER_OUTLET_TEMP | pi | C
BLR_1_ECONOMIZER_INLET_TEMP | UN.UO.BO-71011.ECONOMIZER_INLET_TEMP | pi | C
BLR_1_STACK_TEMPERATURE | UN.UO.BO-71011.STACK_TEMP | pi | C
BLR_1_COMBUSTION_AIR_TEMPERATURE | UN.UO.BO-71011.COMBUSTION_AIR_TEMP | pi | C
BLR_1_MAIN_FUEL_GAS_TEMPERATURE | UN.UO.BO-71011.FUEL_GAS_TEMP | pi | C
BLR_1_FLUE_GAS_OXYGEN | UN.UO.BO-71011.FLUE_O2_PCT | pi | MOLE%
BLR_1_CBD_BLOWDOWN | UN.UO.BO-71011.CBD_BLOWDOWN | pi | KG/HR
BLR_1_COMBUSTION_AIR_FLOW | UN.UO.BO-71011.COMBUSTION_AIR_FLOW | pi | KG/HR
BLR_1_SUPERHEATER_INLET_TEMP | UN.UO.BO-71011.SH_INLET_TEMP | pi | C
BLR_1_DESUPERHEATER_TEMPERATURE | UN.UO.BO-71011.DESUPERHEATER_TEMP | pi | C
BLR_1_DESUPERHEATER_OUTLET_TEMP | UN.UO.BO-71011.STEAM_T | pi | C
BLR_1_HP_STEAM_PRESSURE | UN.UO.BO-71011.STEAM_P | pi | BARG
BLR_2_STEAM_FLOW_RAW | UN.UO.71FI1201.PV | pi | KG/HR
BLR_2_FUEL_GAS_FLOW | UN.UO.BO-7101B.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | KG/HR
BLR_2_FD_FAN_STEAM_RAW | UN.UO.71FI1208.PV | pi | KG/HR
BLR_2_STEAM_DRUM_PRESSURE | UN.UO.BO-71012.STEAM_DRUM_PRESSURE | pi | BARG
BLR_2_BFW_TO_ECONOMIZER | UN.UO.BO-71012.BFW_TO_ECONOMIZER | pi | KG/HR
BLR_2_BFW_TO_DESUPERHEATER | UN.UO.BO-71012.BFW_TO_DESUPERHEATER | pi | KG/HR
BLR_2_ECONOMIZER_OUTLET_TEMP | UN.UO.BO-71012.ECONOMIZER_OUTLET_TEMP | pi | C
BLR_2_ECONOMIZER_INLET_TEMP | UN.UO.BO-71012.ECONOMIZER_INLET_TEMP | pi | C
BLR_2_STACK_TEMPERATURE | UN.UO.BO-71012.STACK_TEMP | pi | C
BLR_2_COMBUSTION_AIR_TEMPERATURE | UN.UO.BO-71012.COMBUSTION_AIR_TEMP | pi | C
BLR_2_MAIN_FUEL_GAS_TEMPERATURE | UN.UO.BO-71012.FUEL_GAS_TEMP | pi | C
BLR_2_FLUE_GAS_OXYGEN | UN.UO.BO-71012.FLUE_O2_PCT | pi | MOLE%
BLR_2_CBD_BLOWDOWN | UN.UO.BO-71012.CBD_BLOWDOWN | pi | KG/HR
BLR_2_COMBUSTION_AIR_FLOW | UN.UO.BO-71012.COMBUSTION_AIR_FLOW | pi | KG/HR
BLR_2_SUPERHEATER_INLET_TEMP | UN.UO.BO-71012.SH_INLET_TEMP | pi | C
BLR_2_DESUPERHEATER_TEMPERATURE | UN.UO.BO-71012.DESUPERHEATER_TEMP | pi | C
BLR_2_DESUPERHEATER_OUTLET_TEMP | UN.UO.BO-71012.STEAM_T | pi | C
BLR_2_HP_STEAM_PRESSURE | UN.UO.BO-71012.STEAM_P | pi | BARG
BLR_3_STEAM_FLOW_RAW | UN.UO.71FI1301.PV | pi | KG/HR
BLR_3_FUEL_GAS_FLOW | UN.UO.BO-7101C.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | KG/HR
BLR_3_FD_FAN_STEAM_RAW | UN.UO.71FI1308.PV | pi | KG/HR
BLR_3_STEAM_DRUM_PRESSURE | UN.UO.BO-71013.STEAM_DRUM_PRESSURE | pi | BARG
BLR_3_BFW_TO_ECONOMIZER | UN.UO.BO-71013.BFW_TO_ECONOMIZER | pi | KG/HR
BLR_3_BFW_TO_DESUPERHEATER | UN.UO.BO-71013.BFW_TO_DESUPERHEATER | pi | KG/HR
BLR_3_ECONOMIZER_OUTLET_TEMP | UN.UO.BO-71013.ECONOMIZER_OUTLET_TEMP | pi | C
BLR_3_ECONOMIZER_INLET_TEMP | UN.UO.BO-71013.ECONOMIZER_INLET_TEMP | pi | C
BLR_3_STACK_TEMPERATURE | UN.UO.BO-71013.STACK_TEMP | pi | C
BLR_3_COMBUSTION_AIR_TEMPERATURE | UN.UO.BO-71013.COMBUSTION_AIR_TEMP | pi | C
BLR_3_MAIN_FUEL_GAS_TEMPERATURE | UN.UO.BO-71013.FUEL_GAS_TEMP | pi | C
BLR_3_FLUE_GAS_OXYGEN | UN.UO.BO-71013.FLUE_O2_PCT | pi | MOLE%
BLR_3_CBD_BLOWDOWN | UN.UO.BO-71013.CBD_BLOWDOWN | pi | KG/HR
BLR_3_COMBUSTION_AIR_FLOW | UN.UO.BO-71013.COMBUSTION_AIR_FLOW | pi | KG/HR
BLR_3_SUPERHEATER_INLET_TEMP | UN.UO.BO-71013.SH_INLET_TEMP | pi | C
BLR_3_DESUPERHEATER_TEMPERATURE | UN.UO.BO-71013.DESUPERHEATER_TEMP | pi | C
BLR_3_DESUPERHEATER_OUTLET_TEMP | UN.UO.BO-71013.STEAM_T | pi | C
BLR_3_HP_STEAM_PRESSURE | UN.UO.BO-71013.STEAM_P | pi | BARG
BLR_4_STEAM_FLOW_RAW | UN.UO.71FI1401.PV | pi | KG/HR
BLR_4_FUEL_GAS_FLOW | UN.UO.BO-7101D.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | KG/HR
BLR_4_FD_FAN_STEAM_RAW | UN.UO.71FI1408.PV | pi | KG/HR
BLR_4_STEAM_DRUM_PRESSURE | UN.UO.BO-71014.STEAM_DRUM_PRESSURE | pi | BARG
BLR_4_BFW_TO_ECONOMIZER | UN.UO.BO-71014.BFW_TO_ECONOMIZER | pi | KG/HR
BLR_4_BFW_TO_DESUPERHEATER | UN.UO.BO-71014.BFW_TO_DESUPERHEATER | pi | KG/HR
BLR_4_ECONOMIZER_OUTLET_TEMP | UN.UO.BO-71014.ECONOMIZER_OUTLET_TEMP | pi | C
BLR_4_ECONOMIZER_INLET_TEMP | UN.UO.BO-71014.ECONOMIZER_INLET_TEMP | pi | C
BLR_4_STACK_TEMPERATURE | UN.UO.BO-71014.STACK_TEMP | pi | C
BLR_4_COMBUSTION_AIR_TEMPERATURE | UN.UO.BO-71014.COMBUSTION_AIR_TEMP | pi | C
BLR_4_MAIN_FUEL_GAS_TEMPERATURE | UN.UO.BO-71014.FUEL_GAS_TEMP | pi | C
BLR_4_FLUE_GAS_OXYGEN | UN.UO.BO-71014.FLUE_O2_PCT | pi | MOLE%
BLR_4_CBD_BLOWDOWN | UN.UO.BO-71014.CBD_BLOWDOWN | pi | KG/HR
BLR_4_COMBUSTION_AIR_FLOW | UN.UO.BO-71014.COMBUSTION_AIR_FLOW | pi | KG/HR
BLR_4_SUPERHEATER_INLET_TEMP | UN.UO.BO-71014.SH_INLET_TEMP | pi | C
BLR_4_DESUPERHEATER_TEMPERATURE | UN.UO.BO-71014.DESUPERHEATER_TEMP | pi | C
BLR_4_DESUPERHEATER_OUTLET_TEMP | UN.UO.BO-71014.STEAM_T | pi | C
BLR_4_HP_STEAM_PRESSURE | UN.UO.BO-71014.STEAM_P | pi | BARG
BLR_5_STEAM_FLOW_RAW | UN.UO.71FI1501A.PV | pi | KG/HR
BLR_5_FUEL_GAS_FLOW | UN.UO.PK-7104E.Boiler_Corrected_Fuel_Flow_PEEO_CALC_OUTPUT | pi | KG/HR
BLR_5_FD_FAN_STEAM_RAW | UN.UO.71FI1508.PV | pi | KG/HR
BLR_5_STEAM_DRUM_PRESSURE | UN.UO.BO-71015.STEAM_DRUM_PRESSURE | pi | BARG
BLR_5_BFW_TO_ECONOMIZER | UN.UO.BO-71015.BFW_TO_ECONOMIZER | pi | KG/HR
BLR_5_BFW_TO_DESUPERHEATER | UN.UO.BO-71015.BFW_TO_DESUPERHEATER | pi | KG/HR
BLR_5_ECONOMIZER_OUTLET_TEMP | UN.UO.BO-71015.ECONOMIZER_OUTLET_TEMP | pi | C
BLR_5_ECONOMIZER_INLET_TEMP | UN.UO.BO-71015.ECONOMIZER_INLET_TEMP | pi | C
BLR_5_STACK_TEMPERATURE | UN.UO.BO-71015.STACK_TEMP | pi | C
BLR_5_COMBUSTION_AIR_TEMPERATURE | UN.UO.BO-71015.COMBUSTION_AIR_TEMP | pi | C
BLR_5_MAIN_FUEL_GAS_TEMPERATURE | UN.UO.BO-71015.FUEL_GAS_TEMP | pi | C
BLR_5_FLUE_GAS_OXYGEN | UN.UO.BO-71015.FLUE_O2_PCT | pi | MOLE%
BLR_5_CBD_BLOWDOWN | UN.UO.BO-71015.CBD_BLOWDOWN | pi | KG/HR
BLR_5_COMBUSTION_AIR_FLOW | UN.UO.BO-71015.COMBUSTION_AIR_FLOW | pi | KG/HR
BLR_5_SUPERHEATER_INLET_TEMP | UN.UO.BO-71015.SH_INLET_TEMP | pi | C
BLR_5_DESUPERHEATER_TEMPERATURE | UN.UO.BO-71015.DESUPERHEATER_TEMP | pi | C
BLR_5_DESUPERHEATER_OUTLET_TEMP | UN.UO.BO-71015.STEAM_T | pi | C
BLR_5_HP_STEAM_PRESSURE | UN.UO.BO-71015.STEAM_P | pi | BARG
BLR_1_BOILER_LOAD |  | inferred
BLR_1_STATUS |  | inferred
BLR_1_FUEL_COMP_TOTAL |  | inferred
BLR_1_FG_NORM_CH4 |  | inferred
BLR_1_FG_NORM_ETHANE |  | inferred
BLR_1_FG_NORM_ETHYLENE |  | inferred
BLR_1_FG_NORM_PROPANE |  | inferred
BLR_1_FG_NORM_CO2 |  | inferred
BLR_1_FG_NORM_IC4 |  | inferred
BLR_1_FG_NORM_NC4 |  | inferred
BLR_1_FG_NORM_NC5 |  | inferred
BLR_1_FG_NORM_IC5 |  | inferred
BLR_1_FG_NORM_N2 |  | inferred
BLR_1_FG_NORM_H2 |  | inferred
BLR_1_FG_MW |  | inferred
BLR_1_FG_DENSITY |  | inferred
BLR_1_LHV_DESIGN |  | inferred
BLR_1_FG_CH4_MASS_PCT |  | inferred
BLR_1_FG_ETHANE_MASS_PCT |  | inferred
BLR_1_FG_ETHYLENE_MASS_PCT |  | inferred
BLR_1_FG_PROPANE_MASS_PCT |  | inferred
BLR_1_FG_N2_MASS_PCT |  | inferred
BLR_1_FG_H2_MASS_PCT |  | inferred
BLR_1_FG_IC4_MASS_PCT |  | inferred
BLR_1_FG_NC4_MASS_PCT |  | inferred
BLR_1_FG_NC5_MASS_PCT |  | inferred
BLR_1_FG_IC5_MASS_PCT |  | inferred
BLR_1_FG_CH4_MASS_FRAC |  | inferred
BLR_1_FG_ETHANE_MASS_FRAC |  | inferred
BLR_1_FG_ETHYLENE_MASS_FRAC |  | inferred
BLR_1_FG_PROPANE_MASS_FRAC |  | inferred
BLR_1_FG_N2_MASS_FRAC |  | inferred
BLR_1_FG_H2_MASS_FRAC |  | inferred
BLR_1_FG_IC4_MASS_FRAC |  | inferred
BLR_1_FG_NC4_MASS_FRAC |  | inferred
BLR_1_FG_NC5_MASS_FRAC |  | inferred
BLR_1_FG_IC5_MASS_FRAC |  | inferred
BLR_1_FG_FLOW_RATE_TPH |  | inferred
BLR_1_AIR_REQ_H2 |  | inferred
BLR_1_AIR_REQ_CH4 |  | inferred
BLR_1_AIR_REQ_ETHANE |  | inferred
BLR_1_AIR_REQ_ETHYLENE |  | inferred
BLR_1_AIR_REQ_PROPANE |  | inferred
BLR_1_AIR_REQ_NC4 |  | inferred
BLR_1_AIR_REQ_IC4 |  | inferred
BLR_1_AIR_REQ_NC5 |  | inferred
BLR_1_AIR_REQ_IC5 |  | inferred
BLR_1_CO2_COMB_H2 |  | inferred
BLR_1_CO2_COMB_CH4 |  | inferred
BLR_1_CO2_COMB_ETHANE |  | inferred
BLR_1_CO2_COMB_ETHYLENE |  | inferred
BLR_1_CO2_COMB_PROPANE |  | inferred
BLR_1_CO2_COMB_NC4 |  | inferred
BLR_1_CO2_COMB_IC4 |  | inferred
BLR_1_CO2_COMB_NC5 |  | inferred
BLR_1_CO2_COMB_IC5 |  | inferred
BLR_1_N2_COMB_H2 |  | inferred
BLR_1_N2_COMB_CH4 |  | inferred
BLR_1_N2_COMB_ETHANE |  | inferred
BLR_1_N2_COMB_ETHYLENE |  | inferred
BLR_1_N2_COMB_PROPANE |  | inferred
BLR_1_N2_COMB_IC4 |  | inferred
BLR_1_N2_COMB_NC4 |  | inferred
BLR_1_N2_COMB_IC5 |  | inferred
BLR_1_N2_COMB_NC5 |  | inferred
BLR_1_H2O_COMB_H2 |  | inferred
BLR_1_H2O_COMB_CH4 |  | inferred
BLR_1_H2O_COMB_ETHANE |  | inferred
BLR_1_H2O_COMB_ETHYLENE |  | inferred
BLR_1_H2O_COMB_PROPANE |  | inferred
BLR_1_H2O_COMB_IC4 |  | inferred
BLR_1_H2O_COMB_NC4 |  | inferred
BLR_1_H2O_COMB_IC5 |  | inferred
BLR_1_H2O_COMB_NC5 |  | inferred
BLR_1_AIR_REQ_COMPLETE |  | inferred
BLR_1_CO2_FORMED |  | inferred
BLR_1_N2_FORMED |  | inferred
BLR_1_H2O_FORMED |  | inferred
BLR_1_VAPOUR_PRESSURE_H2O |  | inferred
BLR_1_AIR_MOISTURE |  | inferred
BLR_1_CORRECTED_COMBUSTION_AIR |  | inferred
BLR_1_CORRECTED_H2O_FORMED |  | inferred
BLR_1_EXCESS_AIR |  | inferred
BLR_1_AIR_FUEL_MASS_RATIO |  | inferred
BLR_1_TOTAL_MOISTURE_WITH_AIR |  | inferred
BLR_1_TOTAL_H2O_PER_KG_FUEL |  | inferred
BLR_1_DRY_FLUE_GAS_RATIO |  | inferred
BLR_1_FLUE_GAS_RATIO |  | inferred
BLR_1_FLUE_GAS_MW |  | inferred
BLR_1_AIR_CP_REF_T |  | inferred
BLR_1_CP_AT_COMB_TEMP |  | inferred
BLR_1_AIR_CP_SENSIBLE_CORRECTED |  | inferred
BLR_1_CP_H2_FUEL_TEMP |  | inferred
BLR_1_CP_CH4_FUEL_TEMP |  | inferred
BLR_1_CP_ETHANE_FUEL_TEMP |  | inferred
BLR_1_CP_PROPANE_FUEL_TEMP |  | inferred
BLR_1_CP_ETHYLENE_FUEL_TEMP |  | inferred
BLR_1_CP_NC4_FUEL_TEMP |  | inferred
BLR_1_CP_IC4_FUEL_TEMP |  | inferred
BLR_1_CP_NC5_FUEL_TEMP |  | inferred
BLR_1_CP_IC5_FUEL_TEMP |  | inferred
BLR_1_CP_FUEL_AT_REF_TEMP |  | inferred
BLR_1_CP_FUEL_AT_FUEL_TEMP |  | inferred
BLR_1_AVG_CP_FUEL_SENSIBLE |  | inferred
BLR_1_CP_AIR_AT_STACK_TEMP |  | inferred
BLR_1_CP_FLUE_CO2_AT_STACK |  | inferred
BLR_1_CP_FLUE_H2O_AT_STACK |  | inferred
BLR_1_CP_FLUE_N2_AT_STACK |  | inferred
BLR_1_AVG_CP_FLUE_AT_STACK |  | inferred
BLR_1_CP_H2O_AT_STACK |  | inferred
BLR_1_SH_CORRECTION_FUEL |  | inferred
BLR_1_SH_CORRECTION_AIR |  | inferred
BLR_1_MIXED_LHV_PER_KG |  | inferred
BLR_1_TOTAL_HEAT_INPUT |  | inferred
BLR_1_HEAT_LOSS_L1 |  | inferred
BLR_1_HEAT_LOSS_L2 |  | inferred
BLR_1_HEAT_LOSS_L3 |  | inferred
BLR_1_HEAT_LOSS_L4 |  | inferred
BLR_1_TOTAL_STACK_LOSS_PER_KG |  | inferred
BLR_1_RADIATION_LOSSES |  | inferred
BLR_1_TOTAL_HEAT_LOSS |  | inferred
BLR_1_TOTAL_HEAT_ABSORBED |  | inferred
BLR_1_INDIRECT_EFFICIENCY |  | inferred
BLR_1_HP_STEAM_ENTHALPY |  | inferred
BLR_1_TOTAL_STEAM_ENERGY |  | inferred
BLR_1_BFW_ENTHALPY |  | inferred
BLR_1_CORRECTED_BFW_FLOW |  | inferred
BLR_1_BFW_ENERGY |  | inferred
BLR_1_FUEL_GAS_ENERGY_INPUT |  | inferred
BLR_1_STEAM_DRUM_TEMP |  | inferred
BLR_1_BLOWDOWN_LOSS |  | inferred
BLR_1_TOTAL_FLUE_GAS_GENERATED |  | inferred
BLR_1_STACK_LOSS |  | inferred
BLR_1_CORRECTED_FUEL_FLOW |  | inferred
BLR_1_FUEL_CONSUMPTION_GCAL |  | inferred
BLR_1_SEC_GCAL_T |  | inferred
BLR_1_SEC_GJ_T |  | inferred
BLR_1_CORRECTED_FUEL_ENERGY_INPUT |  | inferred
BLR_1_THERMAL_EFFICIENCY |  | inferred
BLR_1_FUEL_GAS_CORRECTED_TPH |  | inferred
BLR_1_TOTAL_FLUE_GAS_CORRECTED |  | inferred
BLR_1_STACK_LOSS_CORRECTED |  | inferred
BLR_1_BFW_STEAM_RATIO |  | inferred
BLR_1_CO2_EMISSIONS |  | inferred
BLR_1_CALCULATED_AIRFLOW_NM3H |  | inferred
BLR_1_STEAM_TO_FIRE_RATIO |  | inferred
BLR_1_ECONOMIZER_DUTY |  | inferred
BLR_1_LMTD_ECONOMIZER |  | inferred
BLR_1_UA_ECONOMIZER |  | inferred
BLR_1_FOULING_INDEX |  | inferred
BLR_1_SH_DUTY |  | inferred
BLR_1_SH_SPECIFIC_DUTY |  | inferred
BLR_1_SH_PERFORMANCE |  | inferred
BLR_1_ENERGY_GAINED |  | inferred
BLR_1_CONVECTION_DUTY |  | inferred
BLR_1_RADIATION_DUTY |  | inferred
BLR_1_PCT_DUTY_CONVECTION |  | inferred
BLR_1_PCT_DUTY_RADIANT |  | inferred
BLR_1_DUTY_RATIO_RAD_CONV |  | inferred
BLR_1_RADIATION_SECTION_EFF |  | inferred
BLR_1_CONVECTION_SECTION_EFF |  | inferred
BLR_1_HPS_GEN |  | inferred
BLR_1_FUEL_FLOW |  | inferred
BLR_1_CAPACITY |  | inferred
BLR_1_SPEC_EN_CONS |  | inferred
BLR_1_SPEC_EN_CONS_OPT |  | inferred
BLR_1_SPEC_EN_CONS_DEV |  | inferred
BLR_1_HPS_GEN_WARMUP |  | inferred
BLR_1_FD_FAN_STEAM_REG |  | inferred
BLR_1_FD_FAN_STEAM_WARMUP |  | inferred
BLR_1_FD_FAN_STEAM |  | inferred
BLR_2_BOILER_LOAD |  | inferred
BLR_2_STATUS |  | inferred
BLR_2_FUEL_COMP_TOTAL |  | inferred
BLR_2_FG_NORM_CH4 |  | inferred
BLR_2_FG_NORM_ETHANE |  | inferred
BLR_2_FG_NORM_ETHYLENE |  | inferred
BLR_2_FG_NORM_PROPANE |  | inferred
BLR_2_FG_NORM_CO2 |  | inferred
BLR_2_FG_NORM_IC4 |  | inferred
BLR_2_FG_NORM_NC4 |  | inferred
BLR_2_FG_NORM_NC5 |  | inferred
BLR_2_FG_NORM_IC5 |  | inferred
BLR_2_FG_NORM_N2 |  | inferred
BLR_2_FG_NORM_H2 |  | inferred
BLR_2_FG_MW |  | inferred
BLR_2_FG_DENSITY |  | inferred
BLR_2_LHV_DESIGN |  | inferred
BLR_2_FG_CH4_MASS_PCT |  | inferred
BLR_2_FG_ETHANE_MASS_PCT |  | inferred
BLR_2_FG_ETHYLENE_MASS_PCT |  | inferred
BLR_2_FG_PROPANE_MASS_PCT |  | inferred
BLR_2_FG_N2_MASS_PCT |  | inferred
BLR_2_FG_H2_MASS_PCT |  | inferred
BLR_2_FG_IC4_MASS_PCT |  | inferred
BLR_2_FG_NC4_MASS_PCT |  | inferred
BLR_2_FG_NC5_MASS_PCT |  | inferred
BLR_2_FG_IC5_MASS_PCT |  | inferred
BLR_2_FG_CH4_MASS_FRAC |  | inferred
BLR_2_FG_ETHANE_MASS_FRAC |  | inferred
BLR_2_FG_ETHYLENE_MASS_FRAC |  | inferred
BLR_2_FG_PROPANE_MASS_FRAC |  | inferred
BLR_2_FG_N2_MASS_FRAC |  | inferred
BLR_2_FG_H2_MASS_FRAC |  | inferred
BLR_2_FG_IC4_MASS_FRAC |  | inferred
BLR_2_FG_NC4_MASS_FRAC |  | inferred
BLR_2_FG_NC5_MASS_FRAC |  | inferred
BLR_2_FG_IC5_MASS_FRAC |  | inferred
BLR_2_FG_FLOW_RATE_TPH |  | inferred
BLR_2_AIR_REQ_H2 |  | inferred
BLR_2_AIR_REQ_CH4 |  | inferred
BLR_2_AIR_REQ_ETHANE |  | inferred
BLR_2_AIR_REQ_ETHYLENE |  | inferred
BLR_2_AIR_REQ_PROPANE |  | inferred
BLR_2_AIR_REQ_NC4 |  | inferred
BLR_2_AIR_REQ_IC4 |  | inferred
BLR_2_AIR_REQ_NC5 |  | inferred
BLR_2_AIR_REQ_IC5 |  | inferred
BLR_2_CO2_COMB_H2 |  | inferred
BLR_2_CO2_COMB_CH4 |  | inferred
BLR_2_CO2_COMB_ETHANE |  | inferred
BLR_2_CO2_COMB_ETHYLENE |  | inferred
BLR_2_CO2_COMB_PROPANE |  | inferred
BLR_2_CO2_COMB_NC4 |  | inferred
BLR_2_CO2_COMB_IC4 |  | inferred
BLR_2_CO2_COMB_NC5 |  | inferred
BLR_2_CO2_COMB_IC5 |  | inferred
BLR_2_N2_COMB_H2 |  | inferred
BLR_2_N2_COMB_CH4 |  | inferred
BLR_2_N2_COMB_ETHANE |  | inferred
BLR_2_N2_COMB_ETHYLENE |  | inferred
BLR_2_N2_COMB_PROPANE |  | inferred
BLR_2_N2_COMB_IC4 |  | inferred
BLR_2_N2_COMB_NC4 |  | inferred
BLR_2_N2_COMB_IC5 |  | inferred
BLR_2_N2_COMB_NC5 |  | inferred
BLR_2_H2O_COMB_H2 |  | inferred
BLR_2_H2O_COMB_CH4 |  | inferred
BLR_2_H2O_COMB_ETHANE |  | inferred
BLR_2_H2O_COMB_ETHYLENE |  | inferred
BLR_2_H2O_COMB_PROPANE |  | inferred
BLR_2_H2O_COMB_IC4 |  | inferred
BLR_2_H2O_COMB_NC4 |  | inferred
BLR_2_H2O_COMB_IC5 |  | inferred
BLR_2_H2O_COMB_NC5 |  | inferred
BLR_2_AIR_REQ_COMPLETE |  | inferred
BLR_2_CO2_FORMED |  | inferred
BLR_2_N2_FORMED |  | inferred
BLR_2_H2O_FORMED |  | inferred
BLR_2_VAPOUR_PRESSURE_H2O |  | inferred
BLR_2_AIR_MOISTURE |  | inferred
BLR_2_CORRECTED_COMBUSTION_AIR |  | inferred
BLR_2_CORRECTED_H2O_FORMED |  | inferred
BLR_2_EXCESS_AIR |  | inferred
BLR_2_AIR_FUEL_MASS_RATIO |  | inferred
BLR_2_TOTAL_MOISTURE_WITH_AIR |  | inferred
BLR_2_TOTAL_H2O_PER_KG_FUEL |  | inferred
BLR_2_DRY_FLUE_GAS_RATIO |  | inferred
BLR_2_FLUE_GAS_RATIO |  | inferred
BLR_2_FLUE_GAS_MW |  | inferred
BLR_2_AIR_CP_REF_T |  | inferred
BLR_2_CP_AT_COMB_TEMP |  | inferred
BLR_2_AIR_CP_SENSIBLE_CORRECTED |  | inferred
BLR_2_CP_H2_FUEL_TEMP |  | inferred
BLR_2_CP_CH4_FUEL_TEMP |  | inferred
BLR_2_CP_ETHANE_FUEL_TEMP |  | inferred
BLR_2_CP_PROPANE_FUEL_TEMP |  | inferred
BLR_2_CP_ETHYLENE_FUEL_TEMP |  | inferred
BLR_2_CP_NC4_FUEL_TEMP |  | inferred
BLR_2_CP_IC4_FUEL_TEMP |  | inferred
BLR_2_CP_NC5_FUEL_TEMP |  | inferred
BLR_2_CP_IC5_FUEL_TEMP |  | inferred
BLR_2_CP_FUEL_AT_REF_TEMP |  | inferred
BLR_2_CP_FUEL_AT_FUEL_TEMP |  | inferred
BLR_2_AVG_CP_FUEL_SENSIBLE |  | inferred
BLR_2_CP_AIR_AT_STACK_TEMP |  | inferred
BLR_2_CP_FLUE_CO2_AT_STACK |  | inferred
BLR_2_CP_FLUE_H2O_AT_STACK |  | inferred
BLR_2_CP_FLUE_N2_AT_STACK |  | inferred
BLR_2_AVG_CP_FLUE_AT_STACK |  | inferred
BLR_2_CP_H2O_AT_STACK |  | inferred
BLR_2_SH_CORRECTION_FUEL |  | inferred
BLR_2_SH_CORRECTION_AIR |  | inferred
BLR_2_MIXED_LHV_PER_KG |  | inferred
BLR_2_TOTAL_HEAT_INPUT |  | inferred
BLR_2_HEAT_LOSS_L1 |  | inferred
BLR_2_HEAT_LOSS_L2 |  | inferred
BLR_2_HEAT_LOSS_L3 |  | inferred
BLR_2_HEAT_LOSS_L4 |  | inferred
BLR_2_TOTAL_STACK_LOSS_PER_KG |  | inferred
BLR_2_RADIATION_LOSSES |  | inferred
BLR_2_TOTAL_HEAT_LOSS |  | inferred
BLR_2_TOTAL_HEAT_ABSORBED |  | inferred
BLR_2_INDIRECT_EFFICIENCY |  | inferred
BLR_2_HP_STEAM_ENTHALPY |  | inferred
BLR_2_TOTAL_STEAM_ENERGY |  | inferred
BLR_2_BFW_ENTHALPY |  | inferred
BLR_2_CORRECTED_BFW_FLOW |  | inferred
BLR_2_BFW_ENERGY |  | inferred
BLR_2_FUEL_GAS_ENERGY_INPUT |  | inferred
BLR_2_STEAM_DRUM_TEMP |  | inferred
BLR_2_BLOWDOWN_LOSS |  | inferred
BLR_2_TOTAL_FLUE_GAS_GENERATED |  | inferred
BLR_2_STACK_LOSS |  | inferred
BLR_2_CORRECTED_FUEL_FLOW |  | inferred
BLR_2_FUEL_CONSUMPTION_GCAL |  | inferred
BLR_2_SEC_GCAL_T |  | inferred
BLR_2_SEC_GJ_T |  | inferred
BLR_2_CORRECTED_FUEL_ENERGY_INPUT |  | inferred
BLR_2_THERMAL_EFFICIENCY |  | inferred
BLR_2_FUEL_GAS_CORRECTED_TPH |  | inferred
BLR_2_TOTAL_FLUE_GAS_CORRECTED |  | inferred
BLR_2_STACK_LOSS_CORRECTED |  | inferred
BLR_2_BFW_STEAM_RATIO |  | inferred
BLR_2_CO2_EMISSIONS |  | inferred
BLR_2_CALCULATED_AIRFLOW_NM3H |  | inferred
BLR_2_STEAM_TO_FIRE_RATIO |  | inferred
BLR_2_ECONOMIZER_DUTY |  | inferred
BLR_2_LMTD_ECONOMIZER |  | inferred
BLR_2_UA_ECONOMIZER |  | inferred
BLR_2_FOULING_INDEX |  | inferred
BLR_2_SH_DUTY |  | inferred
BLR_2_SH_SPECIFIC_DUTY |  | inferred
BLR_2_SH_PERFORMANCE |  | inferred
BLR_2_ENERGY_GAINED |  | inferred
BLR_2_CONVECTION_DUTY |  | inferred
BLR_2_RADIATION_DUTY |  | inferred
BLR_2_PCT_DUTY_CONVECTION |  | inferred
BLR_2_PCT_DUTY_RADIANT |  | inferred
BLR_2_DUTY_RATIO_RAD_CONV |  | inferred
BLR_2_RADIATION_SECTION_EFF |  | inferred
BLR_2_CONVECTION_SECTION_EFF |  | inferred
BLR_2_HPS_GEN |  | inferred
BLR_2_FUEL_FLOW |  | inferred
BLR_2_CAPACITY |  | inferred
BLR_2_SPEC_EN_CONS |  | inferred
BLR_2_SPEC_EN_CONS_OPT |  | inferred
BLR_2_SPEC_EN_CONS_DEV |  | inferred
BLR_2_HPS_GEN_WARMUP |  | inferred
BLR_2_FD_FAN_STEAM_REG |  | inferred
BLR_2_FD_FAN_STEAM_WARMUP |  | inferred
BLR_2_FD_FAN_STEAM |  | inferred
BLR_3_BOILER_LOAD |  | inferred
BLR_3_STATUS |  | inferred
BLR_3_FUEL_COMP_TOTAL |  | inferred
BLR_3_FG_NORM_CH4 |  | inferred
BLR_3_FG_NORM_ETHANE |  | inferred
BLR_3_FG_NORM_ETHYLENE |  | inferred
BLR_3_FG_NORM_PROPANE |  | inferred
BLR_3_FG_NORM_CO2 |  | inferred
BLR_3_FG_NORM_IC4 |  | inferred
BLR_3_FG_NORM_NC4 |  | inferred
BLR_3_FG_NORM_NC5 |  | inferred
BLR_3_FG_NORM_IC5 |  | inferred
BLR_3_FG_NORM_N2 |  | inferred
BLR_3_FG_NORM_H2 |  | inferred
BLR_3_FG_MW |  | inferred
BLR_3_FG_DENSITY |  | inferred
BLR_3_LHV_DESIGN |  | inferred
BLR_3_FG_CH4_MASS_PCT |  | inferred
BLR_3_FG_ETHANE_MASS_PCT |  | inferred
BLR_3_FG_ETHYLENE_MASS_PCT |  | inferred
BLR_3_FG_PROPANE_MASS_PCT |  | inferred
BLR_3_FG_N2_MASS_PCT |  | inferred
BLR_3_FG_H2_MASS_PCT |  | inferred
BLR_3_FG_IC4_MASS_PCT |  | inferred
BLR_3_FG_NC4_MASS_PCT |  | inferred
BLR_3_FG_NC5_MASS_PCT |  | inferred
BLR_3_FG_IC5_MASS_PCT |  | inferred
BLR_3_FG_CH4_MASS_FRAC |  | inferred
BLR_3_FG_ETHANE_MASS_FRAC |  | inferred
BLR_3_FG_ETHYLENE_MASS_FRAC |  | inferred
BLR_3_FG_PROPANE_MASS_FRAC |  | inferred
BLR_3_FG_N2_MASS_FRAC |  | inferred
BLR_3_FG_H2_MASS_FRAC |  | inferred
BLR_3_FG_IC4_MASS_FRAC |  | inferred
BLR_3_FG_NC4_MASS_FRAC |  | inferred
BLR_3_FG_NC5_MASS_FRAC |  | inferred
BLR_3_FG_IC5_MASS_FRAC |  | inferred
BLR_3_FG_FLOW_RATE_TPH |  | inferred
BLR_3_AIR_REQ_H2 |  | inferred
BLR_3_AIR_REQ_CH4 |  | inferred
BLR_3_AIR_REQ_ETHANE |  | inferred
BLR_3_AIR_REQ_ETHYLENE |  | inferred
BLR_3_AIR_REQ_PROPANE |  | inferred
BLR_3_AIR_REQ_NC4 |  | inferred
BLR_3_AIR_REQ_IC4 |  | inferred
BLR_3_AIR_REQ_NC5 |  | inferred
BLR_3_AIR_REQ_IC5 |  | inferred
BLR_3_CO2_COMB_H2 |  | inferred
BLR_3_CO2_COMB_CH4 |  | inferred
BLR_3_CO2_COMB_ETHANE |  | inferred
BLR_3_CO2_COMB_ETHYLENE |  | inferred
BLR_3_CO2_COMB_PROPANE |  | inferred
BLR_3_CO2_COMB_NC4 |  | inferred
BLR_3_CO2_COMB_IC4 |  | inferred
BLR_3_CO2_COMB_NC5 |  | inferred
BLR_3_CO2_COMB_IC5 |  | inferred
BLR_3_N2_COMB_H2 |  | inferred
BLR_3_N2_COMB_CH4 |  | inferred
BLR_3_N2_COMB_ETHANE |  | inferred
BLR_3_N2_COMB_ETHYLENE |  | inferred
BLR_3_N2_COMB_PROPANE |  | inferred
BLR_3_N2_COMB_IC4 |  | inferred
BLR_3_N2_COMB_NC4 |  | inferred
BLR_3_N2_COMB_IC5 |  | inferred
BLR_3_N2_COMB_NC5 |  | inferred
BLR_3_H2O_COMB_H2 |  | inferred
BLR_3_H2O_COMB_CH4 |  | inferred
BLR_3_H2O_COMB_ETHANE |  | inferred
BLR_3_H2O_COMB_ETHYLENE |  | inferred
BLR_3_H2O_COMB_PROPANE |  | inferred
BLR_3_H2O_COMB_IC4 |  | inferred
BLR_3_H2O_COMB_NC4 |  | inferred
BLR_3_H2O_COMB_IC5 |  | inferred
BLR_3_H2O_COMB_NC5 |  | inferred
BLR_3_AIR_REQ_COMPLETE |  | inferred
BLR_3_CO2_FORMED |  | inferred
BLR_3_N2_FORMED |  | inferred
BLR_3_H2O_FORMED |  | inferred
BLR_3_VAPOUR_PRESSURE_H2O |  | inferred
BLR_3_AIR_MOISTURE |  | inferred
BLR_3_CORRECTED_COMBUSTION_AIR |  | inferred
BLR_3_CORRECTED_H2O_FORMED |  | inferred
BLR_3_EXCESS_AIR |  | inferred
BLR_3_AIR_FUEL_MASS_RATIO |  | inferred
BLR_3_TOTAL_MOISTURE_WITH_AIR |  | inferred
BLR_3_TOTAL_H2O_PER_KG_FUEL |  | inferred
BLR_3_DRY_FLUE_GAS_RATIO |  | inferred
BLR_3_FLUE_GAS_RATIO |  | inferred
BLR_3_FLUE_GAS_MW |  | inferred
BLR_3_AIR_CP_REF_T |  | inferred
BLR_3_CP_AT_COMB_TEMP |  | inferred
BLR_3_AIR_CP_SENSIBLE_CORRECTED |  | inferred
BLR_3_CP_H2_FUEL_TEMP |  | inferred
BLR_3_CP_CH4_FUEL_TEMP |  | inferred
BLR_3_CP_ETHANE_FUEL_TEMP |  | inferred
BLR_3_CP_PROPANE_FUEL_TEMP |  | inferred
BLR_3_CP_ETHYLENE_FUEL_TEMP |  | inferred
BLR_3_CP_NC4_FUEL_TEMP |  | inferred
BLR_3_CP_IC4_FUEL_TEMP |  | inferred
BLR_3_CP_NC5_FUEL_TEMP |  | inferred
BLR_3_CP_IC5_FUEL_TEMP |  | inferred
BLR_3_CP_FUEL_AT_REF_TEMP |  | inferred
BLR_3_CP_FUEL_AT_FUEL_TEMP |  | inferred
BLR_3_AVG_CP_FUEL_SENSIBLE |  | inferred
BLR_3_CP_AIR_AT_STACK_TEMP |  | inferred
BLR_3_CP_FLUE_CO2_AT_STACK |  | inferred
BLR_3_CP_FLUE_H2O_AT_STACK |  | inferred
BLR_3_CP_FLUE_N2_AT_STACK |  | inferred
BLR_3_AVG_CP_FLUE_AT_STACK |  | inferred
BLR_3_CP_H2O_AT_STACK |  | inferred
BLR_3_SH_CORRECTION_FUEL |  | inferred
BLR_3_SH_CORRECTION_AIR |  | inferred
BLR_3_MIXED_LHV_PER_KG |  | inferred
BLR_3_TOTAL_HEAT_INPUT |  | inferred
BLR_3_HEAT_LOSS_L1 |  | inferred
BLR_3_HEAT_LOSS_L2 |  | inferred
BLR_3_HEAT_LOSS_L3 |  | inferred
BLR_3_HEAT_LOSS_L4 |  | inferred
BLR_3_TOTAL_STACK_LOSS_PER_KG |  | inferred
BLR_3_RADIATION_LOSSES |  | inferred
BLR_3_TOTAL_HEAT_LOSS |  | inferred
BLR_3_TOTAL_HEAT_ABSORBED |  | inferred
BLR_3_INDIRECT_EFFICIENCY |  | inferred
BLR_3_HP_STEAM_ENTHALPY |  | inferred
BLR_3_TOTAL_STEAM_ENERGY |  | inferred
BLR_3_BFW_ENTHALPY |  | inferred
BLR_3_CORRECTED_BFW_FLOW |  | inferred
BLR_3_BFW_ENERGY |  | inferred
BLR_3_FUEL_GAS_ENERGY_INPUT |  | inferred
BLR_3_STEAM_DRUM_TEMP |  | inferred
BLR_3_BLOWDOWN_LOSS |  | inferred
BLR_3_TOTAL_FLUE_GAS_GENERATED |  | inferred
BLR_3_STACK_LOSS |  | inferred
BLR_3_CORRECTED_FUEL_FLOW |  | inferred
BLR_3_FUEL_CONSUMPTION_GCAL |  | inferred
BLR_3_SEC_GCAL_T |  | inferred
BLR_3_SEC_GJ_T |  | inferred
BLR_3_CORRECTED_FUEL_ENERGY_INPUT |  | inferred
BLR_3_THERMAL_EFFICIENCY |  | inferred
BLR_3_FUEL_GAS_CORRECTED_TPH |  | inferred
BLR_3_TOTAL_FLUE_GAS_CORRECTED |  | inferred
BLR_3_STACK_LOSS_CORRECTED |  | inferred
BLR_3_BFW_STEAM_RATIO |  | inferred
BLR_3_CO2_EMISSIONS |  | inferred
BLR_3_CALCULATED_AIRFLOW_NM3H |  | inferred
BLR_3_STEAM_TO_FIRE_RATIO |  | inferred
BLR_3_ECONOMIZER_DUTY |  | inferred
BLR_3_LMTD_ECONOMIZER |  | inferred
BLR_3_UA_ECONOMIZER |  | inferred
BLR_3_FOULING_INDEX |  | inferred
BLR_3_SH_DUTY |  | inferred
BLR_3_SH_SPECIFIC_DUTY |  | inferred
BLR_3_SH_PERFORMANCE |  | inferred
BLR_3_ENERGY_GAINED |  | inferred
BLR_3_CONVECTION_DUTY |  | inferred
BLR_3_RADIATION_DUTY |  | inferred
BLR_3_PCT_DUTY_CONVECTION |  | inferred
BLR_3_PCT_DUTY_RADIANT |  | inferred
BLR_3_DUTY_RATIO_RAD_CONV |  | inferred
BLR_3_RADIATION_SECTION_EFF |  | inferred
BLR_3_CONVECTION_SECTION_EFF |  | inferred
BLR_3_HPS_GEN |  | inferred
BLR_3_FUEL_FLOW |  | inferred
BLR_3_CAPACITY |  | inferred
BLR_3_SPEC_EN_CONS |  | inferred
BLR_3_SPEC_EN_CONS_OPT |  | inferred
BLR_3_SPEC_EN_CONS_DEV |  | inferred
BLR_3_HPS_GEN_WARMUP |  | inferred
BLR_3_FD_FAN_STEAM_REG |  | inferred
BLR_3_FD_FAN_STEAM_WARMUP |  | inferred
BLR_3_FD_FAN_STEAM |  | inferred
BLR_4_BOILER_LOAD |  | inferred
BLR_4_STATUS |  | inferred
BLR_4_FUEL_COMP_TOTAL |  | inferred
BLR_4_FG_NORM_CH4 |  | inferred
BLR_4_FG_NORM_ETHANE |  | inferred
BLR_4_FG_NORM_ETHYLENE |  | inferred
BLR_4_FG_NORM_PROPANE |  | inferred
BLR_4_FG_NORM_CO2 |  | inferred
BLR_4_FG_NORM_IC4 |  | inferred
BLR_4_FG_NORM_NC4 |  | inferred
BLR_4_FG_NORM_NC5 |  | inferred
BLR_4_FG_NORM_IC5 |  | inferred
BLR_4_FG_NORM_N2 |  | inferred
BLR_4_FG_NORM_H2 |  | inferred
BLR_4_FG_MW |  | inferred
BLR_4_FG_DENSITY |  | inferred
BLR_4_LHV_DESIGN |  | inferred
BLR_4_FG_CH4_MASS_PCT |  | inferred
BLR_4_FG_ETHANE_MASS_PCT |  | inferred
BLR_4_FG_ETHYLENE_MASS_PCT |  | inferred
BLR_4_FG_PROPANE_MASS_PCT |  | inferred
BLR_4_FG_N2_MASS_PCT |  | inferred
BLR_4_FG_H2_MASS_PCT |  | inferred
BLR_4_FG_IC4_MASS_PCT |  | inferred
BLR_4_FG_NC4_MASS_PCT |  | inferred
BLR_4_FG_NC5_MASS_PCT |  | inferred
BLR_4_FG_IC5_MASS_PCT |  | inferred
BLR_4_FG_CH4_MASS_FRAC |  | inferred
BLR_4_FG_ETHANE_MASS_FRAC |  | inferred
BLR_4_FG_ETHYLENE_MASS_FRAC |  | inferred
BLR_4_FG_PROPANE_MASS_FRAC |  | inferred
BLR_4_FG_N2_MASS_FRAC |  | inferred
BLR_4_FG_H2_MASS_FRAC |  | inferred
BLR_4_FG_IC4_MASS_FRAC |  | inferred
BLR_4_FG_NC4_MASS_FRAC |  | inferred
BLR_4_FG_NC5_MASS_FRAC |  | inferred
BLR_4_FG_IC5_MASS_FRAC |  | inferred
BLR_4_FG_FLOW_RATE_TPH |  | inferred
BLR_4_AIR_REQ_H2 |  | inferred
BLR_4_AIR_REQ_CH4 |  | inferred
BLR_4_AIR_REQ_ETHANE |  | inferred
BLR_4_AIR_REQ_ETHYLENE |  | inferred
BLR_4_AIR_REQ_PROPANE |  | inferred
BLR_4_AIR_REQ_NC4 |  | inferred
BLR_4_AIR_REQ_IC4 |  | inferred
BLR_4_AIR_REQ_NC5 |  | inferred
BLR_4_AIR_REQ_IC5 |  | inferred
BLR_4_CO2_COMB_H2 |  | inferred
BLR_4_CO2_COMB_CH4 |  | inferred
BLR_4_CO2_COMB_ETHANE |  | inferred
BLR_4_CO2_COMB_ETHYLENE |  | inferred
BLR_4_CO2_COMB_PROPANE |  | inferred
BLR_4_CO2_COMB_NC4 |  | inferred
BLR_4_CO2_COMB_IC4 |  | inferred
BLR_4_CO2_COMB_NC5 |  | inferred
BLR_4_CO2_COMB_IC5 |  | inferred
BLR_4_N2_COMB_H2 |  | inferred
BLR_4_N2_COMB_CH4 |  | inferred
BLR_4_N2_COMB_ETHANE |  | inferred
BLR_4_N2_COMB_ETHYLENE |  | inferred
BLR_4_N2_COMB_PROPANE |  | inferred
BLR_4_N2_COMB_IC4 |  | inferred
BLR_4_N2_COMB_NC4 |  | inferred
BLR_4_N2_COMB_IC5 |  | inferred
BLR_4_N2_COMB_NC5 |  | inferred
BLR_4_H2O_COMB_H2 |  | inferred
BLR_4_H2O_COMB_CH4 |  | inferred
BLR_4_H2O_COMB_ETHANE |  | inferred
BLR_4_H2O_COMB_ETHYLENE |  | inferred
BLR_4_H2O_COMB_PROPANE |  | inferred
BLR_4_H2O_COMB_IC4 |  | inferred
BLR_4_H2O_COMB_NC4 |  | inferred
BLR_4_H2O_COMB_IC5 |  | inferred
BLR_4_H2O_COMB_NC5 |  | inferred
BLR_4_AIR_REQ_COMPLETE |  | inferred
BLR_4_CO2_FORMED |  | inferred
BLR_4_N2_FORMED |  | inferred
BLR_4_H2O_FORMED |  | inferred
BLR_4_VAPOUR_PRESSURE_H2O |  | inferred
BLR_4_AIR_MOISTURE |  | inferred
BLR_4_CORRECTED_COMBUSTION_AIR |  | inferred
BLR_4_CORRECTED_H2O_FORMED |  | inferred
BLR_4_EXCESS_AIR |  | inferred
BLR_4_AIR_FUEL_MASS_RATIO |  | inferred
BLR_4_TOTAL_MOISTURE_WITH_AIR |  | inferred
BLR_4_TOTAL_H2O_PER_KG_FUEL |  | inferred
BLR_4_DRY_FLUE_GAS_RATIO |  | inferred
BLR_4_FLUE_GAS_RATIO |  | inferred
BLR_4_FLUE_GAS_MW |  | inferred
BLR_4_AIR_CP_REF_T |  | inferred
BLR_4_CP_AT_COMB_TEMP |  | inferred
BLR_4_AIR_CP_SENSIBLE_CORRECTED |  | inferred
BLR_4_CP_H2_FUEL_TEMP |  | inferred
BLR_4_CP_CH4_FUEL_TEMP |  | inferred
BLR_4_CP_ETHANE_FUEL_TEMP |  | inferred
BLR_4_CP_PROPANE_FUEL_TEMP |  | inferred
BLR_4_CP_ETHYLENE_FUEL_TEMP |  | inferred
BLR_4_CP_NC4_FUEL_TEMP |  | inferred
BLR_4_CP_IC4_FUEL_TEMP |  | inferred
BLR_4_CP_NC5_FUEL_TEMP |  | inferred
BLR_4_CP_IC5_FUEL_TEMP |  | inferred
BLR_4_CP_FUEL_AT_REF_TEMP |  | inferred
BLR_4_CP_FUEL_AT_FUEL_TEMP |  | inferred
BLR_4_AVG_CP_FUEL_SENSIBLE |  | inferred
BLR_4_CP_AIR_AT_STACK_TEMP |  | inferred
BLR_4_CP_FLUE_CO2_AT_STACK |  | inferred
BLR_4_CP_FLUE_H2O_AT_STACK |  | inferred
BLR_4_CP_FLUE_N2_AT_STACK |  | inferred
BLR_4_AVG_CP_FLUE_AT_STACK |  | inferred
BLR_4_CP_H2O_AT_STACK |  | inferred
BLR_4_SH_CORRECTION_FUEL |  | inferred
BLR_4_SH_CORRECTION_AIR |  | inferred
BLR_4_MIXED_LHV_PER_KG |  | inferred
BLR_4_TOTAL_HEAT_INPUT |  | inferred
BLR_4_HEAT_LOSS_L1 |  | inferred
BLR_4_HEAT_LOSS_L2 |  | inferred
BLR_4_HEAT_LOSS_L3 |  | inferred
BLR_4_HEAT_LOSS_L4 |  | inferred
BLR_4_TOTAL_STACK_LOSS_PER_KG |  | inferred
BLR_4_RADIATION_LOSSES |  | inferred
BLR_4_TOTAL_HEAT_LOSS |  | inferred
BLR_4_TOTAL_HEAT_ABSORBED |  | inferred
BLR_4_INDIRECT_EFFICIENCY |  | inferred
BLR_4_HP_STEAM_ENTHALPY |  | inferred
BLR_4_TOTAL_STEAM_ENERGY |  | inferred
BLR_4_BFW_ENTHALPY |  | inferred
BLR_4_CORRECTED_BFW_FLOW |  | inferred
BLR_4_BFW_ENERGY |  | inferred
BLR_4_FUEL_GAS_ENERGY_INPUT |  | inferred
BLR_4_STEAM_DRUM_TEMP |  | inferred
BLR_4_BLOWDOWN_LOSS |  | inferred
BLR_4_TOTAL_FLUE_GAS_GENERATED |  | inferred
BLR_4_STACK_LOSS |  | inferred
BLR_4_CORRECTED_FUEL_FLOW |  | inferred
BLR_4_FUEL_CONSUMPTION_GCAL |  | inferred
BLR_4_SEC_GCAL_T |  | inferred
BLR_4_SEC_GJ_T |  | inferred
BLR_4_CORRECTED_FUEL_ENERGY_INPUT |  | inferred
BLR_4_THERMAL_EFFICIENCY |  | inferred
BLR_4_FUEL_GAS_CORRECTED_TPH |  | inferred
BLR_4_TOTAL_FLUE_GAS_CORRECTED |  | inferred
BLR_4_STACK_LOSS_CORRECTED |  | inferred
BLR_4_BFW_STEAM_RATIO |  | inferred
BLR_4_CO2_EMISSIONS |  | inferred
BLR_4_CALCULATED_AIRFLOW_NM3H |  | inferred
BLR_4_STEAM_TO_FIRE_RATIO |  | inferred
BLR_4_ECONOMIZER_DUTY |  | inferred
BLR_4_LMTD_ECONOMIZER |  | inferred
BLR_4_UA_ECONOMIZER |  | inferred
BLR_4_FOULING_INDEX |  | inferred
BLR_4_SH_DUTY |  | inferred
BLR_4_SH_SPECIFIC_DUTY |  | inferred
BLR_4_SH_PERFORMANCE |  | inferred
BLR_4_ENERGY_GAINED |  | inferred
BLR_4_CONVECTION_DUTY |  | inferred
BLR_4_RADIATION_DUTY |  | inferred
BLR_4_PCT_DUTY_CONVECTION |  | inferred
BLR_4_PCT_DUTY_RADIANT |  | inferred
BLR_4_DUTY_RATIO_RAD_CONV |  | inferred
BLR_4_RADIATION_SECTION_EFF |  | inferred
BLR_4_CONVECTION_SECTION_EFF |  | inferred
BLR_4_HPS_GEN |  | inferred
BLR_4_FUEL_FLOW |  | inferred
BLR_4_CAPACITY |  | inferred
BLR_4_SPEC_EN_CONS |  | inferred
BLR_4_SPEC_EN_CONS_OPT |  | inferred
BLR_4_SPEC_EN_CONS_DEV |  | inferred
BLR_4_HPS_GEN_WARMUP |  | inferred
BLR_4_FD_FAN_STEAM_REG |  | inferred
BLR_4_FD_FAN_STEAM_WARMUP |  | inferred
BLR_4_FD_FAN_STEAM |  | inferred
BLR_5_BOILER_LOAD |  | inferred
BLR_5_STATUS |  | inferred
BLR_5_FUEL_COMP_TOTAL |  | inferred
BLR_5_FG_NORM_CH4 |  | inferred
BLR_5_FG_NORM_ETHANE |  | inferred
BLR_5_FG_NORM_ETHYLENE |  | inferred
BLR_5_FG_NORM_PROPANE |  | inferred
BLR_5_FG_NORM_CO2 |  | inferred
BLR_5_FG_NORM_IC4 |  | inferred
BLR_5_FG_NORM_NC4 |  | inferred
BLR_5_FG_NORM_NC5 |  | inferred
BLR_5_FG_NORM_IC5 |  | inferred
BLR_5_FG_NORM_N2 |  | inferred
BLR_5_FG_NORM_H2 |  | inferred
BLR_5_FG_MW |  | inferred
BLR_5_FG_DENSITY |  | inferred
BLR_5_LHV_DESIGN |  | inferred
BLR_5_FG_CH4_MASS_PCT |  | inferred
BLR_5_FG_ETHANE_MASS_PCT |  | inferred
BLR_5_FG_ETHYLENE_MASS_PCT |  | inferred
BLR_5_FG_PROPANE_MASS_PCT |  | inferred
BLR_5_FG_N2_MASS_PCT |  | inferred
BLR_5_FG_H2_MASS_PCT |  | inferred
BLR_5_FG_IC4_MASS_PCT |  | inferred
BLR_5_FG_NC4_MASS_PCT |  | inferred
BLR_5_FG_NC5_MASS_PCT |  | inferred
BLR_5_FG_IC5_MASS_PCT |  | inferred
BLR_5_FG_CH4_MASS_FRAC |  | inferred
BLR_5_FG_ETHANE_MASS_FRAC |  | inferred
BLR_5_FG_ETHYLENE_MASS_FRAC |  | inferred
BLR_5_FG_PROPANE_MASS_FRAC |  | inferred
BLR_5_FG_N2_MASS_FRAC |  | inferred
BLR_5_FG_H2_MASS_FRAC |  | inferred
BLR_5_FG_IC4_MASS_FRAC |  | inferred
BLR_5_FG_NC4_MASS_FRAC |  | inferred
BLR_5_FG_NC5_MASS_FRAC |  | inferred
BLR_5_FG_IC5_MASS_FRAC |  | inferred
BLR_5_FG_FLOW_RATE_TPH |  | inferred
BLR_5_AIR_REQ_H2 |  | inferred
BLR_5_AIR_REQ_CH4 |  | inferred
BLR_5_AIR_REQ_ETHANE |  | inferred
BLR_5_AIR_REQ_ETHYLENE |  | inferred
BLR_5_AIR_REQ_PROPANE |  | inferred
BLR_5_AIR_REQ_NC4 |  | inferred
BLR_5_AIR_REQ_IC4 |  | inferred
BLR_5_AIR_REQ_NC5 |  | inferred
BLR_5_AIR_REQ_IC5 |  | inferred
BLR_5_CO2_COMB_H2 |  | inferred
BLR_5_CO2_COMB_CH4 |  | inferred
BLR_5_CO2_COMB_ETHANE |  | inferred
BLR_5_CO2_COMB_ETHYLENE |  | inferred
BLR_5_CO2_COMB_PROPANE |  | inferred
BLR_5_CO2_COMB_NC4 |  | inferred
BLR_5_CO2_COMB_IC4 |  | inferred
BLR_5_CO2_COMB_NC5 |  | inferred
BLR_5_CO2_COMB_IC5 |  | inferred
BLR_5_N2_COMB_H2 |  | inferred
BLR_5_N2_COMB_CH4 |  | inferred
BLR_5_N2_COMB_ETHANE |  | inferred
BLR_5_N2_COMB_ETHYLENE |  | inferred
BLR_5_N2_COMB_PROPANE |  | inferred
BLR_5_N2_COMB_IC4 |  | inferred
BLR_5_N2_COMB_NC4 |  | inferred
BLR_5_N2_COMB_IC5 |  | inferred
BLR_5_N2_COMB_NC5 |  | inferred
BLR_5_H2O_COMB_H2 |  | inferred
BLR_5_H2O_COMB_CH4 |  | inferred
BLR_5_H2O_COMB_ETHANE |  | inferred
BLR_5_H2O_COMB_ETHYLENE |  | inferred
BLR_5_H2O_COMB_PROPANE |  | inferred
BLR_5_H2O_COMB_IC4 |  | inferred
BLR_5_H2O_COMB_NC4 |  | inferred
BLR_5_H2O_COMB_IC5 |  | inferred
BLR_5_H2O_COMB_NC5 |  | inferred
BLR_5_AIR_REQ_COMPLETE |  | inferred
BLR_5_CO2_FORMED |  | inferred
BLR_5_N2_FORMED |  | inferred
BLR_5_H2O_FORMED |  | inferred
BLR_5_VAPOUR_PRESSURE_H2O |  | inferred
BLR_5_AIR_MOISTURE |  | inferred
BLR_5_CORRECTED_COMBUSTION_AIR |  | inferred
BLR_5_CORRECTED_H2O_FORMED |  | inferred
BLR_5_EXCESS_AIR |  | inferred
BLR_5_AIR_FUEL_MASS_RATIO |  | inferred
BLR_5_TOTAL_MOISTURE_WITH_AIR |  | inferred
BLR_5_TOTAL_H2O_PER_KG_FUEL |  | inferred
BLR_5_DRY_FLUE_GAS_RATIO |  | inferred
BLR_5_FLUE_GAS_RATIO |  | inferred
BLR_5_FLUE_GAS_MW |  | inferred
BLR_5_AIR_CP_REF_T |  | inferred
BLR_5_CP_AT_COMB_TEMP |  | inferred
BLR_5_AIR_CP_SENSIBLE_CORRECTED |  | inferred
BLR_5_CP_H2_FUEL_TEMP |  | inferred
BLR_5_CP_CH4_FUEL_TEMP |  | inferred
BLR_5_CP_ETHANE_FUEL_TEMP |  | inferred
BLR_5_CP_PROPANE_FUEL_TEMP |  | inferred
BLR_5_CP_ETHYLENE_FUEL_TEMP |  | inferred
BLR_5_CP_NC4_FUEL_TEMP |  | inferred
BLR_5_CP_IC4_FUEL_TEMP |  | inferred
BLR_5_CP_NC5_FUEL_TEMP |  | inferred
BLR_5_CP_IC5_FUEL_TEMP |  | inferred
BLR_5_CP_FUEL_AT_REF_TEMP |  | inferred
BLR_5_CP_FUEL_AT_FUEL_TEMP |  | inferred
BLR_5_AVG_CP_FUEL_SENSIBLE |  | inferred
BLR_5_CP_AIR_AT_STACK_TEMP |  | inferred
BLR_5_CP_FLUE_CO2_AT_STACK |  | inferred
BLR_5_CP_FLUE_H2O_AT_STACK |  | inferred
BLR_5_CP_FLUE_N2_AT_STACK |  | inferred
BLR_5_AVG_CP_FLUE_AT_STACK |  | inferred
BLR_5_CP_H2O_AT_STACK |  | inferred
BLR_5_SH_CORRECTION_FUEL |  | inferred
BLR_5_SH_CORRECTION_AIR |  | inferred
BLR_5_MIXED_LHV_PER_KG |  | inferred
BLR_5_TOTAL_HEAT_INPUT |  | inferred
BLR_5_HEAT_LOSS_L1 |  | inferred
BLR_5_HEAT_LOSS_L2 |  | inferred
BLR_5_HEAT_LOSS_L3 |  | inferred
BLR_5_HEAT_LOSS_L4 |  | inferred
BLR_5_TOTAL_STACK_LOSS_PER_KG |  | inferred
BLR_5_RADIATION_LOSSES |  | inferred
BLR_5_TOTAL_HEAT_LOSS |  | inferred
BLR_5_TOTAL_HEAT_ABSORBED |  | inferred
BLR_5_INDIRECT_EFFICIENCY |  | inferred
BLR_5_HP_STEAM_ENTHALPY |  | inferred
BLR_5_TOTAL_STEAM_ENERGY |  | inferred
BLR_5_BFW_ENTHALPY |  | inferred
BLR_5_CORRECTED_BFW_FLOW |  | inferred
BLR_5_BFW_ENERGY |  | inferred
BLR_5_FUEL_GAS_ENERGY_INPUT |  | inferred
BLR_5_STEAM_DRUM_TEMP |  | inferred
BLR_5_BLOWDOWN_LOSS |  | inferred
BLR_5_TOTAL_FLUE_GAS_GENERATED |  | inferred
BLR_5_STACK_LOSS |  | inferred
BLR_5_CORRECTED_FUEL_FLOW |  | inferred
BLR_5_FUEL_CONSUMPTION_GCAL |  | inferred
BLR_5_SEC_GCAL_T |  | inferred
BLR_5_SEC_GJ_T |  | inferred
BLR_5_CORRECTED_FUEL_ENERGY_INPUT |  | inferred
BLR_5_THERMAL_EFFICIENCY |  | inferred
BLR_5_FUEL_GAS_CORRECTED_TPH |  | inferred
BLR_5_TOTAL_FLUE_GAS_CORRECTED |  | inferred
BLR_5_STACK_LOSS_CORRECTED |  | inferred
BLR_5_BFW_STEAM_RATIO |  | inferred
BLR_5_CO2_EMISSIONS |  | inferred
BLR_5_CALCULATED_AIRFLOW_NM3H |  | inferred
BLR_5_STEAM_TO_FIRE_RATIO |  | inferred
BLR_5_ECONOMIZER_DUTY |  | inferred
BLR_5_LMTD_ECONOMIZER |  | inferred
BLR_5_UA_ECONOMIZER |  | inferred
BLR_5_FOULING_INDEX |  | inferred
BLR_5_SH_DUTY |  | inferred
BLR_5_SH_SPECIFIC_DUTY |  | inferred
BLR_5_SH_PERFORMANCE |  | inferred
BLR_5_ENERGY_GAINED |  | inferred
BLR_5_CONVECTION_DUTY |  | inferred
BLR_5_RADIATION_DUTY |  | inferred
BLR_5_PCT_DUTY_CONVECTION |  | inferred
BLR_5_PCT_DUTY_RADIANT |  | inferred
BLR_5_DUTY_RATIO_RAD_CONV |  | inferred
BLR_5_RADIATION_SECTION_EFF |  | inferred
BLR_5_CONVECTION_SECTION_EFF |  | inferred
BLR_5_HPS_GEN |  | inferred
BLR_5_FUEL_FLOW |  | inferred
BLR_5_CAPACITY |  | inferred
BLR_5_SPEC_EN_CONS |  | inferred
BLR_5_SPEC_EN_CONS_OPT |  | inferred
BLR_5_SPEC_EN_CONS_DEV |  | inferred
BLR_5_HPS_GEN_WARMUP |  | inferred
BLR_5_FD_FAN_STEAM_REG |  | inferred
BLR_5_FD_FAN_STEAM_WARMUP |  | inferred
BLR_5_FD_FAN_STEAM |  | inferred
BLR_1_STATUS |  | inferred
BLR_1_HPS_GEN |  | inferred
BLR_1_FUEL_FLOW |  | inferred
BLR_1_FD_FAN_STEAM |  | inferred
BLR_2_STATUS |  | inferred
BLR_2_HPS_GEN |  | inferred
BLR_2_FUEL_FLOW |  | inferred
BLR_2_FD_FAN_STEAM |  | inferred
BLR_3_STATUS |  | inferred
BLR_3_HPS_GEN |  | inferred
BLR_3_FUEL_FLOW |  | inferred
BLR_3_FD_FAN_STEAM |  | inferred
BLR_4_STATUS |  | inferred
BLR_4_HPS_GEN |  | inferred
BLR_4_FUEL_FLOW |  | inferred
BLR_4_FD_FAN_STEAM |  | inferred
BLR_5_STATUS |  | inferred
BLR_5_HPS_GEN |  | inferred
BLR_5_FUEL_FLOW |  | inferred
BLR_5_FD_FAN_STEAM |  | inferred

## master_pi_data
time_stamp | BLR_1_STEAM_FLOW_RAW | BLR_1_FUEL_GAS_FLOW | BLR_1_FD_FAN_STEAM_RAW | BLR_1_STEAM_DRUM_PRESSURE | BLR_1_BFW_TO_ECONOMIZER | BLR_1_BFW_TO_DESUPERHEATER | BLR_1_ECONOMIZER_OUTLET_TEMP | BLR_1_ECONOMIZER_INLET_TEMP | BLR_1_STACK_TEMPERATURE | BLR_1_COMBUSTION_AIR_TEMPERATURE | BLR_1_MAIN_FUEL_GAS_TEMPERATURE | BLR_1_FLUE_GAS_OXYGEN | BLR_1_CBD_BLOWDOWN | BLR_1_COMBUSTION_AIR_FLOW | BLR_1_SUPERHEATER_INLET_TEMP | BLR_1_DESUPERHEATER_TEMPERATURE | BLR_1_DESUPERHEATER_OUTLET_TEMP | BLR_1_HP_STEAM_PRESSURE | BLR_2_STEAM_FLOW_RAW | BLR_2_FUEL_GAS_FLOW | BLR_2_FD_FAN_STEAM_RAW | BLR_2_STEAM_DRUM_PRESSURE | BLR_2_BFW_TO_ECONOMIZER | BLR_2_BFW_TO_DESUPERHEATER | BLR_2_ECONOMIZER_OUTLET_TEMP | BLR_2_ECONOMIZER_INLET_TEMP | BLR_2_STACK_TEMPERATURE | BLR_2_COMBUSTION_AIR_TEMPERATURE | BLR_2_MAIN_FUEL_GAS_TEMPERATURE | BLR_2_FLUE_GAS_OXYGEN | BLR_2_CBD_BLOWDOWN | BLR_2_COMBUSTION_AIR_FLOW | BLR_2_SUPERHEATER_INLET_TEMP | BLR_2_DESUPERHEATER_TEMPERATURE | BLR_2_DESUPERHEATER_OUTLET_TEMP | BLR_2_HP_STEAM_PRESSURE | BLR_3_STEAM_FLOW_RAW | BLR_3_FUEL_GAS_FLOW | BLR_3_FD_FAN_STEAM_RAW | BLR_3_STEAM_DRUM_PRESSURE | BLR_3_BFW_TO_ECONOMIZER | BLR_3_BFW_TO_DESUPERHEATER | BLR_3_ECONOMIZER_OUTLET_TEMP | BLR_3_ECONOMIZER_INLET_TEMP | BLR_3_STACK_TEMPERATURE | BLR_3_COMBUSTION_AIR_TEMPERATURE | BLR_3_MAIN_FUEL_GAS_TEMPERATURE | BLR_3_FLUE_GAS_OXYGEN | BLR_3_CBD_BLOWDOWN | BLR_3_COMBUSTION_AIR_FLOW | BLR_3_SUPERHEATER_INLET_TEMP | BLR_3_DESUPERHEATER_TEMPERATURE | BLR_3_DESUPERHEATER_OUTLET_TEMP | BLR_3_HP_STEAM_PRESSURE | BLR_4_STEAM_FLOW_RAW | BLR_4_FUEL_GAS_FLOW | BLR_4_FD_FAN_STEAM_RAW | BLR_4_STEAM_DRUM_PRESSURE | BLR_4_BFW_TO_ECONOMIZER | BLR_4_BFW_TO_DESUPERHEATER | BLR_4_ECONOMIZER_OUTLET_TEMP | BLR_4_ECONOMIZER_INLET_TEMP | BLR_4_STACK_TEMPERATURE | BLR_4_COMBUSTION_AIR_TEMPERATURE | BLR_4_MAIN_FUEL_GAS_TEMPERATURE | BLR_4_FLUE_GAS_OXYGEN | BLR_4_CBD_BLOWDOWN | BLR_4_COMBUSTION_AIR_FLOW | BLR_4_SUPERHEATER_INLET_TEMP | BLR_4_DESUPERHEATER_TEMPERATURE | BLR_4_DESUPERHEATER_OUTLET_TEMP | BLR_4_HP_STEAM_PRESSURE | BLR_5_STEAM_FLOW_RAW | BLR_5_FUEL_GAS_FLOW | BLR_5_FD_FAN_STEAM_RAW | BLR_5_STEAM_DRUM_PRESSURE | BLR_5_BFW_TO_ECONOMIZER | BLR_5_BFW_TO_DESUPERHEATER | BLR_5_ECONOMIZER_OUTLET_TEMP | BLR_5_ECONOMIZER_INLET_TEMP | BLR_5_STACK_TEMPERATURE | BLR_5_COMBUSTION_AIR_TEMPERATURE | BLR_5_MAIN_FUEL_GAS_TEMPERATURE | BLR_5_FLUE_GAS_OXYGEN | BLR_5_CBD_BLOWDOWN | BLR_5_COMBUSTION_AIR_FLOW | BLR_5_SUPERHEATER_INLET_TEMP | BLR_5_DESUPERHEATER_TEMPERATURE | BLR_5_DESUPERHEATER_OUTLET_TEMP | BLR_5_HP_STEAM_PRESSURE
2026-05-07 08:54

## inferred
tag_name | formula_expression
BLR_1_BOILER_LOAD | [BLR_1_STEAM_FLOW_RAW]/150000*100
BLR_1_STATUS | if([BLR_1_BOILER_LOAD]>25&&[BLR_1_DESUPERHEATER_OUTLET_TEMP]>370&&[BLR_1_HP_STEAM_PRESSURE]>40,1,0)
BLR_1_FUEL_COMP_TOTAL | ([UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]+[UN.UO.BOILER_FG_CH4_CONCENTRATION]+[UN.UO.BOILER_FG_ETHANE_CONCENTRATION]+[UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]+[UN.UO.BOILER_FG_PROPANE_CONCENTRATION]+[UN.UO.BOILER_FG_NC4_CONCENTRATION]+[UN.UO.BOILER_FG_IC4_CONCENTRATION]+[UN.UO.BOILER_FG_NC5_CONCENTRATION]+[UN.UO.BOILER_FG_IC5_CONCENTRATION]+[UN.UO.BOILER_FG_N2_CONCENTRATION])
BLR_1_FG_NORM_CH4 | [UN.UO.BOILER_FG_CH4_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_ETHANE | [UN.UO.BOILER_FG_ETHANE_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_ETHYLENE | [UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_PROPANE | [UN.UO.BOILER_FG_PROPANE_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_CO2 | 0
BLR_1_FG_NORM_IC4 | [UN.UO.BOILER_FG_IC4_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_NC4 | [UN.UO.BOILER_FG_NC4_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_NC5 | [UN.UO.BOILER_FG_NC5_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_IC5 | [UN.UO.BOILER_FG_IC5_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_N2 | [UN.UO.BOILER_FG_N2_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_NORM_H2 | [UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]/[BLR_1_FUEL_COMP_TOTAL]*100
BLR_1_FG_MW | ([BLR_1_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]+[BLR_1_FG_NORM_CH4]*[COMPONENT_METHANE_MW]+[BLR_1_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]+[BLR_1_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]+[BLR_1_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]+[BLR_1_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]+[BLR_1_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]+[BLR_1_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]+[BLR_1_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]+[BLR_1_FG_NORM_N2]*[COMPONENT_NITROGEN_MW])/100
BLR_1_FG_DENSITY | [BLR_1_FG_MW]/22.414
BLR_1_LHV_DESIGN | ([LHV_FG]/[BLR_1_FG_DENSITY])/1000
BLR_1_FG_CH4_MASS_PCT | [BLR_1_FG_NORM_CH4]*[COMPONENT_METHANE_MW]/[BLR_1_FG_MW]
BLR_1_FG_ETHANE_MASS_PCT | [BLR_1_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]/[BLR_1_FG_MW]
BLR_1_FG_ETHYLENE_MASS_PCT | [BLR_1_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]/[BLR_1_FG_MW]
BLR_1_FG_PROPANE_MASS_PCT | [BLR_1_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]/[BLR_1_FG_MW]
BLR_1_FG_N2_MASS_PCT | [BLR_1_FG_NORM_N2]*[COMPONENT_NITROGEN_MW]/[BLR_1_FG_MW]
BLR_1_FG_H2_MASS_PCT | [BLR_1_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]/[BLR_1_FG_MW]
BLR_1_FG_IC4_MASS_PCT | [BLR_1_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]/[BLR_1_FG_MW]
BLR_1_FG_NC4_MASS_PCT | [BLR_1_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]/[BLR_1_FG_MW]
BLR_1_FG_NC5_MASS_PCT | [BLR_1_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]/[BLR_1_FG_MW]
BLR_1_FG_IC5_MASS_PCT | [BLR_1_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]/[BLR_1_FG_MW]
BLR_1_FG_CH4_MASS_FRAC | [BLR_1_FG_CH4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_ETHANE_MASS_FRAC | [BLR_1_FG_ETHANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_ETHYLENE_MASS_FRAC | [BLR_1_FG_ETHYLENE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_PROPANE_MASS_FRAC | [BLR_1_FG_PROPANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_N2_MASS_FRAC | [BLR_1_FG_N2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_H2_MASS_FRAC | [BLR_1_FG_H2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_IC4_MASS_FRAC | [BLR_1_FG_IC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_NC4_MASS_FRAC | [BLR_1_FG_NC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_NC5_MASS_FRAC | [BLR_1_FG_NC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_IC5_MASS_FRAC | [BLR_1_FG_IC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_1_FG_FLOW_RATE_TPH | [BLR_1_FUEL_GAS_FLOW]/1000
BLR_1_AIR_REQ_H2 | [BLR_1_FG_H2_MASS_FRAC]*34.344
BLR_1_AIR_REQ_CH4 | [BLR_1_FG_CH4_MASS_FRAC]*17.265
BLR_1_AIR_REQ_ETHANE | [BLR_1_FG_ETHANE_MASS_FRAC]*16.119
BLR_1_AIR_REQ_ETHYLENE | [BLR_1_FG_ETHYLENE_MASS_FRAC]*14.807
BLR_1_AIR_REQ_PROPANE | [BLR_1_FG_PROPANE_MASS_FRAC]*15.703
BLR_1_AIR_REQ_NC4 | [BLR_1_FG_NC4_MASS_FRAC]*15.487
BLR_1_AIR_REQ_IC4 | [BLR_1_FG_IC4_MASS_FRAC]*15.487
BLR_1_AIR_REQ_NC5 | [BLR_1_FG_NC5_MASS_FRAC]*15.353
BLR_1_AIR_REQ_IC5 | [BLR_1_FG_IC5_MASS_FRAC]*15.353
BLR_1_CO2_COMB_H2 | [BLR_1_FG_H2_MASS_FRAC]*0
BLR_1_CO2_COMB_CH4 | [BLR_1_FG_CH4_MASS_FRAC]*2.744
BLR_1_CO2_COMB_ETHANE | [BLR_1_FG_ETHANE_MASS_FRAC]*2.927
BLR_1_CO2_COMB_ETHYLENE | [BLR_1_FG_ETHYLENE_MASS_FRAC]*3.138
BLR_1_CO2_COMB_PROPANE | [BLR_1_FG_PROPANE_MASS_FRAC]*2.994
BLR_1_CO2_COMB_NC4 | [BLR_1_FG_NC4_MASS_FRAC]*3.029
BLR_1_CO2_COMB_IC4 | [BLR_1_FG_IC4_MASS_FRAC]*3.029
BLR_1_CO2_COMB_NC5 | [BLR_1_FG_NC5_MASS_FRAC]*3.05
BLR_1_CO2_COMB_IC5 | [BLR_1_FG_IC5_MASS_FRAC]*3.05
BLR_1_N2_COMB_H2 | [BLR_1_FG_H2_MASS_FRAC]*26.407
BLR_1_N2_COMB_CH4 | [BLR_1_FG_CH4_MASS_FRAC]*13.275
BLR_1_N2_COMB_ETHANE | [BLR_1_FG_ETHANE_MASS_FRAC]*12.394
BLR_1_N2_COMB_ETHYLENE | [BLR_1_FG_ETHYLENE_MASS_FRAC]*11.385
BLR_1_N2_COMB_PROPANE | [BLR_1_FG_PROPANE_MASS_FRAC]*12.074
BLR_1_N2_COMB_IC4 | [BLR_1_FG_IC4_MASS_FRAC]*11.908
BLR_1_N2_COMB_NC4 | [BLR_1_FG_NC4_MASS_FRAC]*11.908
BLR_1_N2_COMB_IC5 | [BLR_1_FG_IC5_MASS_FRAC]*11.805
BLR_1_N2_COMB_NC5 | [BLR_1_FG_NC5_MASS_FRAC]*11.805
BLR_1_H2O_COMB_H2 | [BLR_1_FG_H2_MASS_FRAC]*8.937
BLR_1_H2O_COMB_CH4 | [BLR_1_FG_CH4_MASS_FRAC]*2.246
BLR_1_H2O_COMB_ETHANE | [BLR_1_FG_ETHANE_MASS_FRAC]*1.798
BLR_1_H2O_COMB_ETHYLENE | [BLR_1_FG_ETHYLENE_MASS_FRAC]*1.285
BLR_1_H2O_COMB_PROPANE | [BLR_1_FG_PROPANE_MASS_FRAC]*1.634
BLR_1_H2O_COMB_IC4 | [BLR_1_FG_NC4_MASS_FRAC]*1.55
BLR_1_H2O_COMB_NC4 | [BLR_1_FG_IC4_MASS_FRAC]*1.55
BLR_1_H2O_COMB_IC5 | [BLR_1_FG_IC5_MASS_FRAC]*1.498
BLR_1_H2O_COMB_NC5 | [BLR_1_FG_NC5_MASS_FRAC]*1.498
BLR_1_AIR_REQ_COMPLETE | [BLR_1_AIR_REQ_H2]+[BLR_1_AIR_REQ_CH4]+[BLR_1_AIR_REQ_ETHANE]+[BLR_1_AIR_REQ_ETHYLENE]+[BLR_1_AIR_REQ_PROPANE]+[BLR_1_AIR_REQ_NC4]+[BLR_1_AIR_REQ_IC4]+[BLR_1_AIR_REQ_NC5]+[BLR_1_AIR_REQ_IC5]
BLR_1_CO2_FORMED | [BLR_1_CO2_COMB_CH4]+[BLR_1_CO2_COMB_ETHANE]+[BLR_1_CO2_COMB_ETHYLENE]+[BLR_1_CO2_COMB_PROPANE]+[BLR_1_CO2_COMB_NC4]+[BLR_1_CO2_COMB_IC4]+[BLR_1_CO2_COMB_NC5]+[BLR_1_CO2_COMB_IC5]
BLR_1_N2_FORMED | [BLR_1_N2_COMB_H2]+[BLR_1_N2_COMB_CH4]+[BLR_1_N2_COMB_ETHANE]+[BLR_1_N2_COMB_ETHYLENE]+[BLR_1_N2_COMB_PROPANE]+[BLR_1_N2_COMB_IC4]+[BLR_1_N2_COMB_NC4]+[BLR_1_N2_COMB_IC5]+[BLR_1_N2_COMB_NC5]
BLR_1_H2O_FORMED | [BLR_1_H2O_COMB_H2]+[BLR_1_H2O_COMB_CH4]+[BLR_1_H2O_COMB_ETHANE]+[BLR_1_H2O_COMB_ETHYLENE]+[BLR_1_H2O_COMB_PROPANE]+[BLR_1_H2O_COMB_IC4]+[BLR_1_H2O_COMB_NC4]+[BLR_1_H2O_COMB_IC5]+[BLR_1_H2O_COMB_NC5]
BLR_1_VAPOUR_PRESSURE_H2O | 10^(8.07131-(1730.63/(233.426+[UN.UO.AMBIENT_TEMP])))
BLR_1_AIR_MOISTURE | [BLR_1_VAPOUR_PRESSURE_H2O]/(760-[BLR_1_VAPOUR_PRESSURE_H2O]*[UN.UO.RELATIVE_HUMIDITY_CLEAN])*[UN.UO.RELATIVE_HUMIDITY_CLEAN]*18.015/28.96
BLR_1_CORRECTED_COMBUSTION_AIR | [BLR_1_AIR_REQ_COMPLETE]/(1-[BLR_1_AIR_MOISTURE])
BLR_1_CORRECTED_H2O_FORMED | [BLR_1_H2O_FORMED]+([BLR_1_CORRECTED_COMBUSTION_AIR]-[BLR_1_AIR_REQ_COMPLETE])
BLR_1_EXCESS_AIR | ((28.96*[BLR_1_FLUE_GAS_OXYGEN])*([BLR_1_N2_FORMED]/28.01+[BLR_1_CORRECTED_H2O_FORMED]/18.015+[BLR_1_CO2_FORMED]/44.01)/(20.95-[BLR_1_FLUE_GAS_OXYGEN]))
BLR_1_AIR_FUEL_MASS_RATIO | [BLR_1_EXCESS_AIR]+[BLR_1_CORRECTED_COMBUSTION_AIR]
BLR_1_TOTAL_MOISTURE_WITH_AIR | [BLR_1_AIR_FUEL_MASS_RATIO]*[BLR_1_AIR_MOISTURE]
BLR_1_TOTAL_H2O_PER_KG_FUEL | [BLR_1_TOTAL_MOISTURE_WITH_AIR]+[BLR_1_H2O_FORMED]
BLR_1_DRY_FLUE_GAS_RATIO | [BLR_1_EXCESS_AIR]*(1-[BLR_1_AIR_MOISTURE])+[BLR_1_N2_FORMED]+[BLR_1_CO2_FORMED]
BLR_1_FLUE_GAS_RATIO | [BLR_1_DRY_FLUE_GAS_RATIO]+[BLR_1_TOTAL_H2O_PER_KG_FUEL]
BLR_1_FLUE_GAS_MW | [BLR_1_FLUE_GAS_RATIO]/([BLR_1_CO2_FORMED]/44.01+[BLR_1_TOTAL_H2O_PER_KG_FUEL]/18.015+[BLR_1_N2_FORMED]/28.01+[BLR_1_EXCESS_AIR]/28.96)
BLR_1_AIR_CP_REF_T | 6.96
BLR_1_CP_AT_COMB_TEMP | (((28.98641)+1.85398*(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_1_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_1_AIR_CP_SENSIBLE_CORRECTED | (([BLR_1_AIR_CP_REF_T]+[BLR_1_CP_AT_COMB_TEMP])/2)/28.96
BLR_1_CP_H2_FUEL_TEMP | ((33.066178)-11.363417*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)+11.432816*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-2.772874*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(-0.158558/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_CH4_FUEL_TEMP | ((-0.703029)+108.4773*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-42.52157*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+5.862788*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.678565/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_ETHANE_FUEL_TEMP | (6.08161+173.58246*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-66.91905*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+9.08912*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.129136/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_PROPANE_FUEL_TEMP | (12.66081+232.07025*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-70.34461*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+0.60714*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.026957/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_ETHYLENE_FUEL_TEMP | (-6.38788+184.4019*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-112.9718*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+28.49593*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+0.31554/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2)*0.239
BLR_1_CP_NC4_FUEL_TEMP | (22.1581+292.5894*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-85.8165*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-1.01394*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.00635/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_IC4_FUEL_TEMP | (8.32666+344.92332*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-141.6499*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-17.40270*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.02600/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_NC5_FUEL_TEMP | (-36.73509+580.37577*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-341.58654*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-78.49965*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(1.08617/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_IC5_FUEL_TEMP | (-16.14269+517.36368*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-271.31408*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-56.15662*(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.31713/(([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_FUEL_AT_REF_TEMP | (([BLR_1_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*6.876+[BLR_1_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*8.45+([BLR_1_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*10.02+([BLR_1_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*12.52+([BLR_1_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*17.72+([BLR_1_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79)+([BLR_1_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26+[BLR_1_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79+[BLR_1_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26)))*[BLR_1_FG_MW]
BLR_1_CP_FUEL_AT_FUEL_TEMP | (([BLR_1_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*[BLR_1_CP_H2_FUEL_TEMP]+[BLR_1_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*[BLR_1_CP_CH4_FUEL_TEMP]+([BLR_1_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*[BLR_1_CP_ETHYLENE_FUEL_TEMP]+([BLR_1_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*[BLR_1_CP_ETHANE_FUEL_TEMP]+([BLR_1_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*[BLR_1_CP_PROPANE_FUEL_TEMP]+([BLR_1_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_1_CP_NC4_FUEL_TEMP])+([BLR_1_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_1_CP_NC5_FUEL_TEMP]+[BLR_1_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_1_CP_IC4_FUEL_TEMP]+[BLR_1_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_1_CP_IC5_FUEL_TEMP])))*[BLR_1_FG_MW]
BLR_1_AVG_CP_FUEL_SENSIBLE | (([BLR_1_CP_FUEL_AT_REF_TEMP]+[BLR_1_CP_FUEL_AT_FUEL_TEMP])/[BLR_1_FG_MW])/2
BLR_1_CP_AIR_AT_STACK_TEMP | (((28.98641)+1.85398*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_1_CP_FLUE_CO2_AT_STACK | ((24.99735)+55.18696*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)-33.69137*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2+7.948387*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.136638/(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_CP_FLUE_H2O_AT_STACK | 8.22+0.00015*([BLR_1_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_1_STACK_TEMPERATURE]+273.15)^2)
BLR_1_CP_FLUE_N2_AT_STACK | ((28.98641)+1.85398*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_1_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_1_AVG_CP_FLUE_AT_STACK | ([BLR_1_CP_FLUE_CO2_AT_STACK]*[BLR_1_CO2_FORMED]/44.01+[BLR_1_CP_FLUE_N2_AT_STACK]*[BLR_1_N2_FORMED]/28.01+[BLR_1_EXCESS_AIR]/28.85*[BLR_1_CP_AIR_AT_STACK_TEMP])/([BLR_1_FLUE_GAS_RATIO]/[BLR_1_FLUE_GAS_MW])/[BLR_1_FLUE_GAS_MW]
BLR_1_CP_H2O_AT_STACK | (8.22+0.00015*([BLR_1_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_1_STACK_TEMPERATURE]+273.15)^2))/18.015
BLR_1_SH_CORRECTION_FUEL | if([BLR_1_AVG_CP_FUEL_SENSIBLE]*([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]-15.6)<0,0,[BLR_1_AVG_CP_FUEL_SENSIBLE]*([BLR_1_MAIN_FUEL_GAS_TEMPERATURE]-15.6))
BLR_1_SH_CORRECTION_AIR | [BLR_1_AIR_CP_SENSIBLE_CORRECTED]*([BLR_1_COMBUSTION_AIR_TEMPERATURE]-15.6)*[BLR_1_AIR_FUEL_MASS_RATIO]
BLR_1_MIXED_LHV_PER_KG | [UN.UO.BOILER_LHV]
BLR_1_TOTAL_HEAT_INPUT | if([BLR_1_STATUS]==0,0,[BLR_1_SH_CORRECTION_FUEL]+[BLR_1_SH_CORRECTION_AIR]+[BLR_1_MIXED_LHV_PER_KG])
BLR_1_HEAT_LOSS_L1 | if([BLR_1_STATUS]==0,0,[BLR_1_DRY_FLUE_GAS_RATIO]*([BLR_1_AVG_CP_FLUE_AT_STACK]*([BLR_1_STACK_TEMPERATURE]-15.6)))
BLR_1_HEAT_LOSS_L2 | if([BLR_1_STATUS]==0,0,9*[BLR_1_FG_H2_MASS_FRAC]*(584+[BLR_1_CP_H2O_AT_STACK]*([BLR_1_STACK_TEMPERATURE]-[UN.UO.AMBIENT_TEMP])))
BLR_1_HEAT_LOSS_L3 | if([BLR_1_STATUS]==0,0,[BLR_1_TOTAL_H2O_PER_KG_FUEL]*([BLR_1_STACK_TEMPERATURE]*1.77251246754294+2494.5133413964-2529.43)/4.184)
BLR_1_HEAT_LOSS_L4 | if([BLR_1_STATUS]==0,0,0*10^-6*28*5654*[BLR_1_BOILER_LOAD])
BLR_1_TOTAL_STACK_LOSS_PER_KG | if([BLR_1_STATUS]==0,0,[BLR_1_HEAT_LOSS_L4]+[BLR_1_HEAT_LOSS_L3]+[BLR_1_HEAT_LOSS_L1]+[BLR_1_HEAT_LOSS_L2])
BLR_1_RADIATION_LOSSES | if([BLR_1_STATUS]==0,0,[BLR_1_MIXED_LHV_PER_KG]*(-0.000004*[BLR_1_BOILER_LOAD]^3+0.001*[BLR_1_BOILER_LOAD]^2-0.0899*[BLR_1_BOILER_LOAD]+3.2426)/100)
BLR_1_TOTAL_HEAT_LOSS | if([BLR_1_STATUS]==0,0,[BLR_1_TOTAL_STACK_LOSS_PER_KG]+[BLR_1_RADIATION_LOSSES])
BLR_1_TOTAL_HEAT_ABSORBED | if([BLR_1_STATUS]==0,0,[BLR_1_TOTAL_HEAT_INPUT]-[BLR_1_TOTAL_HEAT_LOSS])
BLR_1_INDIRECT_EFFICIENCY | if([BLR_1_STATUS]==0,0,[BLR_1_TOTAL_HEAT_ABSORBED]/[BLR_1_TOTAL_HEAT_INPUT]*100)
BLR_1_HP_STEAM_ENTHALPY | if([BLR_1_STATUS]==0,0,(2175.54628147543-1.32764297764643*[BLR_1_HP_STEAM_PRESSURE]+2.66244961166282*[BLR_1_DESUPERHEATER_OUTLET_TEMP])*0.239+2)
BLR_1_TOTAL_STEAM_ENERGY | if([BLR_1_STATUS]==0,0,[BLR_1_STEAM_FLOW_RAW]*[BLR_1_HP_STEAM_ENTHALPY]/1000000)
BLR_1_BFW_ENTHALPY | if([BLR_1_STATUS]==0,0,[BLR_1_ECONOMIZER_INLET_TEMP])
BLR_1_CORRECTED_BFW_FLOW | if([BLR_1_STATUS]==0,0,([BLR_1_BFW_TO_ECONOMIZER]+[BLR_1_BFW_TO_DESUPERHEATER]-([BLR_1_BFW_TO_ECONOMIZER]+[BLR_1_BFW_TO_DESUPERHEATER]-[BLR_1_STEAM_FLOW_RAW]-[BLR_1_CBD_BLOWDOWN]))/1000)
BLR_1_BFW_ENERGY | if([BLR_1_STATUS]==0,0,[BLR_1_CORRECTED_BFW_FLOW]*[BLR_1_BFW_ENTHALPY]/1000)
BLR_1_FUEL_GAS_ENERGY_INPUT | if([BLR_1_STATUS]==0,0,[BLR_1_FG_FLOW_RATE_TPH]*1000*[BLR_1_MIXED_LHV_PER_KG]/10^6)
BLR_1_STEAM_DRUM_TEMP | if([BLR_1_STATUS]==0,0,4.02521999671835*log([BLR_1_STEAM_DRUM_PRESSURE]*98.065)^3-4.64392873298701*log([BLR_1_STEAM_DRUM_PRESSURE]*98.065)^2+11.2370106828649*log([BLR_1_STEAM_DRUM_PRESSURE]*98.065)+83.4806425229703)
BLR_1_BLOWDOWN_LOSS | if([BLR_1_STATUS]==0,0,(([BLR_1_CBD_BLOWDOWN]/1000)*(([BLR_1_STEAM_DRUM_PRESSURE]*2.11087739028321+[BLR_1_SUPERHEATER_INLET_TEMP]*2.94757709065418+278.050085762461)*0.2390006-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.0678913878546345+[BLR_1_SUPERHEATER_INLET_TEMP]*4.22416911685416-3.01717714574329)*0.2390006))/1000)
BLR_1_TOTAL_FLUE_GAS_GENERATED | if([BLR_1_STATUS]==0,0,[BLR_1_FUEL_GAS_FLOW]/1000*[BLR_1_FLUE_GAS_RATIO])
BLR_1_STACK_LOSS | if([BLR_1_STATUS]==0,0,[BLR_1_TOTAL_STACK_LOSS_PER_KG]*[BLR_1_FUEL_GAS_FLOW]/(1000*1000))
BLR_1_CORRECTED_FUEL_FLOW | if([BLR_1_STATUS]==0,0,[BLR_1_FUEL_GAS_FLOW]-(([BLR_1_FUEL_GAS_ENERGY_INPUT]-([BLR_1_TOTAL_STEAM_ENERGY]-[BLR_1_BFW_ENERGY]+[BLR_1_BLOWDOWN_LOSS]+[BLR_1_STACK_LOSS]+[BLR_1_FUEL_GAS_ENERGY_INPUT]*0.0112+[BLR_1_FUEL_GAS_ENERGY_INPUT]*(-0.000004*[BLR_1_BOILER_LOAD]^3+0.001*[BLR_1_BOILER_LOAD]^2-0.0899*[BLR_1_BOILER_LOAD]+3.2426)/100+([BLR_1_HEAT_LOSS_L3]*([BLR_1_FUEL_GAS_FLOW]/1000)*0.239006/1000)))/[BLR_1_MIXED_LHV_PER_KG]/1000))
BLR_1_FUEL_CONSUMPTION_GCAL | if([BLR_1_STATUS]==0,0,[BLR_1_CORRECTED_FUEL_FLOW]*[BLR_1_MIXED_LHV_PER_KG]/10^6)
BLR_1_SEC_GCAL_T | if([BLR_1_STATUS]==0,0,[BLR_1_FUEL_CONSUMPTION_GCAL]/([BLR_1_STEAM_FLOW_RAW]/1000))
BLR_1_SEC_GJ_T | if([BLR_1_STATUS]==0,0,[BLR_1_FUEL_CONSUMPTION_GCAL]/([BLR_1_STEAM_FLOW_RAW]/1000)*4.184)
BLR_1_CORRECTED_FUEL_ENERGY_INPUT | if([BLR_1_STATUS]==0,0,[BLR_1_CORRECTED_FUEL_FLOW]*[BLR_1_MIXED_LHV_PER_KG]/10^6)
BLR_1_THERMAL_EFFICIENCY | if([BLR_1_STATUS]==0,0,([BLR_1_TOTAL_STEAM_ENERGY]-[BLR_1_BFW_ENERGY])/[BLR_1_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_1_FUEL_GAS_CORRECTED_TPH | if([BLR_1_STATUS]==0,0,[BLR_1_CORRECTED_FUEL_FLOW]/1000)
BLR_1_TOTAL_FLUE_GAS_CORRECTED | if([BLR_1_STATUS]==0,0,[BLR_1_FUEL_GAS_CORRECTED_TPH]*[BLR_1_FLUE_GAS_RATIO])
BLR_1_STACK_LOSS_CORRECTED | if([BLR_1_STATUS]==0,0,[BLR_1_TOTAL_STACK_LOSS_PER_KG]*[BLR_1_FUEL_GAS_CORRECTED_TPH]/1000)
BLR_1_BFW_STEAM_RATIO | if([BLR_1_STATUS]==0,0,([BLR_1_STEAM_FLOW_RAW]+[BLR_1_CBD_BLOWDOWN])/([BLR_1_CORRECTED_BFW_FLOW]*1000))
BLR_1_CO2_EMISSIONS | if([BLR_1_STATUS]==0,0,[BLR_1_CO2_FORMED]*[BLR_1_FUEL_GAS_CORRECTED_TPH])
BLR_1_CALCULATED_AIRFLOW_NM3H | if([BLR_1_STATUS]==0,0,[BLR_1_AIR_FUEL_MASS_RATIO]*[BLR_1_CORRECTED_FUEL_FLOW]/(28.96/22.414)/1000)
BLR_1_STEAM_TO_FIRE_RATIO | if([BLR_1_STATUS]==0,0,[BLR_1_STEAM_FLOW_RAW]/([BLR_1_FG_FLOW_RATE_TPH]*[BLR_1_MIXED_LHV_PER_KG])*1000)
BLR_1_ECONOMIZER_DUTY | if([BLR_1_STATUS]==0,0,[BLR_1_CORRECTED_BFW_FLOW]*(([BLR_1_STEAM_DRUM_PRESSURE]*0.033652+[BLR_1_ECONOMIZER_OUTLET_TEMP]*4.52730-53.56679)-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.067891+[BLR_1_ECONOMIZER_INLET_TEMP]*4.22417-3.01718))*0.239006/1000)
BLR_1_LMTD_ECONOMIZER | if([BLR_1_STATUS]==0,0,((673-[BLR_1_ECONOMIZER_OUTLET_TEMP])-([BLR_1_STACK_TEMPERATURE]-[BLR_1_ECONOMIZER_INLET_TEMP]))/ln((673-[BLR_1_ECONOMIZER_OUTLET_TEMP])/(-[BLR_1_ECONOMIZER_INLET_TEMP]+[BLR_1_STACK_TEMPERATURE])))
BLR_1_UA_ECONOMIZER | if([BLR_1_STATUS]==0,0,[BLR_1_ECONOMIZER_DUTY]/[BLR_1_LMTD_ECONOMIZER])
BLR_1_FOULING_INDEX | if([BLR_1_STATUS]==0,0,1/[BLR_1_UA_ECONOMIZER])
BLR_1_SH_DUTY | if([BLR_1_STATUS]==0,0,[BLR_1_STEAM_FLOW_RAW]*(([BLR_1_STEAM_DRUM_PRESSURE]*-2.64315+[BLR_1_DESUPERHEATER_TEMPERATURE]*3.58096+1939.73413)-([BLR_1_STEAM_DRUM_PRESSURE]*-4.27591+[BLR_1_SUPERHEATER_INLET_TEMP]*3.45878+2082.10231))*0.239006/1000000)
BLR_1_SH_SPECIFIC_DUTY | if([BLR_1_STATUS]==0,0,[BLR_1_SH_DUTY]/[BLR_1_STEAM_FLOW_RAW]*1000)
BLR_1_SH_PERFORMANCE | if([BLR_1_STATUS]==0,0,[BLR_1_SH_SPECIFIC_DUTY]/0.128049016*100)
BLR_1_ENERGY_GAINED | if([BLR_1_STATUS]==0,0,[BLR_1_TOTAL_STEAM_ENERGY]-[BLR_1_BFW_ENERGY])
BLR_1_CONVECTION_DUTY | if([BLR_1_STATUS]==0,0,[BLR_1_ECONOMIZER_DUTY]+[BLR_1_SH_DUTY]+[BLR_1_STACK_LOSS_CORRECTED])
BLR_1_RADIATION_DUTY | if([BLR_1_STATUS]==0,0,[BLR_1_ENERGY_GAINED]-[BLR_1_CONVECTION_DUTY])
BLR_1_PCT_DUTY_CONVECTION | if([BLR_1_STATUS]==0,0,[BLR_1_CONVECTION_DUTY]/[BLR_1_ENERGY_GAINED]*100)
BLR_1_PCT_DUTY_RADIANT | if([BLR_1_STATUS]==0,0,[BLR_1_RADIATION_DUTY]/[BLR_1_ENERGY_GAINED]*100)
BLR_1_DUTY_RATIO_RAD_CONV | if([BLR_1_STATUS]==0,0,[BLR_1_PCT_DUTY_RADIANT]/[BLR_1_PCT_DUTY_CONVECTION])
BLR_1_RADIATION_SECTION_EFF | if([BLR_1_STATUS]==0,0,[BLR_1_RADIATION_DUTY]/[BLR_1_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_1_CONVECTION_SECTION_EFF | if([BLR_1_STATUS]==0,0,[BLR_1_CONVECTION_DUTY]/[BLR_1_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_1_HPS_GEN | if([BLR_1_STEAM_FLOW_RAW]<0,0,[BLR_1_STEAM_FLOW_RAW]/1000)
BLR_1_FUEL_FLOW | [BLR_1_FUEL_GAS_FLOW]*[BLR_1_STATUS]/1000
BLR_1_CAPACITY | 150
BLR_1_SPEC_EN_CONS | if([BLR_1_HPS_GEN]==0,0,[BLR_1_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_1_HPS_GEN])
BLR_1_SPEC_EN_CONS_OPT | (8e-06*[BLR_1_HPS_GEN]^2+-0.0017*[BLR_1_HPS_GEN]+3.0167)*[BLR_1_STATUS]
BLR_1_SPEC_EN_CONS_DEV | if([BLR_1_STATUS]==0,0,([BLR_1_SPEC_EN_CONS_OPT]-[BLR_1_SPEC_EN_CONS])/[BLR_1_SPEC_EN_CONS_OPT])
BLR_1_HPS_GEN_WARMUP | if([BLR_1_STATUS]==0,[BLR_1_HPS_GEN],0)
BLR_1_FD_FAN_STEAM_REG | ((4378.1-32.667*[BLR_1_HPS_GEN]+0.4255*[BLR_1_HPS_GEN]^2)/1000)
BLR_1_FD_FAN_STEAM_WARMUP | if([BLR_1_FD_FAN_STEAM_RAW]>100&&[BLR_1_FD_FAN_STEAM_RAW]<8000&&[BLR_1_STATUS]==0,[BLR_1_FD_FAN_STEAM_RAW]/1000,0)
BLR_1_FD_FAN_STEAM | if([BLR_1_FD_FAN_STEAM_RAW]<500,0,[BLR_1_FD_FAN_STEAM_RAW]/1000)
BLR_2_BOILER_LOAD | [BLR_2_STEAM_FLOW_RAW]/150000*100
BLR_2_STATUS | if([BLR_2_BOILER_LOAD]>25&&[BLR_2_DESUPERHEATER_OUTLET_TEMP]>370&&[BLR_2_HP_STEAM_PRESSURE]>40,1,0)
BLR_2_FUEL_COMP_TOTAL | ([UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]+[UN.UO.BOILER_FG_CH4_CONCENTRATION]+[UN.UO.BOILER_FG_ETHANE_CONCENTRATION]+[UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]+[UN.UO.BOILER_FG_PROPANE_CONCENTRATION]+[UN.UO.BOILER_FG_NC4_CONCENTRATION]+[UN.UO.BOILER_FG_IC4_CONCENTRATION]+[UN.UO.BOILER_FG_NC5_CONCENTRATION]+[UN.UO.BOILER_FG_IC5_CONCENTRATION]+[UN.UO.BOILER_FG_N2_CONCENTRATION])
BLR_2_FG_NORM_CH4 | [UN.UO.BOILER_FG_CH4_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_ETHANE | [UN.UO.BOILER_FG_ETHANE_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_ETHYLENE | [UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_PROPANE | [UN.UO.BOILER_FG_PROPANE_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_CO2 | 0
BLR_2_FG_NORM_IC4 | [UN.UO.BOILER_FG_IC4_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_NC4 | [UN.UO.BOILER_FG_NC4_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_NC5 | [UN.UO.BOILER_FG_NC5_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_IC5 | [UN.UO.BOILER_FG_IC5_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_N2 | [UN.UO.BOILER_FG_N2_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_NORM_H2 | [UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]/[BLR_2_FUEL_COMP_TOTAL]*100
BLR_2_FG_MW | ([BLR_2_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]+[BLR_2_FG_NORM_CH4]*[COMPONENT_METHANE_MW]+[BLR_2_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]+[BLR_2_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]+[BLR_2_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]+[BLR_2_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]+[BLR_2_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]+[BLR_2_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]+[BLR_2_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]+[BLR_2_FG_NORM_N2]*[COMPONENT_NITROGEN_MW])/100
BLR_2_FG_DENSITY | [BLR_2_FG_MW]/22.414
BLR_2_LHV_DESIGN | ([LHV_FG]/[BLR_2_FG_DENSITY])/1000
BLR_2_FG_CH4_MASS_PCT | [BLR_2_FG_NORM_CH4]*[COMPONENT_METHANE_MW]/[BLR_2_FG_MW]
BLR_2_FG_ETHANE_MASS_PCT | [BLR_2_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]/[BLR_2_FG_MW]
BLR_2_FG_ETHYLENE_MASS_PCT | [BLR_2_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]/[BLR_2_FG_MW]
BLR_2_FG_PROPANE_MASS_PCT | [BLR_2_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]/[BLR_2_FG_MW]
BLR_2_FG_N2_MASS_PCT | [BLR_2_FG_NORM_N2]*[COMPONENT_NITROGEN_MW]/[BLR_2_FG_MW]
BLR_2_FG_H2_MASS_PCT | [BLR_2_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]/[BLR_2_FG_MW]
BLR_2_FG_IC4_MASS_PCT | [BLR_2_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]/[BLR_2_FG_MW]
BLR_2_FG_NC4_MASS_PCT | [BLR_2_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]/[BLR_2_FG_MW]
BLR_2_FG_NC5_MASS_PCT | [BLR_2_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]/[BLR_2_FG_MW]
BLR_2_FG_IC5_MASS_PCT | [BLR_2_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]/[BLR_2_FG_MW]
BLR_2_FG_CH4_MASS_FRAC | [BLR_2_FG_CH4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_ETHANE_MASS_FRAC | [BLR_2_FG_ETHANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_ETHYLENE_MASS_FRAC | [BLR_2_FG_ETHYLENE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_PROPANE_MASS_FRAC | [BLR_2_FG_PROPANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_N2_MASS_FRAC | [BLR_2_FG_N2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_H2_MASS_FRAC | [BLR_2_FG_H2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_IC4_MASS_FRAC | [BLR_2_FG_IC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_NC4_MASS_FRAC | [BLR_2_FG_NC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_NC5_MASS_FRAC | [BLR_2_FG_NC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_IC5_MASS_FRAC | [BLR_2_FG_IC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_2_FG_FLOW_RATE_TPH | [BLR_2_FUEL_GAS_FLOW]/1000
BLR_2_AIR_REQ_H2 | [BLR_2_FG_H2_MASS_FRAC]*34.344
BLR_2_AIR_REQ_CH4 | [BLR_2_FG_CH4_MASS_FRAC]*17.265
BLR_2_AIR_REQ_ETHANE | [BLR_2_FG_ETHANE_MASS_FRAC]*16.119
BLR_2_AIR_REQ_ETHYLENE | [BLR_2_FG_ETHYLENE_MASS_FRAC]*14.807
BLR_2_AIR_REQ_PROPANE | [BLR_2_FG_PROPANE_MASS_FRAC]*15.703
BLR_2_AIR_REQ_NC4 | [BLR_2_FG_NC4_MASS_FRAC]*15.487
BLR_2_AIR_REQ_IC4 | [BLR_2_FG_IC4_MASS_FRAC]*15.487
BLR_2_AIR_REQ_NC5 | [BLR_2_FG_NC5_MASS_FRAC]*15.353
BLR_2_AIR_REQ_IC5 | [BLR_2_FG_IC5_MASS_FRAC]*15.353
BLR_2_CO2_COMB_H2 | [BLR_2_FG_H2_MASS_FRAC]*0
BLR_2_CO2_COMB_CH4 | [BLR_2_FG_CH4_MASS_FRAC]*2.744
BLR_2_CO2_COMB_ETHANE | [BLR_2_FG_ETHANE_MASS_FRAC]*2.927
BLR_2_CO2_COMB_ETHYLENE | [BLR_2_FG_ETHYLENE_MASS_FRAC]*3.138
BLR_2_CO2_COMB_PROPANE | [BLR_2_FG_PROPANE_MASS_FRAC]*2.994
BLR_2_CO2_COMB_NC4 | [BLR_2_FG_NC4_MASS_FRAC]*3.029
BLR_2_CO2_COMB_IC4 | [BLR_2_FG_IC4_MASS_FRAC]*3.029
BLR_2_CO2_COMB_NC5 | [BLR_2_FG_NC5_MASS_FRAC]*3.05
BLR_2_CO2_COMB_IC5 | [BLR_2_FG_IC5_MASS_FRAC]*3.05
BLR_2_N2_COMB_H2 | [BLR_2_FG_H2_MASS_FRAC]*26.407
BLR_2_N2_COMB_CH4 | [BLR_2_FG_CH4_MASS_FRAC]*13.275
BLR_2_N2_COMB_ETHANE | [BLR_2_FG_ETHANE_MASS_FRAC]*12.394
BLR_2_N2_COMB_ETHYLENE | [BLR_2_FG_ETHYLENE_MASS_FRAC]*11.385
BLR_2_N2_COMB_PROPANE | [BLR_2_FG_PROPANE_MASS_FRAC]*12.074
BLR_2_N2_COMB_IC4 | [BLR_2_FG_IC4_MASS_FRAC]*11.908
BLR_2_N2_COMB_NC4 | [BLR_2_FG_NC4_MASS_FRAC]*11.908
BLR_2_N2_COMB_IC5 | [BLR_2_FG_IC5_MASS_FRAC]*11.805
BLR_2_N2_COMB_NC5 | [BLR_2_FG_NC5_MASS_FRAC]*11.805
BLR_2_H2O_COMB_H2 | [BLR_2_FG_H2_MASS_FRAC]*8.937
BLR_2_H2O_COMB_CH4 | [BLR_2_FG_CH4_MASS_FRAC]*2.246
BLR_2_H2O_COMB_ETHANE | [BLR_2_FG_ETHANE_MASS_FRAC]*1.798
BLR_2_H2O_COMB_ETHYLENE | [BLR_2_FG_ETHYLENE_MASS_FRAC]*1.285
BLR_2_H2O_COMB_PROPANE | [BLR_2_FG_PROPANE_MASS_FRAC]*1.634
BLR_2_H2O_COMB_IC4 | [BLR_2_FG_NC4_MASS_FRAC]*1.55
BLR_2_H2O_COMB_NC4 | [BLR_2_FG_IC4_MASS_FRAC]*1.55
BLR_2_H2O_COMB_IC5 | [BLR_2_FG_IC5_MASS_FRAC]*1.498
BLR_2_H2O_COMB_NC5 | [BLR_2_FG_NC5_MASS_FRAC]*1.498
BLR_2_AIR_REQ_COMPLETE | [BLR_2_AIR_REQ_H2]+[BLR_2_AIR_REQ_CH4]+[BLR_2_AIR_REQ_ETHANE]+[BLR_2_AIR_REQ_ETHYLENE]+[BLR_2_AIR_REQ_PROPANE]+[BLR_2_AIR_REQ_NC4]+[BLR_2_AIR_REQ_IC4]+[BLR_2_AIR_REQ_NC5]+[BLR_2_AIR_REQ_IC5]
BLR_2_CO2_FORMED | [BLR_2_CO2_COMB_CH4]+[BLR_2_CO2_COMB_ETHANE]+[BLR_2_CO2_COMB_ETHYLENE]+[BLR_2_CO2_COMB_PROPANE]+[BLR_2_CO2_COMB_NC4]+[BLR_2_CO2_COMB_IC4]+[BLR_2_CO2_COMB_NC5]+[BLR_2_CO2_COMB_IC5]
BLR_2_N2_FORMED | [BLR_2_N2_COMB_H2]+[BLR_2_N2_COMB_CH4]+[BLR_2_N2_COMB_ETHANE]+[BLR_2_N2_COMB_ETHYLENE]+[BLR_2_N2_COMB_PROPANE]+[BLR_2_N2_COMB_IC4]+[BLR_2_N2_COMB_NC4]+[BLR_2_N2_COMB_IC5]+[BLR_2_N2_COMB_NC5]
BLR_2_H2O_FORMED | [BLR_2_H2O_COMB_H2]+[BLR_2_H2O_COMB_CH4]+[BLR_2_H2O_COMB_ETHANE]+[BLR_2_H2O_COMB_ETHYLENE]+[BLR_2_H2O_COMB_PROPANE]+[BLR_2_H2O_COMB_IC4]+[BLR_2_H2O_COMB_NC4]+[BLR_2_H2O_COMB_IC5]+[BLR_2_H2O_COMB_NC5]
BLR_2_VAPOUR_PRESSURE_H2O | 10^(8.07131-(1730.63/(233.426+[UN.UO.AMBIENT_TEMP])))
BLR_2_AIR_MOISTURE | [BLR_2_VAPOUR_PRESSURE_H2O]/(760-[BLR_2_VAPOUR_PRESSURE_H2O]*[UN.UO.RELATIVE_HUMIDITY_CLEAN])*[UN.UO.RELATIVE_HUMIDITY_CLEAN]*18.015/28.96
BLR_2_CORRECTED_COMBUSTION_AIR | [BLR_2_AIR_REQ_COMPLETE]/(1-[BLR_2_AIR_MOISTURE])
BLR_2_CORRECTED_H2O_FORMED | [BLR_2_H2O_FORMED]+([BLR_2_CORRECTED_COMBUSTION_AIR]-[BLR_2_AIR_REQ_COMPLETE])
BLR_2_EXCESS_AIR | ((28.96*[BLR_2_FLUE_GAS_OXYGEN])*([BLR_2_N2_FORMED]/28.01+[BLR_2_CORRECTED_H2O_FORMED]/18.015+[BLR_2_CO2_FORMED]/44.01)/(20.95-[BLR_2_FLUE_GAS_OXYGEN]))
BLR_2_AIR_FUEL_MASS_RATIO | [BLR_2_EXCESS_AIR]+[BLR_2_CORRECTED_COMBUSTION_AIR]
BLR_2_TOTAL_MOISTURE_WITH_AIR | [BLR_2_AIR_FUEL_MASS_RATIO]*[BLR_2_AIR_MOISTURE]
BLR_2_TOTAL_H2O_PER_KG_FUEL | [BLR_2_TOTAL_MOISTURE_WITH_AIR]+[BLR_2_H2O_FORMED]
BLR_2_DRY_FLUE_GAS_RATIO | [BLR_2_EXCESS_AIR]*(1-[BLR_2_AIR_MOISTURE])+[BLR_2_N2_FORMED]+[BLR_2_CO2_FORMED]
BLR_2_FLUE_GAS_RATIO | [BLR_2_DRY_FLUE_GAS_RATIO]+[BLR_2_TOTAL_H2O_PER_KG_FUEL]
BLR_2_FLUE_GAS_MW | [BLR_2_FLUE_GAS_RATIO]/([BLR_2_CO2_FORMED]/44.01+[BLR_2_TOTAL_H2O_PER_KG_FUEL]/18.015+[BLR_2_N2_FORMED]/28.01+[BLR_2_EXCESS_AIR]/28.96)
BLR_2_AIR_CP_REF_T | 6.96
BLR_2_CP_AT_COMB_TEMP | (((28.98641)+1.85398*(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_2_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_2_AIR_CP_SENSIBLE_CORRECTED | (([BLR_2_AIR_CP_REF_T]+[BLR_2_CP_AT_COMB_TEMP])/2)/28.96
BLR_2_CP_H2_FUEL_TEMP | ((33.066178)-11.363417*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)+11.432816*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-2.772874*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(-0.158558/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_CH4_FUEL_TEMP | ((-0.703029)+108.4773*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-42.52157*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+5.862788*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.678565/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_ETHANE_FUEL_TEMP | (6.08161+173.58246*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-66.91905*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+9.08912*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.129136/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_PROPANE_FUEL_TEMP | (12.66081+232.07025*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-70.34461*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+0.60714*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.026957/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_ETHYLENE_FUEL_TEMP | (-6.38788+184.4019*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-112.9718*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+28.49593*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+0.31554/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2)*0.239
BLR_2_CP_NC4_FUEL_TEMP | (22.1581+292.5894*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-85.8165*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-1.01394*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.00635/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_IC4_FUEL_TEMP | (8.32666+344.92332*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-141.6499*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-17.40270*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.02600/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_NC5_FUEL_TEMP | (-36.73509+580.37577*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-341.58654*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-78.49965*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(1.08617/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_IC5_FUEL_TEMP | (-16.14269+517.36368*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-271.31408*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-56.15662*(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.31713/(([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_FUEL_AT_REF_TEMP | (([BLR_2_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*6.876+[BLR_2_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*8.45+([BLR_2_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*10.02+([BLR_2_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*12.52+([BLR_2_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*17.72+([BLR_2_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79)+([BLR_2_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26+[BLR_2_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79+[BLR_2_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26)))*[BLR_2_FG_MW]
BLR_2_CP_FUEL_AT_FUEL_TEMP | (([BLR_2_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*[BLR_2_CP_H2_FUEL_TEMP]+[BLR_2_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*[BLR_2_CP_CH4_FUEL_TEMP]+([BLR_2_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*[BLR_2_CP_ETHYLENE_FUEL_TEMP]+([BLR_2_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*[BLR_2_CP_ETHANE_FUEL_TEMP]+([BLR_2_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*[BLR_2_CP_PROPANE_FUEL_TEMP]+([BLR_2_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_2_CP_NC4_FUEL_TEMP])+([BLR_2_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_2_CP_NC5_FUEL_TEMP]+[BLR_2_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_2_CP_IC4_FUEL_TEMP]+[BLR_2_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_2_CP_IC5_FUEL_TEMP])))*[BLR_2_FG_MW]
BLR_2_AVG_CP_FUEL_SENSIBLE | (([BLR_2_CP_FUEL_AT_REF_TEMP]+[BLR_2_CP_FUEL_AT_FUEL_TEMP])/[BLR_2_FG_MW])/2
BLR_2_CP_AIR_AT_STACK_TEMP | (((28.98641)+1.85398*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_2_CP_FLUE_CO2_AT_STACK | ((24.99735)+55.18696*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)-33.69137*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2+7.948387*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.136638/(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_CP_FLUE_H2O_AT_STACK | 8.22+0.00015*([BLR_2_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_2_STACK_TEMPERATURE]+273.15)^2)
BLR_2_CP_FLUE_N2_AT_STACK | ((28.98641)+1.85398*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_2_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_2_AVG_CP_FLUE_AT_STACK | ([BLR_2_CP_FLUE_CO2_AT_STACK]*[BLR_2_CO2_FORMED]/44.01+[BLR_2_CP_FLUE_N2_AT_STACK]*[BLR_2_N2_FORMED]/28.01+[BLR_2_EXCESS_AIR]/28.85*[BLR_2_CP_AIR_AT_STACK_TEMP])/([BLR_2_FLUE_GAS_RATIO]/[BLR_2_FLUE_GAS_MW])/[BLR_2_FLUE_GAS_MW]
BLR_2_CP_H2O_AT_STACK | (8.22+0.00015*([BLR_2_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_2_STACK_TEMPERATURE]+273.15)^2))/18.015
BLR_2_SH_CORRECTION_FUEL | if([BLR_2_AVG_CP_FUEL_SENSIBLE]*([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]-15.6)<0,0,[BLR_2_AVG_CP_FUEL_SENSIBLE]*([BLR_2_MAIN_FUEL_GAS_TEMPERATURE]-15.6))
BLR_2_SH_CORRECTION_AIR | [BLR_2_AIR_CP_SENSIBLE_CORRECTED]*([BLR_2_COMBUSTION_AIR_TEMPERATURE]-15.6)*[BLR_2_AIR_FUEL_MASS_RATIO]
BLR_2_MIXED_LHV_PER_KG | [UN.UO.BOILER_LHV]
BLR_2_TOTAL_HEAT_INPUT | if([BLR_2_STATUS]==0,0,[BLR_2_SH_CORRECTION_FUEL]+[BLR_2_SH_CORRECTION_AIR]+[BLR_2_MIXED_LHV_PER_KG])
BLR_2_HEAT_LOSS_L1 | if([BLR_2_STATUS]==0,0,[BLR_2_DRY_FLUE_GAS_RATIO]*([BLR_2_AVG_CP_FLUE_AT_STACK]*([BLR_2_STACK_TEMPERATURE]-15.6)))
BLR_2_HEAT_LOSS_L2 | if([BLR_2_STATUS]==0,0,9*[BLR_2_FG_H2_MASS_FRAC]*(584+[BLR_2_CP_H2O_AT_STACK]*([BLR_2_STACK_TEMPERATURE]-[UN.UO.AMBIENT_TEMP])))
BLR_2_HEAT_LOSS_L3 | if([BLR_2_STATUS]==0,0,[BLR_2_TOTAL_H2O_PER_KG_FUEL]*([BLR_2_STACK_TEMPERATURE]*1.77251246754294+2494.5133413964-2529.43)/4.184)
BLR_2_HEAT_LOSS_L4 | if([BLR_2_STATUS]==0,0,0*10^-6*28*5654*[BLR_2_BOILER_LOAD])
BLR_2_TOTAL_STACK_LOSS_PER_KG | if([BLR_2_STATUS]==0,0,[BLR_2_HEAT_LOSS_L4]+[BLR_2_HEAT_LOSS_L3]+[BLR_2_HEAT_LOSS_L1]+[BLR_2_HEAT_LOSS_L2])
BLR_2_RADIATION_LOSSES | if([BLR_2_STATUS]==0,0,[BLR_2_MIXED_LHV_PER_KG]*(-0.000004*[BLR_2_BOILER_LOAD]^3+0.001*[BLR_2_BOILER_LOAD]^2-0.0899*[BLR_2_BOILER_LOAD]+3.2426)/100)
BLR_2_TOTAL_HEAT_LOSS | if([BLR_2_STATUS]==0,0,[BLR_2_TOTAL_STACK_LOSS_PER_KG]+[BLR_2_RADIATION_LOSSES])
BLR_2_TOTAL_HEAT_ABSORBED | if([BLR_2_STATUS]==0,0,[BLR_2_TOTAL_HEAT_INPUT]-[BLR_2_TOTAL_HEAT_LOSS])
BLR_2_INDIRECT_EFFICIENCY | if([BLR_2_STATUS]==0,0,[BLR_2_TOTAL_HEAT_ABSORBED]/[BLR_2_TOTAL_HEAT_INPUT]*100)
BLR_2_HP_STEAM_ENTHALPY | if([BLR_2_STATUS]==0,0,(2175.54628147543-1.32764297764643*[BLR_2_HP_STEAM_PRESSURE]+2.66244961166282*[BLR_2_DESUPERHEATER_OUTLET_TEMP])*0.239+2)
BLR_2_TOTAL_STEAM_ENERGY | if([BLR_2_STATUS]==0,0,[BLR_2_STEAM_FLOW_RAW]*[BLR_2_HP_STEAM_ENTHALPY]/1000000)
BLR_2_BFW_ENTHALPY | if([BLR_2_STATUS]==0,0,[BLR_2_ECONOMIZER_INLET_TEMP])
BLR_2_CORRECTED_BFW_FLOW | if([BLR_2_STATUS]==0,0,([BLR_2_BFW_TO_ECONOMIZER]+[BLR_2_BFW_TO_DESUPERHEATER]-([BLR_2_BFW_TO_ECONOMIZER]+[BLR_2_BFW_TO_DESUPERHEATER]-[BLR_2_STEAM_FLOW_RAW]-[BLR_2_CBD_BLOWDOWN]))/1000)
BLR_2_BFW_ENERGY | if([BLR_2_STATUS]==0,0,[BLR_2_CORRECTED_BFW_FLOW]*[BLR_2_BFW_ENTHALPY]/1000)
BLR_2_FUEL_GAS_ENERGY_INPUT | if([BLR_2_STATUS]==0,0,[BLR_2_FG_FLOW_RATE_TPH]*1000*[BLR_2_MIXED_LHV_PER_KG]/10^6)
BLR_2_STEAM_DRUM_TEMP | if([BLR_2_STATUS]==0,0,4.02521999671835*log([BLR_2_STEAM_DRUM_PRESSURE]*98.065)^3-4.64392873298701*log([BLR_2_STEAM_DRUM_PRESSURE]*98.065)^2+11.2370106828649*log([BLR_2_STEAM_DRUM_PRESSURE]*98.065)+83.4806425229703)
BLR_2_BLOWDOWN_LOSS | if([BLR_2_STATUS]==0,0,(([BLR_2_CBD_BLOWDOWN]/1000)*(([BLR_2_STEAM_DRUM_PRESSURE]*2.11087739028321+[BLR_2_SUPERHEATER_INLET_TEMP]*2.94757709065418+278.050085762461)*0.2390006-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.0678913878546345+[BLR_2_SUPERHEATER_INLET_TEMP]*4.22416911685416-3.01717714574329)*0.2390006))/1000)
BLR_2_TOTAL_FLUE_GAS_GENERATED | if([BLR_2_STATUS]==0,0,[BLR_2_FUEL_GAS_FLOW]/1000*[BLR_2_FLUE_GAS_RATIO])
BLR_2_STACK_LOSS | if([BLR_2_STATUS]==0,0,[BLR_2_TOTAL_STACK_LOSS_PER_KG]*[BLR_2_FUEL_GAS_FLOW]/(1000*1000))
BLR_2_CORRECTED_FUEL_FLOW | if([BLR_2_STATUS]==0,0,[BLR_2_FUEL_GAS_FLOW]-(([BLR_2_FUEL_GAS_ENERGY_INPUT]-([BLR_2_TOTAL_STEAM_ENERGY]-[BLR_2_BFW_ENERGY]+[BLR_2_BLOWDOWN_LOSS]+[BLR_2_STACK_LOSS]+[BLR_2_FUEL_GAS_ENERGY_INPUT]*0.0112+[BLR_2_FUEL_GAS_ENERGY_INPUT]*(-0.000004*[BLR_2_BOILER_LOAD]^3+0.001*[BLR_2_BOILER_LOAD]^2-0.0899*[BLR_2_BOILER_LOAD]+3.2426)/100+([BLR_2_HEAT_LOSS_L3]*([BLR_2_FUEL_GAS_FLOW]/1000)*0.239006/1000)))/[BLR_2_MIXED_LHV_PER_KG]/1000))
BLR_2_FUEL_CONSUMPTION_GCAL | if([BLR_2_STATUS]==0,0,[BLR_2_CORRECTED_FUEL_FLOW]*[BLR_2_MIXED_LHV_PER_KG]/10^6)
BLR_2_SEC_GCAL_T | if([BLR_2_STATUS]==0,0,[BLR_2_FUEL_CONSUMPTION_GCAL]/([BLR_2_STEAM_FLOW_RAW]/1000))
BLR_2_SEC_GJ_T | if([BLR_2_STATUS]==0,0,[BLR_2_FUEL_CONSUMPTION_GCAL]/([BLR_2_STEAM_FLOW_RAW]/1000)*4.184)
BLR_2_CORRECTED_FUEL_ENERGY_INPUT | if([BLR_2_STATUS]==0,0,[BLR_2_CORRECTED_FUEL_FLOW]*[BLR_2_MIXED_LHV_PER_KG]/10^6)
BLR_2_THERMAL_EFFICIENCY | if([BLR_2_STATUS]==0,0,([BLR_2_TOTAL_STEAM_ENERGY]-[BLR_2_BFW_ENERGY])/[BLR_2_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_2_FUEL_GAS_CORRECTED_TPH | if([BLR_2_STATUS]==0,0,[BLR_2_CORRECTED_FUEL_FLOW]/1000)
BLR_2_TOTAL_FLUE_GAS_CORRECTED | if([BLR_2_STATUS]==0,0,[BLR_2_FUEL_GAS_CORRECTED_TPH]*[BLR_2_FLUE_GAS_RATIO])
BLR_2_STACK_LOSS_CORRECTED | if([BLR_2_STATUS]==0,0,[BLR_2_TOTAL_STACK_LOSS_PER_KG]*[BLR_2_FUEL_GAS_CORRECTED_TPH]/1000)
BLR_2_BFW_STEAM_RATIO | if([BLR_2_STATUS]==0,0,([BLR_2_STEAM_FLOW_RAW]+[BLR_2_CBD_BLOWDOWN])/([BLR_2_CORRECTED_BFW_FLOW]*1000))
BLR_2_CO2_EMISSIONS | if([BLR_2_STATUS]==0,0,[BLR_2_CO2_FORMED]*[BLR_2_FUEL_GAS_CORRECTED_TPH])
BLR_2_CALCULATED_AIRFLOW_NM3H | if([BLR_2_STATUS]==0,0,[BLR_2_AIR_FUEL_MASS_RATIO]*[BLR_2_CORRECTED_FUEL_FLOW]/(28.96/22.414)/1000)
BLR_2_STEAM_TO_FIRE_RATIO | if([BLR_2_STATUS]==0,0,[BLR_2_STEAM_FLOW_RAW]/([BLR_2_FG_FLOW_RATE_TPH]*[BLR_2_MIXED_LHV_PER_KG])*1000)
BLR_2_ECONOMIZER_DUTY | if([BLR_2_STATUS]==0,0,[BLR_2_CORRECTED_BFW_FLOW]*(([BLR_2_STEAM_DRUM_PRESSURE]*0.033652+[BLR_2_ECONOMIZER_OUTLET_TEMP]*4.52730-53.56679)-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.067891+[BLR_2_ECONOMIZER_INLET_TEMP]*4.22417-3.01718))*0.239006/1000)
BLR_2_LMTD_ECONOMIZER | if([BLR_2_STATUS]==0,0,((673-[BLR_2_ECONOMIZER_OUTLET_TEMP])-([BLR_2_STACK_TEMPERATURE]-[BLR_2_ECONOMIZER_INLET_TEMP]))/ln((673-[BLR_2_ECONOMIZER_OUTLET_TEMP])/(-[BLR_2_ECONOMIZER_INLET_TEMP]+[BLR_2_STACK_TEMPERATURE])))
BLR_2_UA_ECONOMIZER | if([BLR_2_STATUS]==0,0,[BLR_2_ECONOMIZER_DUTY]/[BLR_2_LMTD_ECONOMIZER])
BLR_2_FOULING_INDEX | if([BLR_2_STATUS]==0,0,1/[BLR_2_UA_ECONOMIZER])
BLR_2_SH_DUTY | if([BLR_2_STATUS]==0,0,[BLR_2_STEAM_FLOW_RAW]*(([BLR_2_STEAM_DRUM_PRESSURE]*-2.64315+[BLR_2_DESUPERHEATER_TEMPERATURE]*3.58096+1939.73413)-([BLR_2_STEAM_DRUM_PRESSURE]*-4.27591+[BLR_2_SUPERHEATER_INLET_TEMP]*3.45878+2082.10231))*0.239006/1000000)
BLR_2_SH_SPECIFIC_DUTY | if([BLR_2_STATUS]==0,0,[BLR_2_SH_DUTY]/[BLR_2_STEAM_FLOW_RAW]*1000)
BLR_2_SH_PERFORMANCE | if([BLR_2_STATUS]==0,0,[BLR_2_SH_SPECIFIC_DUTY]/0.128049016*100)
BLR_2_ENERGY_GAINED | if([BLR_2_STATUS]==0,0,[BLR_2_TOTAL_STEAM_ENERGY]-[BLR_2_BFW_ENERGY])
BLR_2_CONVECTION_DUTY | if([BLR_2_STATUS]==0,0,[BLR_2_ECONOMIZER_DUTY]+[BLR_2_SH_DUTY]+[BLR_2_STACK_LOSS_CORRECTED])
BLR_2_RADIATION_DUTY | if([BLR_2_STATUS]==0,0,[BLR_2_ENERGY_GAINED]-[BLR_2_CONVECTION_DUTY])
BLR_2_PCT_DUTY_CONVECTION | if([BLR_2_STATUS]==0,0,[BLR_2_CONVECTION_DUTY]/[BLR_2_ENERGY_GAINED]*100)
BLR_2_PCT_DUTY_RADIANT | if([BLR_2_STATUS]==0,0,[BLR_2_RADIATION_DUTY]/[BLR_2_ENERGY_GAINED]*100)
BLR_2_DUTY_RATIO_RAD_CONV | if([BLR_2_STATUS]==0,0,[BLR_2_PCT_DUTY_RADIANT]/[BLR_2_PCT_DUTY_CONVECTION])
BLR_2_RADIATION_SECTION_EFF | if([BLR_2_STATUS]==0,0,[BLR_2_RADIATION_DUTY]/[BLR_2_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_2_CONVECTION_SECTION_EFF | if([BLR_2_STATUS]==0,0,[BLR_2_CONVECTION_DUTY]/[BLR_2_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_2_HPS_GEN | if([BLR_2_STEAM_FLOW_RAW]<0,0,[BLR_2_STEAM_FLOW_RAW]/1000)
BLR_2_FUEL_FLOW | [BLR_2_FUEL_GAS_FLOW]*[BLR_2_STATUS]/1000
BLR_2_CAPACITY | 150
BLR_2_SPEC_EN_CONS | if([BLR_2_HPS_GEN]==0,0,[BLR_2_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_2_HPS_GEN])
BLR_2_SPEC_EN_CONS_OPT | (8e-06*[BLR_2_HPS_GEN]^2+-0.0017*[BLR_2_HPS_GEN]+3.0167)*[BLR_2_STATUS]
BLR_2_SPEC_EN_CONS_DEV | if([BLR_2_STATUS]==0,0,([BLR_2_SPEC_EN_CONS_OPT]-[BLR_2_SPEC_EN_CONS])/[BLR_2_SPEC_EN_CONS_OPT])
BLR_2_HPS_GEN_WARMUP | if([BLR_2_STATUS]==0,[BLR_2_HPS_GEN],0)
BLR_2_FD_FAN_STEAM_REG | ((4711.7-39.276*[BLR_2_HPS_GEN]+0.4601*[BLR_2_HPS_GEN]^2)/1000)
BLR_2_FD_FAN_STEAM_WARMUP | if([BLR_2_FD_FAN_STEAM_RAW]>100&&[BLR_2_FD_FAN_STEAM_RAW]<8000&&[BLR_2_STATUS]==0,[BLR_2_FD_FAN_STEAM_RAW]/1000,0)
BLR_2_FD_FAN_STEAM | if([BLR_2_FD_FAN_STEAM_RAW]<500,0,[BLR_2_FD_FAN_STEAM_RAW]/1000)
BLR_3_BOILER_LOAD | [BLR_3_STEAM_FLOW_RAW]/150000*100
BLR_3_STATUS | if([BLR_3_BOILER_LOAD]>25&&[BLR_3_DESUPERHEATER_OUTLET_TEMP]>370&&[BLR_3_HP_STEAM_PRESSURE]>40,1,0)
BLR_3_FUEL_COMP_TOTAL | ([UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]+[UN.UO.BOILER_FG_CH4_CONCENTRATION]+[UN.UO.BOILER_FG_ETHANE_CONCENTRATION]+[UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]+[UN.UO.BOILER_FG_PROPANE_CONCENTRATION]+[UN.UO.BOILER_FG_NC4_CONCENTRATION]+[UN.UO.BOILER_FG_IC4_CONCENTRATION]+[UN.UO.BOILER_FG_NC5_CONCENTRATION]+[UN.UO.BOILER_FG_IC5_CONCENTRATION]+[UN.UO.BOILER_FG_N2_CONCENTRATION])
BLR_3_FG_NORM_CH4 | [UN.UO.BOILER_FG_CH4_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_ETHANE | [UN.UO.BOILER_FG_ETHANE_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_ETHYLENE | [UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_PROPANE | [UN.UO.BOILER_FG_PROPANE_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_CO2 | 0
BLR_3_FG_NORM_IC4 | [UN.UO.BOILER_FG_IC4_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_NC4 | [UN.UO.BOILER_FG_NC4_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_NC5 | [UN.UO.BOILER_FG_NC5_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_IC5 | [UN.UO.BOILER_FG_IC5_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_N2 | [UN.UO.BOILER_FG_N2_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_NORM_H2 | [UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]/[BLR_3_FUEL_COMP_TOTAL]*100
BLR_3_FG_MW | ([BLR_3_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]+[BLR_3_FG_NORM_CH4]*[COMPONENT_METHANE_MW]+[BLR_3_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]+[BLR_3_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]+[BLR_3_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]+[BLR_3_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]+[BLR_3_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]+[BLR_3_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]+[BLR_3_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]+[BLR_3_FG_NORM_N2]*[COMPONENT_NITROGEN_MW])/100
BLR_3_FG_DENSITY | [BLR_3_FG_MW]/22.414
BLR_3_LHV_DESIGN | ([LHV_FG]/[BLR_3_FG_DENSITY])/1000
BLR_3_FG_CH4_MASS_PCT | [BLR_3_FG_NORM_CH4]*[COMPONENT_METHANE_MW]/[BLR_3_FG_MW]
BLR_3_FG_ETHANE_MASS_PCT | [BLR_3_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]/[BLR_3_FG_MW]
BLR_3_FG_ETHYLENE_MASS_PCT | [BLR_3_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]/[BLR_3_FG_MW]
BLR_3_FG_PROPANE_MASS_PCT | [BLR_3_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]/[BLR_3_FG_MW]
BLR_3_FG_N2_MASS_PCT | [BLR_3_FG_NORM_N2]*[COMPONENT_NITROGEN_MW]/[BLR_3_FG_MW]
BLR_3_FG_H2_MASS_PCT | [BLR_3_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]/[BLR_3_FG_MW]
BLR_3_FG_IC4_MASS_PCT | [BLR_3_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]/[BLR_3_FG_MW]
BLR_3_FG_NC4_MASS_PCT | [BLR_3_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]/[BLR_3_FG_MW]
BLR_3_FG_NC5_MASS_PCT | [BLR_3_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]/[BLR_3_FG_MW]
BLR_3_FG_IC5_MASS_PCT | [BLR_3_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]/[BLR_3_FG_MW]
BLR_3_FG_CH4_MASS_FRAC | [BLR_3_FG_CH4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_ETHANE_MASS_FRAC | [BLR_3_FG_ETHANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_ETHYLENE_MASS_FRAC | [BLR_3_FG_ETHYLENE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_PROPANE_MASS_FRAC | [BLR_3_FG_PROPANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_N2_MASS_FRAC | [BLR_3_FG_N2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_H2_MASS_FRAC | [BLR_3_FG_H2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_IC4_MASS_FRAC | [BLR_3_FG_IC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_NC4_MASS_FRAC | [BLR_3_FG_NC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_NC5_MASS_FRAC | [BLR_3_FG_NC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_IC5_MASS_FRAC | [BLR_3_FG_IC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_3_FG_FLOW_RATE_TPH | [BLR_3_FUEL_GAS_FLOW]/1000
BLR_3_AIR_REQ_H2 | [BLR_3_FG_H2_MASS_FRAC]*34.344
BLR_3_AIR_REQ_CH4 | [BLR_3_FG_CH4_MASS_FRAC]*17.265
BLR_3_AIR_REQ_ETHANE | [BLR_3_FG_ETHANE_MASS_FRAC]*16.119
BLR_3_AIR_REQ_ETHYLENE | [BLR_3_FG_ETHYLENE_MASS_FRAC]*14.807
BLR_3_AIR_REQ_PROPANE | [BLR_3_FG_PROPANE_MASS_FRAC]*15.703
BLR_3_AIR_REQ_NC4 | [BLR_3_FG_NC4_MASS_FRAC]*15.487
BLR_3_AIR_REQ_IC4 | [BLR_3_FG_IC4_MASS_FRAC]*15.487
BLR_3_AIR_REQ_NC5 | [BLR_3_FG_NC5_MASS_FRAC]*15.353
BLR_3_AIR_REQ_IC5 | [BLR_3_FG_IC5_MASS_FRAC]*15.353
BLR_3_CO2_COMB_H2 | [BLR_3_FG_H2_MASS_FRAC]*0
BLR_3_CO2_COMB_CH4 | [BLR_3_FG_CH4_MASS_FRAC]*2.744
BLR_3_CO2_COMB_ETHANE | [BLR_3_FG_ETHANE_MASS_FRAC]*2.927
BLR_3_CO2_COMB_ETHYLENE | [BLR_3_FG_ETHYLENE_MASS_FRAC]*3.138
BLR_3_CO2_COMB_PROPANE | [BLR_3_FG_PROPANE_MASS_FRAC]*2.994
BLR_3_CO2_COMB_NC4 | [BLR_3_FG_NC4_MASS_FRAC]*3.029
BLR_3_CO2_COMB_IC4 | [BLR_3_FG_IC4_MASS_FRAC]*3.029
BLR_3_CO2_COMB_NC5 | [BLR_3_FG_NC5_MASS_FRAC]*3.05
BLR_3_CO2_COMB_IC5 | [BLR_3_FG_IC5_MASS_FRAC]*3.05
BLR_3_N2_COMB_H2 | [BLR_3_FG_H2_MASS_FRAC]*26.407
BLR_3_N2_COMB_CH4 | [BLR_3_FG_CH4_MASS_FRAC]*13.275
BLR_3_N2_COMB_ETHANE | [BLR_3_FG_ETHANE_MASS_FRAC]*12.394
BLR_3_N2_COMB_ETHYLENE | [BLR_3_FG_ETHYLENE_MASS_FRAC]*11.385
BLR_3_N2_COMB_PROPANE | [BLR_3_FG_PROPANE_MASS_FRAC]*12.074
BLR_3_N2_COMB_IC4 | [BLR_3_FG_IC4_MASS_FRAC]*11.908
BLR_3_N2_COMB_NC4 | [BLR_3_FG_NC4_MASS_FRAC]*11.908
BLR_3_N2_COMB_IC5 | [BLR_3_FG_IC5_MASS_FRAC]*11.805
BLR_3_N2_COMB_NC5 | [BLR_3_FG_NC5_MASS_FRAC]*11.805
BLR_3_H2O_COMB_H2 | [BLR_3_FG_H2_MASS_FRAC]*8.937
BLR_3_H2O_COMB_CH4 | [BLR_3_FG_CH4_MASS_FRAC]*2.246
BLR_3_H2O_COMB_ETHANE | [BLR_3_FG_ETHANE_MASS_FRAC]*1.798
BLR_3_H2O_COMB_ETHYLENE | [BLR_3_FG_ETHYLENE_MASS_FRAC]*1.285
BLR_3_H2O_COMB_PROPANE | [BLR_3_FG_PROPANE_MASS_FRAC]*1.634
BLR_3_H2O_COMB_IC4 | [BLR_3_FG_NC4_MASS_FRAC]*1.55
BLR_3_H2O_COMB_NC4 | [BLR_3_FG_IC4_MASS_FRAC]*1.55
BLR_3_H2O_COMB_IC5 | [BLR_3_FG_IC5_MASS_FRAC]*1.498
BLR_3_H2O_COMB_NC5 | [BLR_3_FG_NC5_MASS_FRAC]*1.498
BLR_3_AIR_REQ_COMPLETE | [BLR_3_AIR_REQ_H2]+[BLR_3_AIR_REQ_CH4]+[BLR_3_AIR_REQ_ETHANE]+[BLR_3_AIR_REQ_ETHYLENE]+[BLR_3_AIR_REQ_PROPANE]+[BLR_3_AIR_REQ_NC4]+[BLR_3_AIR_REQ_IC4]+[BLR_3_AIR_REQ_NC5]+[BLR_3_AIR_REQ_IC5]
BLR_3_CO2_FORMED | [BLR_3_CO2_COMB_CH4]+[BLR_3_CO2_COMB_ETHANE]+[BLR_3_CO2_COMB_ETHYLENE]+[BLR_3_CO2_COMB_PROPANE]+[BLR_3_CO2_COMB_NC4]+[BLR_3_CO2_COMB_IC4]+[BLR_3_CO2_COMB_NC5]+[BLR_3_CO2_COMB_IC5]
BLR_3_N2_FORMED | [BLR_3_N2_COMB_H2]+[BLR_3_N2_COMB_CH4]+[BLR_3_N2_COMB_ETHANE]+[BLR_3_N2_COMB_ETHYLENE]+[BLR_3_N2_COMB_PROPANE]+[BLR_3_N2_COMB_IC4]+[BLR_3_N2_COMB_NC4]+[BLR_3_N2_COMB_IC5]+[BLR_3_N2_COMB_NC5]
BLR_3_H2O_FORMED | [BLR_3_H2O_COMB_H2]+[BLR_3_H2O_COMB_CH4]+[BLR_3_H2O_COMB_ETHANE]+[BLR_3_H2O_COMB_ETHYLENE]+[BLR_3_H2O_COMB_PROPANE]+[BLR_3_H2O_COMB_IC4]+[BLR_3_H2O_COMB_NC4]+[BLR_3_H2O_COMB_IC5]+[BLR_3_H2O_COMB_NC5]
BLR_3_VAPOUR_PRESSURE_H2O | 10^(8.07131-(1730.63/(233.426+[UN.UO.AMBIENT_TEMP])))
BLR_3_AIR_MOISTURE | [BLR_3_VAPOUR_PRESSURE_H2O]/(760-[BLR_3_VAPOUR_PRESSURE_H2O]*[UN.UO.RELATIVE_HUMIDITY_CLEAN])*[UN.UO.RELATIVE_HUMIDITY_CLEAN]*18.015/28.96
BLR_3_CORRECTED_COMBUSTION_AIR | [BLR_3_AIR_REQ_COMPLETE]/(1-[BLR_3_AIR_MOISTURE])
BLR_3_CORRECTED_H2O_FORMED | [BLR_3_H2O_FORMED]+([BLR_3_CORRECTED_COMBUSTION_AIR]-[BLR_3_AIR_REQ_COMPLETE])
BLR_3_EXCESS_AIR | ((28.96*[BLR_3_FLUE_GAS_OXYGEN])*([BLR_3_N2_FORMED]/28.01+[BLR_3_CORRECTED_H2O_FORMED]/18.015+[BLR_3_CO2_FORMED]/44.01)/(20.95-[BLR_3_FLUE_GAS_OXYGEN]))
BLR_3_AIR_FUEL_MASS_RATIO | [BLR_3_EXCESS_AIR]+[BLR_3_CORRECTED_COMBUSTION_AIR]
BLR_3_TOTAL_MOISTURE_WITH_AIR | [BLR_3_AIR_FUEL_MASS_RATIO]*[BLR_3_AIR_MOISTURE]
BLR_3_TOTAL_H2O_PER_KG_FUEL | [BLR_3_TOTAL_MOISTURE_WITH_AIR]+[BLR_3_H2O_FORMED]
BLR_3_DRY_FLUE_GAS_RATIO | [BLR_3_EXCESS_AIR]*(1-[BLR_3_AIR_MOISTURE])+[BLR_3_N2_FORMED]+[BLR_3_CO2_FORMED]
BLR_3_FLUE_GAS_RATIO | [BLR_3_DRY_FLUE_GAS_RATIO]+[BLR_3_TOTAL_H2O_PER_KG_FUEL]
BLR_3_FLUE_GAS_MW | [BLR_3_FLUE_GAS_RATIO]/([BLR_3_CO2_FORMED]/44.01+[BLR_3_TOTAL_H2O_PER_KG_FUEL]/18.015+[BLR_3_N2_FORMED]/28.01+[BLR_3_EXCESS_AIR]/28.96)
BLR_3_AIR_CP_REF_T | 6.96
BLR_3_CP_AT_COMB_TEMP | (((28.98641)+1.85398*(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_3_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_3_AIR_CP_SENSIBLE_CORRECTED | (([BLR_3_AIR_CP_REF_T]+[BLR_3_CP_AT_COMB_TEMP])/2)/28.96
BLR_3_CP_H2_FUEL_TEMP | ((33.066178)-11.363417*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)+11.432816*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-2.772874*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(-0.158558/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_CH4_FUEL_TEMP | ((-0.703029)+108.4773*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-42.52157*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+5.862788*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.678565/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_ETHANE_FUEL_TEMP | (6.08161+173.58246*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-66.91905*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+9.08912*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.129136/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_PROPANE_FUEL_TEMP | (12.66081+232.07025*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-70.34461*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+0.60714*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.026957/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_ETHYLENE_FUEL_TEMP | (-6.38788+184.4019*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-112.9718*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+28.49593*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+0.31554/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2)*0.239
BLR_3_CP_NC4_FUEL_TEMP | (22.1581+292.5894*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-85.8165*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-1.01394*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.00635/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_IC4_FUEL_TEMP | (8.32666+344.92332*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-141.6499*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-17.40270*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.02600/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_NC5_FUEL_TEMP | (-36.73509+580.37577*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-341.58654*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-78.49965*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(1.08617/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_IC5_FUEL_TEMP | (-16.14269+517.36368*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-271.31408*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-56.15662*(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.31713/(([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_FUEL_AT_REF_TEMP | (([BLR_3_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*6.876+[BLR_3_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*8.45+([BLR_3_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*10.02+([BLR_3_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*12.52+([BLR_3_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*17.72+([BLR_3_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79)+([BLR_3_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26+[BLR_3_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79+[BLR_3_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26)))*[BLR_3_FG_MW]
BLR_3_CP_FUEL_AT_FUEL_TEMP | (([BLR_3_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*[BLR_3_CP_H2_FUEL_TEMP]+[BLR_3_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*[BLR_3_CP_CH4_FUEL_TEMP]+([BLR_3_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*[BLR_3_CP_ETHYLENE_FUEL_TEMP]+([BLR_3_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*[BLR_3_CP_ETHANE_FUEL_TEMP]+([BLR_3_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*[BLR_3_CP_PROPANE_FUEL_TEMP]+([BLR_3_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_3_CP_NC4_FUEL_TEMP])+([BLR_3_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_3_CP_NC5_FUEL_TEMP]+[BLR_3_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_3_CP_IC4_FUEL_TEMP]+[BLR_3_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_3_CP_IC5_FUEL_TEMP])))*[BLR_3_FG_MW]
BLR_3_AVG_CP_FUEL_SENSIBLE | (([BLR_3_CP_FUEL_AT_REF_TEMP]+[BLR_3_CP_FUEL_AT_FUEL_TEMP])/[BLR_3_FG_MW])/2
BLR_3_CP_AIR_AT_STACK_TEMP | (((28.98641)+1.85398*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_3_CP_FLUE_CO2_AT_STACK | ((24.99735)+55.18696*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)-33.69137*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2+7.948387*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.136638/(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_CP_FLUE_H2O_AT_STACK | 8.22+0.00015*([BLR_3_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_3_STACK_TEMPERATURE]+273.15)^2)
BLR_3_CP_FLUE_N2_AT_STACK | ((28.98641)+1.85398*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_3_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_3_AVG_CP_FLUE_AT_STACK | ([BLR_3_CP_FLUE_CO2_AT_STACK]*[BLR_3_CO2_FORMED]/44.01+[BLR_3_CP_FLUE_N2_AT_STACK]*[BLR_3_N2_FORMED]/28.01+[BLR_3_EXCESS_AIR]/28.85*[BLR_3_CP_AIR_AT_STACK_TEMP])/([BLR_3_FLUE_GAS_RATIO]/[BLR_3_FLUE_GAS_MW])/[BLR_3_FLUE_GAS_MW]
BLR_3_CP_H2O_AT_STACK | (8.22+0.00015*([BLR_3_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_3_STACK_TEMPERATURE]+273.15)^2))/18.015
BLR_3_SH_CORRECTION_FUEL | if([BLR_3_AVG_CP_FUEL_SENSIBLE]*([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]-15.6)<0,0,[BLR_3_AVG_CP_FUEL_SENSIBLE]*([BLR_3_MAIN_FUEL_GAS_TEMPERATURE]-15.6))
BLR_3_SH_CORRECTION_AIR | [BLR_3_AIR_CP_SENSIBLE_CORRECTED]*([BLR_3_COMBUSTION_AIR_TEMPERATURE]-15.6)*[BLR_3_AIR_FUEL_MASS_RATIO]
BLR_3_MIXED_LHV_PER_KG | [UN.UO.BOILER_LHV]
BLR_3_TOTAL_HEAT_INPUT | if([BLR_3_STATUS]==0,0,[BLR_3_SH_CORRECTION_FUEL]+[BLR_3_SH_CORRECTION_AIR]+[BLR_3_MIXED_LHV_PER_KG])
BLR_3_HEAT_LOSS_L1 | if([BLR_3_STATUS]==0,0,[BLR_3_DRY_FLUE_GAS_RATIO]*([BLR_3_AVG_CP_FLUE_AT_STACK]*([BLR_3_STACK_TEMPERATURE]-15.6)))
BLR_3_HEAT_LOSS_L2 | if([BLR_3_STATUS]==0,0,9*[BLR_3_FG_H2_MASS_FRAC]*(584+[BLR_3_CP_H2O_AT_STACK]*([BLR_3_STACK_TEMPERATURE]-[UN.UO.AMBIENT_TEMP])))
BLR_3_HEAT_LOSS_L3 | if([BLR_3_STATUS]==0,0,[BLR_3_TOTAL_H2O_PER_KG_FUEL]*([BLR_3_STACK_TEMPERATURE]*1.77251246754294+2494.5133413964-2529.43)/4.184)
BLR_3_HEAT_LOSS_L4 | if([BLR_3_STATUS]==0,0,0*10^-6*28*5654*[BLR_3_BOILER_LOAD])
BLR_3_TOTAL_STACK_LOSS_PER_KG | if([BLR_3_STATUS]==0,0,[BLR_3_HEAT_LOSS_L4]+[BLR_3_HEAT_LOSS_L3]+[BLR_3_HEAT_LOSS_L1]+[BLR_3_HEAT_LOSS_L2])
BLR_3_RADIATION_LOSSES | if([BLR_3_STATUS]==0,0,[BLR_3_MIXED_LHV_PER_KG]*(-0.000004*[BLR_3_BOILER_LOAD]^3+0.001*[BLR_3_BOILER_LOAD]^2-0.0899*[BLR_3_BOILER_LOAD]+3.2426)/100)
BLR_3_TOTAL_HEAT_LOSS | if([BLR_3_STATUS]==0,0,[BLR_3_TOTAL_STACK_LOSS_PER_KG]+[BLR_3_RADIATION_LOSSES])
BLR_3_TOTAL_HEAT_ABSORBED | if([BLR_3_STATUS]==0,0,[BLR_3_TOTAL_HEAT_INPUT]-[BLR_3_TOTAL_HEAT_LOSS])
BLR_3_INDIRECT_EFFICIENCY | if([BLR_3_STATUS]==0,0,[BLR_3_TOTAL_HEAT_ABSORBED]/[BLR_3_TOTAL_HEAT_INPUT]*100)
BLR_3_HP_STEAM_ENTHALPY | if([BLR_3_STATUS]==0,0,(2175.54628147543-1.32764297764643*[BLR_3_HP_STEAM_PRESSURE]+2.66244961166282*[BLR_3_DESUPERHEATER_OUTLET_TEMP])*0.239+2)
BLR_3_TOTAL_STEAM_ENERGY | if([BLR_3_STATUS]==0,0,[BLR_3_STEAM_FLOW_RAW]*[BLR_3_HP_STEAM_ENTHALPY]/1000000)
BLR_3_BFW_ENTHALPY | if([BLR_3_STATUS]==0,0,[BLR_3_ECONOMIZER_INLET_TEMP])
BLR_3_CORRECTED_BFW_FLOW | if([BLR_3_STATUS]==0,0,([BLR_3_BFW_TO_ECONOMIZER]+[BLR_3_BFW_TO_DESUPERHEATER]-([BLR_3_BFW_TO_ECONOMIZER]+[BLR_3_BFW_TO_DESUPERHEATER]-[BLR_3_STEAM_FLOW_RAW]-[BLR_3_CBD_BLOWDOWN]))/1000)
BLR_3_BFW_ENERGY | if([BLR_3_STATUS]==0,0,[BLR_3_CORRECTED_BFW_FLOW]*[BLR_3_BFW_ENTHALPY]/1000)
BLR_3_FUEL_GAS_ENERGY_INPUT | if([BLR_3_STATUS]==0,0,[BLR_3_FG_FLOW_RATE_TPH]*1000*[BLR_3_MIXED_LHV_PER_KG]/10^6)
BLR_3_STEAM_DRUM_TEMP | if([BLR_3_STATUS]==0,0,4.02521999671835*log([BLR_3_STEAM_DRUM_PRESSURE]*98.065)^3-4.64392873298701*log([BLR_3_STEAM_DRUM_PRESSURE]*98.065)^2+11.2370106828649*log([BLR_3_STEAM_DRUM_PRESSURE]*98.065)+83.4806425229703)
BLR_3_BLOWDOWN_LOSS | if([BLR_3_STATUS]==0,0,(([BLR_3_CBD_BLOWDOWN]/1000)*(([BLR_3_STEAM_DRUM_PRESSURE]*2.11087739028321+[BLR_3_SUPERHEATER_INLET_TEMP]*2.94757709065418+278.050085762461)*0.2390006-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.0678913878546345+[BLR_3_SUPERHEATER_INLET_TEMP]*4.22416911685416-3.01717714574329)*0.2390006))/1000)
BLR_3_TOTAL_FLUE_GAS_GENERATED | if([BLR_3_STATUS]==0,0,[BLR_3_FUEL_GAS_FLOW]/1000*[BLR_3_FLUE_GAS_RATIO])
BLR_3_STACK_LOSS | if([BLR_3_STATUS]==0,0,[BLR_3_TOTAL_STACK_LOSS_PER_KG]*[BLR_3_FUEL_GAS_FLOW]/(1000*1000))
BLR_3_CORRECTED_FUEL_FLOW | if([BLR_3_STATUS]==0,0,[BLR_3_FUEL_GAS_FLOW]-(([BLR_3_FUEL_GAS_ENERGY_INPUT]-([BLR_3_TOTAL_STEAM_ENERGY]-[BLR_3_BFW_ENERGY]+[BLR_3_BLOWDOWN_LOSS]+[BLR_3_STACK_LOSS]+[BLR_3_FUEL_GAS_ENERGY_INPUT]*0.0112+[BLR_3_FUEL_GAS_ENERGY_INPUT]*(-0.000004*[BLR_3_BOILER_LOAD]^3+0.001*[BLR_3_BOILER_LOAD]^2-0.0899*[BLR_3_BOILER_LOAD]+3.2426)/100+([BLR_3_HEAT_LOSS_L3]*([BLR_3_FUEL_GAS_FLOW]/1000)*0.239006/1000)))/[BLR_3_MIXED_LHV_PER_KG]/1000))
BLR_3_FUEL_CONSUMPTION_GCAL | if([BLR_3_STATUS]==0,0,[BLR_3_CORRECTED_FUEL_FLOW]*[BLR_3_MIXED_LHV_PER_KG]/10^6)
BLR_3_SEC_GCAL_T | if([BLR_3_STATUS]==0,0,[BLR_3_FUEL_CONSUMPTION_GCAL]/([BLR_3_STEAM_FLOW_RAW]/1000))
BLR_3_SEC_GJ_T | if([BLR_3_STATUS]==0,0,[BLR_3_FUEL_CONSUMPTION_GCAL]/([BLR_3_STEAM_FLOW_RAW]/1000)*4.184)
BLR_3_CORRECTED_FUEL_ENERGY_INPUT | if([BLR_3_STATUS]==0,0,[BLR_3_CORRECTED_FUEL_FLOW]*[BLR_3_MIXED_LHV_PER_KG]/10^6)
BLR_3_THERMAL_EFFICIENCY | if([BLR_3_STATUS]==0,0,([BLR_3_TOTAL_STEAM_ENERGY]-[BLR_3_BFW_ENERGY])/[BLR_3_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_3_FUEL_GAS_CORRECTED_TPH | if([BLR_3_STATUS]==0,0,[BLR_3_CORRECTED_FUEL_FLOW]/1000)
BLR_3_TOTAL_FLUE_GAS_CORRECTED | if([BLR_3_STATUS]==0,0,[BLR_3_FUEL_GAS_CORRECTED_TPH]*[BLR_3_FLUE_GAS_RATIO])
BLR_3_STACK_LOSS_CORRECTED | if([BLR_3_STATUS]==0,0,[BLR_3_TOTAL_STACK_LOSS_PER_KG]*[BLR_3_FUEL_GAS_CORRECTED_TPH]/1000)
BLR_3_BFW_STEAM_RATIO | if([BLR_3_STATUS]==0,0,([BLR_3_STEAM_FLOW_RAW]+[BLR_3_CBD_BLOWDOWN])/([BLR_3_CORRECTED_BFW_FLOW]*1000))
BLR_3_CO2_EMISSIONS | if([BLR_3_STATUS]==0,0,[BLR_3_CO2_FORMED]*[BLR_3_FUEL_GAS_CORRECTED_TPH])
BLR_3_CALCULATED_AIRFLOW_NM3H | if([BLR_3_STATUS]==0,0,[BLR_3_AIR_FUEL_MASS_RATIO]*[BLR_3_CORRECTED_FUEL_FLOW]/(28.96/22.414)/1000)
BLR_3_STEAM_TO_FIRE_RATIO | if([BLR_3_STATUS]==0,0,[BLR_3_STEAM_FLOW_RAW]/([BLR_3_FG_FLOW_RATE_TPH]*[BLR_3_MIXED_LHV_PER_KG])*1000)
BLR_3_ECONOMIZER_DUTY | if([BLR_3_STATUS]==0,0,[BLR_3_CORRECTED_BFW_FLOW]*(([BLR_3_STEAM_DRUM_PRESSURE]*0.033652+[BLR_3_ECONOMIZER_OUTLET_TEMP]*4.52730-53.56679)-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.067891+[BLR_3_ECONOMIZER_INLET_TEMP]*4.22417-3.01718))*0.239006/1000)
BLR_3_LMTD_ECONOMIZER | if([BLR_3_STATUS]==0,0,((673-[BLR_3_ECONOMIZER_OUTLET_TEMP])-([BLR_3_STACK_TEMPERATURE]-[BLR_3_ECONOMIZER_INLET_TEMP]))/ln((673-[BLR_3_ECONOMIZER_OUTLET_TEMP])/(-[BLR_3_ECONOMIZER_INLET_TEMP]+[BLR_3_STACK_TEMPERATURE])))
BLR_3_UA_ECONOMIZER | if([BLR_3_STATUS]==0,0,[BLR_3_ECONOMIZER_DUTY]/[BLR_3_LMTD_ECONOMIZER])
BLR_3_FOULING_INDEX | if([BLR_3_STATUS]==0,0,1/[BLR_3_UA_ECONOMIZER])
BLR_3_SH_DUTY | if([BLR_3_STATUS]==0,0,[BLR_3_STEAM_FLOW_RAW]*(([BLR_3_STEAM_DRUM_PRESSURE]*-2.64315+[BLR_3_DESUPERHEATER_TEMPERATURE]*3.58096+1939.73413)-([BLR_3_STEAM_DRUM_PRESSURE]*-4.27591+[BLR_3_SUPERHEATER_INLET_TEMP]*3.45878+2082.10231))*0.239006/1000000)
BLR_3_SH_SPECIFIC_DUTY | if([BLR_3_STATUS]==0,0,[BLR_3_SH_DUTY]/[BLR_3_STEAM_FLOW_RAW]*1000)
BLR_3_SH_PERFORMANCE | if([BLR_3_STATUS]==0,0,[BLR_3_SH_SPECIFIC_DUTY]/0.128049016*100)
BLR_3_ENERGY_GAINED | if([BLR_3_STATUS]==0,0,[BLR_3_TOTAL_STEAM_ENERGY]-[BLR_3_BFW_ENERGY])
BLR_3_CONVECTION_DUTY | if([BLR_3_STATUS]==0,0,[BLR_3_ECONOMIZER_DUTY]+[BLR_3_SH_DUTY]+[BLR_3_STACK_LOSS_CORRECTED])
BLR_3_RADIATION_DUTY | if([BLR_3_STATUS]==0,0,[BLR_3_ENERGY_GAINED]-[BLR_3_CONVECTION_DUTY])
BLR_3_PCT_DUTY_CONVECTION | if([BLR_3_STATUS]==0,0,[BLR_3_CONVECTION_DUTY]/[BLR_3_ENERGY_GAINED]*100)
BLR_3_PCT_DUTY_RADIANT | if([BLR_3_STATUS]==0,0,[BLR_3_RADIATION_DUTY]/[BLR_3_ENERGY_GAINED]*100)
BLR_3_DUTY_RATIO_RAD_CONV | if([BLR_3_STATUS]==0,0,[BLR_3_PCT_DUTY_RADIANT]/[BLR_3_PCT_DUTY_CONVECTION])
BLR_3_RADIATION_SECTION_EFF | if([BLR_3_STATUS]==0,0,[BLR_3_RADIATION_DUTY]/[BLR_3_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_3_CONVECTION_SECTION_EFF | if([BLR_3_STATUS]==0,0,[BLR_3_CONVECTION_DUTY]/[BLR_3_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_3_HPS_GEN | if([BLR_3_STEAM_FLOW_RAW]<0,0,[BLR_3_STEAM_FLOW_RAW]/1000)
BLR_3_FUEL_FLOW | [BLR_3_FUEL_GAS_FLOW]*[BLR_3_STATUS]/1000
BLR_3_CAPACITY | 150
BLR_3_SPEC_EN_CONS | if([BLR_3_HPS_GEN]==0,0,[BLR_3_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_3_HPS_GEN])
BLR_3_SPEC_EN_CONS_OPT | (8e-06*[BLR_3_HPS_GEN]^2+-0.0017*[BLR_3_HPS_GEN]+3.0167)*[BLR_3_STATUS]
BLR_3_SPEC_EN_CONS_DEV | if([BLR_3_STATUS]==0,0,([BLR_3_SPEC_EN_CONS_OPT]-[BLR_3_SPEC_EN_CONS])/[BLR_3_SPEC_EN_CONS_OPT])
BLR_3_HPS_GEN_WARMUP | if([BLR_3_STATUS]==0,[BLR_3_HPS_GEN],0)
BLR_3_FD_FAN_STEAM_REG | ((4701.3-35.004*[BLR_3_HPS_GEN]+0.4481*[BLR_3_HPS_GEN]^2)/1000)
BLR_3_FD_FAN_STEAM_WARMUP | if([BLR_3_FD_FAN_STEAM_RAW]>100&&[BLR_3_FD_FAN_STEAM_RAW]<8000&&[BLR_3_STATUS]==0,[BLR_3_FD_FAN_STEAM_RAW]/1000,0)
BLR_3_FD_FAN_STEAM | if([BLR_3_FD_FAN_STEAM_RAW]<500,0,[BLR_3_FD_FAN_STEAM_RAW]/1000)
BLR_4_BOILER_LOAD | [BLR_4_STEAM_FLOW_RAW]/150000*100
BLR_4_STATUS | if([BLR_4_BOILER_LOAD]>25&&[BLR_4_DESUPERHEATER_OUTLET_TEMP]>370&&[BLR_4_HP_STEAM_PRESSURE]>40,1,0)
BLR_4_FUEL_COMP_TOTAL | ([UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]+[UN.UO.BOILER_FG_CH4_CONCENTRATION]+[UN.UO.BOILER_FG_ETHANE_CONCENTRATION]+[UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]+[UN.UO.BOILER_FG_PROPANE_CONCENTRATION]+[UN.UO.BOILER_FG_NC4_CONCENTRATION]+[UN.UO.BOILER_FG_IC4_CONCENTRATION]+[UN.UO.BOILER_FG_NC5_CONCENTRATION]+[UN.UO.BOILER_FG_IC5_CONCENTRATION]+[UN.UO.BOILER_FG_N2_CONCENTRATION])
BLR_4_FG_NORM_CH4 | [UN.UO.BOILER_FG_CH4_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_ETHANE | [UN.UO.BOILER_FG_ETHANE_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_ETHYLENE | [UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_PROPANE | [UN.UO.BOILER_FG_PROPANE_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_CO2 | 0
BLR_4_FG_NORM_IC4 | [UN.UO.BOILER_FG_IC4_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_NC4 | [UN.UO.BOILER_FG_NC4_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_NC5 | [UN.UO.BOILER_FG_NC5_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_IC5 | [UN.UO.BOILER_FG_IC5_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_N2 | [UN.UO.BOILER_FG_N2_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_NORM_H2 | [UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]/[BLR_4_FUEL_COMP_TOTAL]*100
BLR_4_FG_MW | ([BLR_4_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]+[BLR_4_FG_NORM_CH4]*[COMPONENT_METHANE_MW]+[BLR_4_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]+[BLR_4_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]+[BLR_4_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]+[BLR_4_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]+[BLR_4_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]+[BLR_4_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]+[BLR_4_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]+[BLR_4_FG_NORM_N2]*[COMPONENT_NITROGEN_MW])/100
BLR_4_FG_DENSITY | [BLR_4_FG_MW]/22.414
BLR_4_LHV_DESIGN | ([LHV_FG]/[BLR_4_FG_DENSITY])/1000
BLR_4_FG_CH4_MASS_PCT | [BLR_4_FG_NORM_CH4]*[COMPONENT_METHANE_MW]/[BLR_4_FG_MW]
BLR_4_FG_ETHANE_MASS_PCT | [BLR_4_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]/[BLR_4_FG_MW]
BLR_4_FG_ETHYLENE_MASS_PCT | [BLR_4_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]/[BLR_4_FG_MW]
BLR_4_FG_PROPANE_MASS_PCT | [BLR_4_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]/[BLR_4_FG_MW]
BLR_4_FG_N2_MASS_PCT | [BLR_4_FG_NORM_N2]*[COMPONENT_NITROGEN_MW]/[BLR_4_FG_MW]
BLR_4_FG_H2_MASS_PCT | [BLR_4_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]/[BLR_4_FG_MW]
BLR_4_FG_IC4_MASS_PCT | [BLR_4_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]/[BLR_4_FG_MW]
BLR_4_FG_NC4_MASS_PCT | [BLR_4_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]/[BLR_4_FG_MW]
BLR_4_FG_NC5_MASS_PCT | [BLR_4_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]/[BLR_4_FG_MW]
BLR_4_FG_IC5_MASS_PCT | [BLR_4_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]/[BLR_4_FG_MW]
BLR_4_FG_CH4_MASS_FRAC | [BLR_4_FG_CH4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_ETHANE_MASS_FRAC | [BLR_4_FG_ETHANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_ETHYLENE_MASS_FRAC | [BLR_4_FG_ETHYLENE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_PROPANE_MASS_FRAC | [BLR_4_FG_PROPANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_N2_MASS_FRAC | [BLR_4_FG_N2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_H2_MASS_FRAC | [BLR_4_FG_H2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_IC4_MASS_FRAC | [BLR_4_FG_IC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_NC4_MASS_FRAC | [BLR_4_FG_NC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_NC5_MASS_FRAC | [BLR_4_FG_NC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_IC5_MASS_FRAC | [BLR_4_FG_IC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_4_FG_FLOW_RATE_TPH | [BLR_4_FUEL_GAS_FLOW]/1000
BLR_4_AIR_REQ_H2 | [BLR_4_FG_H2_MASS_FRAC]*34.344
BLR_4_AIR_REQ_CH4 | [BLR_4_FG_CH4_MASS_FRAC]*17.265
BLR_4_AIR_REQ_ETHANE | [BLR_4_FG_ETHANE_MASS_FRAC]*16.119
BLR_4_AIR_REQ_ETHYLENE | [BLR_4_FG_ETHYLENE_MASS_FRAC]*14.807
BLR_4_AIR_REQ_PROPANE | [BLR_4_FG_PROPANE_MASS_FRAC]*15.703
BLR_4_AIR_REQ_NC4 | [BLR_4_FG_NC4_MASS_FRAC]*15.487
BLR_4_AIR_REQ_IC4 | [BLR_4_FG_IC4_MASS_FRAC]*15.487
BLR_4_AIR_REQ_NC5 | [BLR_4_FG_NC5_MASS_FRAC]*15.353
BLR_4_AIR_REQ_IC5 | [BLR_4_FG_IC5_MASS_FRAC]*15.353
BLR_4_CO2_COMB_H2 | [BLR_4_FG_H2_MASS_FRAC]*0
BLR_4_CO2_COMB_CH4 | [BLR_4_FG_CH4_MASS_FRAC]*2.744
BLR_4_CO2_COMB_ETHANE | [BLR_4_FG_ETHANE_MASS_FRAC]*2.927
BLR_4_CO2_COMB_ETHYLENE | [BLR_4_FG_ETHYLENE_MASS_FRAC]*3.138
BLR_4_CO2_COMB_PROPANE | [BLR_4_FG_PROPANE_MASS_FRAC]*2.994
BLR_4_CO2_COMB_NC4 | [BLR_4_FG_NC4_MASS_FRAC]*3.029
BLR_4_CO2_COMB_IC4 | [BLR_4_FG_IC4_MASS_FRAC]*3.029
BLR_4_CO2_COMB_NC5 | [BLR_4_FG_NC5_MASS_FRAC]*3.05
BLR_4_CO2_COMB_IC5 | [BLR_4_FG_IC5_MASS_FRAC]*3.05
BLR_4_N2_COMB_H2 | [BLR_4_FG_H2_MASS_FRAC]*26.407
BLR_4_N2_COMB_CH4 | [BLR_4_FG_CH4_MASS_FRAC]*13.275
BLR_4_N2_COMB_ETHANE | [BLR_4_FG_ETHANE_MASS_FRAC]*12.394
BLR_4_N2_COMB_ETHYLENE | [BLR_4_FG_ETHYLENE_MASS_FRAC]*11.385
BLR_4_N2_COMB_PROPANE | [BLR_4_FG_PROPANE_MASS_FRAC]*12.074
BLR_4_N2_COMB_IC4 | [BLR_4_FG_IC4_MASS_FRAC]*11.908
BLR_4_N2_COMB_NC4 | [BLR_4_FG_NC4_MASS_FRAC]*11.908
BLR_4_N2_COMB_IC5 | [BLR_4_FG_IC5_MASS_FRAC]*11.805
BLR_4_N2_COMB_NC5 | [BLR_4_FG_NC5_MASS_FRAC]*11.805
BLR_4_H2O_COMB_H2 | [BLR_4_FG_H2_MASS_FRAC]*8.937
BLR_4_H2O_COMB_CH4 | [BLR_4_FG_CH4_MASS_FRAC]*2.246
BLR_4_H2O_COMB_ETHANE | [BLR_4_FG_ETHANE_MASS_FRAC]*1.798
BLR_4_H2O_COMB_ETHYLENE | [BLR_4_FG_ETHYLENE_MASS_FRAC]*1.285
BLR_4_H2O_COMB_PROPANE | [BLR_4_FG_PROPANE_MASS_FRAC]*1.634
BLR_4_H2O_COMB_IC4 | [BLR_4_FG_NC4_MASS_FRAC]*1.55
BLR_4_H2O_COMB_NC4 | [BLR_4_FG_IC4_MASS_FRAC]*1.55
BLR_4_H2O_COMB_IC5 | [BLR_4_FG_IC5_MASS_FRAC]*1.498
BLR_4_H2O_COMB_NC5 | [BLR_4_FG_NC5_MASS_FRAC]*1.498
BLR_4_AIR_REQ_COMPLETE | [BLR_4_AIR_REQ_H2]+[BLR_4_AIR_REQ_CH4]+[BLR_4_AIR_REQ_ETHANE]+[BLR_4_AIR_REQ_ETHYLENE]+[BLR_4_AIR_REQ_PROPANE]+[BLR_4_AIR_REQ_NC4]+[BLR_4_AIR_REQ_IC4]+[BLR_4_AIR_REQ_NC5]+[BLR_4_AIR_REQ_IC5]
BLR_4_CO2_FORMED | [BLR_4_CO2_COMB_CH4]+[BLR_4_CO2_COMB_ETHANE]+[BLR_4_CO2_COMB_ETHYLENE]+[BLR_4_CO2_COMB_PROPANE]+[BLR_4_CO2_COMB_NC4]+[BLR_4_CO2_COMB_IC4]+[BLR_4_CO2_COMB_NC5]+[BLR_4_CO2_COMB_IC5]
BLR_4_N2_FORMED | [BLR_4_N2_COMB_H2]+[BLR_4_N2_COMB_CH4]+[BLR_4_N2_COMB_ETHANE]+[BLR_4_N2_COMB_ETHYLENE]+[BLR_4_N2_COMB_PROPANE]+[BLR_4_N2_COMB_IC4]+[BLR_4_N2_COMB_NC4]+[BLR_4_N2_COMB_IC5]+[BLR_4_N2_COMB_NC5]
BLR_4_H2O_FORMED | [BLR_4_H2O_COMB_H2]+[BLR_4_H2O_COMB_CH4]+[BLR_4_H2O_COMB_ETHANE]+[BLR_4_H2O_COMB_ETHYLENE]+[BLR_4_H2O_COMB_PROPANE]+[BLR_4_H2O_COMB_IC4]+[BLR_4_H2O_COMB_NC4]+[BLR_4_H2O_COMB_IC5]+[BLR_4_H2O_COMB_NC5]
BLR_4_VAPOUR_PRESSURE_H2O | 10^(8.07131-(1730.63/(233.426+[UN.UO.AMBIENT_TEMP])))
BLR_4_AIR_MOISTURE | [BLR_4_VAPOUR_PRESSURE_H2O]/(760-[BLR_4_VAPOUR_PRESSURE_H2O]*[UN.UO.RELATIVE_HUMIDITY_CLEAN])*[UN.UO.RELATIVE_HUMIDITY_CLEAN]*18.015/28.96
BLR_4_CORRECTED_COMBUSTION_AIR | [BLR_4_AIR_REQ_COMPLETE]/(1-[BLR_4_AIR_MOISTURE])
BLR_4_CORRECTED_H2O_FORMED | [BLR_4_H2O_FORMED]+([BLR_4_CORRECTED_COMBUSTION_AIR]-[BLR_4_AIR_REQ_COMPLETE])
BLR_4_EXCESS_AIR | ((28.96*[BLR_4_FLUE_GAS_OXYGEN])*([BLR_4_N2_FORMED]/28.01+[BLR_4_CORRECTED_H2O_FORMED]/18.015+[BLR_4_CO2_FORMED]/44.01)/(20.95-[BLR_4_FLUE_GAS_OXYGEN]))
BLR_4_AIR_FUEL_MASS_RATIO | [BLR_4_EXCESS_AIR]+[BLR_4_CORRECTED_COMBUSTION_AIR]
BLR_4_TOTAL_MOISTURE_WITH_AIR | [BLR_4_AIR_FUEL_MASS_RATIO]*[BLR_4_AIR_MOISTURE]
BLR_4_TOTAL_H2O_PER_KG_FUEL | [BLR_4_TOTAL_MOISTURE_WITH_AIR]+[BLR_4_H2O_FORMED]
BLR_4_DRY_FLUE_GAS_RATIO | [BLR_4_EXCESS_AIR]*(1-[BLR_4_AIR_MOISTURE])+[BLR_4_N2_FORMED]+[BLR_4_CO2_FORMED]
BLR_4_FLUE_GAS_RATIO | [BLR_4_DRY_FLUE_GAS_RATIO]+[BLR_4_TOTAL_H2O_PER_KG_FUEL]
BLR_4_FLUE_GAS_MW | [BLR_4_FLUE_GAS_RATIO]/([BLR_4_CO2_FORMED]/44.01+[BLR_4_TOTAL_H2O_PER_KG_FUEL]/18.015+[BLR_4_N2_FORMED]/28.01+[BLR_4_EXCESS_AIR]/28.96)
BLR_4_AIR_CP_REF_T | 6.96
BLR_4_CP_AT_COMB_TEMP | (((28.98641)+1.85398*(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_4_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_4_AIR_CP_SENSIBLE_CORRECTED | (([BLR_4_AIR_CP_REF_T]+[BLR_4_CP_AT_COMB_TEMP])/2)/28.96
BLR_4_CP_H2_FUEL_TEMP | ((33.066178)-11.363417*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)+11.432816*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-2.772874*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(-0.158558/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_CH4_FUEL_TEMP | ((-0.703029)+108.4773*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-42.52157*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+5.862788*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.678565/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_ETHANE_FUEL_TEMP | (6.08161+173.58246*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-66.91905*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+9.08912*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.129136/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_PROPANE_FUEL_TEMP | (12.66081+232.07025*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-70.34461*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+0.60714*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.026957/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_ETHYLENE_FUEL_TEMP | (-6.38788+184.4019*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-112.9718*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+28.49593*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+0.31554/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2)*0.239
BLR_4_CP_NC4_FUEL_TEMP | (22.1581+292.5894*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-85.8165*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-1.01394*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.00635/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_IC4_FUEL_TEMP | (8.32666+344.92332*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-141.6499*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-17.40270*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.02600/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_NC5_FUEL_TEMP | (-36.73509+580.37577*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-341.58654*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-78.49965*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(1.08617/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_IC5_FUEL_TEMP | (-16.14269+517.36368*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-271.31408*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-56.15662*(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.31713/(([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_FUEL_AT_REF_TEMP | (([BLR_4_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*6.876+[BLR_4_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*8.45+([BLR_4_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*10.02+([BLR_4_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*12.52+([BLR_4_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*17.72+([BLR_4_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79)+([BLR_4_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26+[BLR_4_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79+[BLR_4_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26)))*[BLR_4_FG_MW]
BLR_4_CP_FUEL_AT_FUEL_TEMP | (([BLR_4_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*[BLR_4_CP_H2_FUEL_TEMP]+[BLR_4_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*[BLR_4_CP_CH4_FUEL_TEMP]+([BLR_4_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*[BLR_4_CP_ETHYLENE_FUEL_TEMP]+([BLR_4_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*[BLR_4_CP_ETHANE_FUEL_TEMP]+([BLR_4_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*[BLR_4_CP_PROPANE_FUEL_TEMP]+([BLR_4_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_4_CP_NC4_FUEL_TEMP])+([BLR_4_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_4_CP_NC5_FUEL_TEMP]+[BLR_4_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_4_CP_IC4_FUEL_TEMP]+[BLR_4_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_4_CP_IC5_FUEL_TEMP])))*[BLR_4_FG_MW]
BLR_4_AVG_CP_FUEL_SENSIBLE | (([BLR_4_CP_FUEL_AT_REF_TEMP]+[BLR_4_CP_FUEL_AT_FUEL_TEMP])/[BLR_4_FG_MW])/2
BLR_4_CP_AIR_AT_STACK_TEMP | (((28.98641)+1.85398*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_4_CP_FLUE_CO2_AT_STACK | ((24.99735)+55.18696*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)-33.69137*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2+7.948387*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.136638/(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_CP_FLUE_H2O_AT_STACK | 8.22+0.00015*([BLR_4_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_4_STACK_TEMPERATURE]+273.15)^2)
BLR_4_CP_FLUE_N2_AT_STACK | ((28.98641)+1.85398*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_4_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_4_AVG_CP_FLUE_AT_STACK | ([BLR_4_CP_FLUE_CO2_AT_STACK]*[BLR_4_CO2_FORMED]/44.01+[BLR_4_CP_FLUE_N2_AT_STACK]*[BLR_4_N2_FORMED]/28.01+[BLR_4_EXCESS_AIR]/28.85*[BLR_4_CP_AIR_AT_STACK_TEMP])/([BLR_4_FLUE_GAS_RATIO]/[BLR_4_FLUE_GAS_MW])/[BLR_4_FLUE_GAS_MW]
BLR_4_CP_H2O_AT_STACK | (8.22+0.00015*([BLR_4_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_4_STACK_TEMPERATURE]+273.15)^2))/18.015
BLR_4_SH_CORRECTION_FUEL | if([BLR_4_AVG_CP_FUEL_SENSIBLE]*([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]-15.6)<0,0,[BLR_4_AVG_CP_FUEL_SENSIBLE]*([BLR_4_MAIN_FUEL_GAS_TEMPERATURE]-15.6))
BLR_4_SH_CORRECTION_AIR | [BLR_4_AIR_CP_SENSIBLE_CORRECTED]*([BLR_4_COMBUSTION_AIR_TEMPERATURE]-15.6)*[BLR_4_AIR_FUEL_MASS_RATIO]
BLR_4_MIXED_LHV_PER_KG | [UN.UO.BOILER_LHV]
BLR_4_TOTAL_HEAT_INPUT | if([BLR_4_STATUS]==0,0,[BLR_4_SH_CORRECTION_FUEL]+[BLR_4_SH_CORRECTION_AIR]+[BLR_4_MIXED_LHV_PER_KG])
BLR_4_HEAT_LOSS_L1 | if([BLR_4_STATUS]==0,0,[BLR_4_DRY_FLUE_GAS_RATIO]*([BLR_4_AVG_CP_FLUE_AT_STACK]*([BLR_4_STACK_TEMPERATURE]-15.6)))
BLR_4_HEAT_LOSS_L2 | if([BLR_4_STATUS]==0,0,9*[BLR_4_FG_H2_MASS_FRAC]*(584+[BLR_4_CP_H2O_AT_STACK]*([BLR_4_STACK_TEMPERATURE]-[UN.UO.AMBIENT_TEMP])))
BLR_4_HEAT_LOSS_L3 | if([BLR_4_STATUS]==0,0,[BLR_4_TOTAL_H2O_PER_KG_FUEL]*([BLR_4_STACK_TEMPERATURE]*1.77251246754294+2494.5133413964-2529.43)/4.184)
BLR_4_HEAT_LOSS_L4 | if([BLR_4_STATUS]==0,0,0*10^-6*28*5654*[BLR_4_BOILER_LOAD])
BLR_4_TOTAL_STACK_LOSS_PER_KG | if([BLR_4_STATUS]==0,0,[BLR_4_HEAT_LOSS_L4]+[BLR_4_HEAT_LOSS_L3]+[BLR_4_HEAT_LOSS_L1]+[BLR_4_HEAT_LOSS_L2])
BLR_4_RADIATION_LOSSES | if([BLR_4_STATUS]==0,0,[BLR_4_MIXED_LHV_PER_KG]*(-0.000004*[BLR_4_BOILER_LOAD]^3+0.001*[BLR_4_BOILER_LOAD]^2-0.0899*[BLR_4_BOILER_LOAD]+3.2426)/100)
BLR_4_TOTAL_HEAT_LOSS | if([BLR_4_STATUS]==0,0,[BLR_4_TOTAL_STACK_LOSS_PER_KG]+[BLR_4_RADIATION_LOSSES])
BLR_4_TOTAL_HEAT_ABSORBED | if([BLR_4_STATUS]==0,0,[BLR_4_TOTAL_HEAT_INPUT]-[BLR_4_TOTAL_HEAT_LOSS])
BLR_4_INDIRECT_EFFICIENCY | if([BLR_4_STATUS]==0,0,[BLR_4_TOTAL_HEAT_ABSORBED]/[BLR_4_TOTAL_HEAT_INPUT]*100)
BLR_4_HP_STEAM_ENTHALPY | if([BLR_4_STATUS]==0,0,(2175.54628147543-1.32764297764643*[BLR_4_HP_STEAM_PRESSURE]+2.66244961166282*[BLR_4_DESUPERHEATER_OUTLET_TEMP])*0.239+2)
BLR_4_TOTAL_STEAM_ENERGY | if([BLR_4_STATUS]==0,0,[BLR_4_STEAM_FLOW_RAW]*[BLR_4_HP_STEAM_ENTHALPY]/1000000)
BLR_4_BFW_ENTHALPY | if([BLR_4_STATUS]==0,0,[BLR_4_ECONOMIZER_INLET_TEMP])
BLR_4_CORRECTED_BFW_FLOW | if([BLR_4_STATUS]==0,0,([BLR_4_BFW_TO_ECONOMIZER]+[BLR_4_BFW_TO_DESUPERHEATER]-([BLR_4_BFW_TO_ECONOMIZER]+[BLR_4_BFW_TO_DESUPERHEATER]-[BLR_4_STEAM_FLOW_RAW]-[BLR_4_CBD_BLOWDOWN]))/1000)
BLR_4_BFW_ENERGY | if([BLR_4_STATUS]==0,0,[BLR_4_CORRECTED_BFW_FLOW]*[BLR_4_BFW_ENTHALPY]/1000)
BLR_4_FUEL_GAS_ENERGY_INPUT | if([BLR_4_STATUS]==0,0,[BLR_4_FG_FLOW_RATE_TPH]*1000*[BLR_4_MIXED_LHV_PER_KG]/10^6)
BLR_4_STEAM_DRUM_TEMP | if([BLR_4_STATUS]==0,0,4.02521999671835*log([BLR_4_STEAM_DRUM_PRESSURE]*98.065)^3-4.64392873298701*log([BLR_4_STEAM_DRUM_PRESSURE]*98.065)^2+11.2370106828649*log([BLR_4_STEAM_DRUM_PRESSURE]*98.065)+83.4806425229703)
BLR_4_BLOWDOWN_LOSS | if([BLR_4_STATUS]==0,0,(([BLR_4_CBD_BLOWDOWN]/1000)*(([BLR_4_STEAM_DRUM_PRESSURE]*2.11087739028321+[BLR_4_SUPERHEATER_INLET_TEMP]*2.94757709065418+278.050085762461)*0.2390006-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.0678913878546345+[BLR_4_SUPERHEATER_INLET_TEMP]*4.22416911685416-3.01717714574329)*0.2390006))/1000)
BLR_4_TOTAL_FLUE_GAS_GENERATED | if([BLR_4_STATUS]==0,0,[BLR_4_FUEL_GAS_FLOW]/1000*[BLR_4_FLUE_GAS_RATIO])
BLR_4_STACK_LOSS | if([BLR_4_STATUS]==0,0,[BLR_4_TOTAL_STACK_LOSS_PER_KG]*[BLR_4_FUEL_GAS_FLOW]/(1000*1000))
BLR_4_CORRECTED_FUEL_FLOW | if([BLR_4_STATUS]==0,0,[BLR_4_FUEL_GAS_FLOW]-(([BLR_4_FUEL_GAS_ENERGY_INPUT]-([BLR_4_TOTAL_STEAM_ENERGY]-[BLR_4_BFW_ENERGY]+[BLR_4_BLOWDOWN_LOSS]+[BLR_4_STACK_LOSS]+[BLR_4_FUEL_GAS_ENERGY_INPUT]*0.0112+[BLR_4_FUEL_GAS_ENERGY_INPUT]*(-0.000004*[BLR_4_BOILER_LOAD]^3+0.001*[BLR_4_BOILER_LOAD]^2-0.0899*[BLR_4_BOILER_LOAD]+3.2426)/100+([BLR_4_HEAT_LOSS_L3]*([BLR_4_FUEL_GAS_FLOW]/1000)*0.239006/1000)))/[BLR_4_MIXED_LHV_PER_KG]/1000))
BLR_4_FUEL_CONSUMPTION_GCAL | if([BLR_4_STATUS]==0,0,[BLR_4_CORRECTED_FUEL_FLOW]*[BLR_4_MIXED_LHV_PER_KG]/10^6)
BLR_4_SEC_GCAL_T | if([BLR_4_STATUS]==0,0,[BLR_4_FUEL_CONSUMPTION_GCAL]/([BLR_4_STEAM_FLOW_RAW]/1000))
BLR_4_SEC_GJ_T | if([BLR_4_STATUS]==0,0,[BLR_4_FUEL_CONSUMPTION_GCAL]/([BLR_4_STEAM_FLOW_RAW]/1000)*4.184)
BLR_4_CORRECTED_FUEL_ENERGY_INPUT | if([BLR_4_STATUS]==0,0,[BLR_4_CORRECTED_FUEL_FLOW]*[BLR_4_MIXED_LHV_PER_KG]/10^6)
BLR_4_THERMAL_EFFICIENCY | if([BLR_4_STATUS]==0,0,([BLR_4_TOTAL_STEAM_ENERGY]-[BLR_4_BFW_ENERGY])/[BLR_4_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_4_FUEL_GAS_CORRECTED_TPH | if([BLR_4_STATUS]==0,0,[BLR_4_CORRECTED_FUEL_FLOW]/1000)
BLR_4_TOTAL_FLUE_GAS_CORRECTED | if([BLR_4_STATUS]==0,0,[BLR_4_FUEL_GAS_CORRECTED_TPH]*[BLR_4_FLUE_GAS_RATIO])
BLR_4_STACK_LOSS_CORRECTED | if([BLR_4_STATUS]==0,0,[BLR_4_TOTAL_STACK_LOSS_PER_KG]*[BLR_4_FUEL_GAS_CORRECTED_TPH]/1000)
BLR_4_BFW_STEAM_RATIO | if([BLR_4_STATUS]==0,0,([BLR_4_STEAM_FLOW_RAW]+[BLR_4_CBD_BLOWDOWN])/([BLR_4_CORRECTED_BFW_FLOW]*1000))
BLR_4_CO2_EMISSIONS | if([BLR_4_STATUS]==0,0,[BLR_4_CO2_FORMED]*[BLR_4_FUEL_GAS_CORRECTED_TPH])
BLR_4_CALCULATED_AIRFLOW_NM3H | if([BLR_4_STATUS]==0,0,[BLR_4_AIR_FUEL_MASS_RATIO]*[BLR_4_CORRECTED_FUEL_FLOW]/(28.96/22.414)/1000)
BLR_4_STEAM_TO_FIRE_RATIO | if([BLR_4_STATUS]==0,0,[BLR_4_STEAM_FLOW_RAW]/([BLR_4_FG_FLOW_RATE_TPH]*[BLR_4_MIXED_LHV_PER_KG])*1000)
BLR_4_ECONOMIZER_DUTY | if([BLR_4_STATUS]==0,0,[BLR_4_CORRECTED_BFW_FLOW]*(([BLR_4_STEAM_DRUM_PRESSURE]*0.033652+[BLR_4_ECONOMIZER_OUTLET_TEMP]*4.52730-53.56679)-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.067891+[BLR_4_ECONOMIZER_INLET_TEMP]*4.22417-3.01718))*0.239006/1000)
BLR_4_LMTD_ECONOMIZER | if([BLR_4_STATUS]==0,0,((673-[BLR_4_ECONOMIZER_OUTLET_TEMP])-([BLR_4_STACK_TEMPERATURE]-[BLR_4_ECONOMIZER_INLET_TEMP]))/ln((673-[BLR_4_ECONOMIZER_OUTLET_TEMP])/(-[BLR_4_ECONOMIZER_INLET_TEMP]+[BLR_4_STACK_TEMPERATURE])))
BLR_4_UA_ECONOMIZER | if([BLR_4_STATUS]==0,0,[BLR_4_ECONOMIZER_DUTY]/[BLR_4_LMTD_ECONOMIZER])
BLR_4_FOULING_INDEX | if([BLR_4_STATUS]==0,0,1/[BLR_4_UA_ECONOMIZER])
BLR_4_SH_DUTY | if([BLR_4_STATUS]==0,0,[BLR_4_STEAM_FLOW_RAW]*(([BLR_4_STEAM_DRUM_PRESSURE]*-2.64315+[BLR_4_DESUPERHEATER_TEMPERATURE]*3.58096+1939.73413)-([BLR_4_STEAM_DRUM_PRESSURE]*-4.27591+[BLR_4_SUPERHEATER_INLET_TEMP]*3.45878+2082.10231))*0.239006/1000000)
BLR_4_SH_SPECIFIC_DUTY | if([BLR_4_STATUS]==0,0,[BLR_4_SH_DUTY]/[BLR_4_STEAM_FLOW_RAW]*1000)
BLR_4_SH_PERFORMANCE | if([BLR_4_STATUS]==0,0,[BLR_4_SH_SPECIFIC_DUTY]/0.128049016*100)
BLR_4_ENERGY_GAINED | if([BLR_4_STATUS]==0,0,[BLR_4_TOTAL_STEAM_ENERGY]-[BLR_4_BFW_ENERGY])
BLR_4_CONVECTION_DUTY | if([BLR_4_STATUS]==0,0,[BLR_4_ECONOMIZER_DUTY]+[BLR_4_SH_DUTY]+[BLR_4_STACK_LOSS_CORRECTED])
BLR_4_RADIATION_DUTY | if([BLR_4_STATUS]==0,0,[BLR_4_ENERGY_GAINED]-[BLR_4_CONVECTION_DUTY])
BLR_4_PCT_DUTY_CONVECTION | if([BLR_4_STATUS]==0,0,[BLR_4_CONVECTION_DUTY]/[BLR_4_ENERGY_GAINED]*100)
BLR_4_PCT_DUTY_RADIANT | if([BLR_4_STATUS]==0,0,[BLR_4_RADIATION_DUTY]/[BLR_4_ENERGY_GAINED]*100)
BLR_4_DUTY_RATIO_RAD_CONV | if([BLR_4_STATUS]==0,0,[BLR_4_PCT_DUTY_RADIANT]/[BLR_4_PCT_DUTY_CONVECTION])
BLR_4_RADIATION_SECTION_EFF | if([BLR_4_STATUS]==0,0,[BLR_4_RADIATION_DUTY]/[BLR_4_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_4_CONVECTION_SECTION_EFF | if([BLR_4_STATUS]==0,0,[BLR_4_CONVECTION_DUTY]/[BLR_4_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_4_HPS_GEN | if([BLR_4_STEAM_FLOW_RAW]<0,0,[BLR_4_STEAM_FLOW_RAW]/1000)
BLR_4_FUEL_FLOW | [BLR_4_FUEL_GAS_FLOW]*[BLR_4_STATUS]/1000
BLR_4_CAPACITY | 150
BLR_4_SPEC_EN_CONS | if([BLR_4_HPS_GEN]==0,0,[BLR_4_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_4_HPS_GEN])
BLR_4_SPEC_EN_CONS_OPT | (8e-06*[BLR_4_HPS_GEN]^2+-0.0017*[BLR_4_HPS_GEN]+3.0167)*[BLR_4_STATUS]
BLR_4_SPEC_EN_CONS_DEV | if([BLR_4_STATUS]==0,0,([BLR_4_SPEC_EN_CONS_OPT]-[BLR_4_SPEC_EN_CONS])/[BLR_4_SPEC_EN_CONS_OPT])
BLR_4_HPS_GEN_WARMUP | if([BLR_4_STATUS]==0,[BLR_4_HPS_GEN],0)
BLR_4_FD_FAN_STEAM_REG | ((5015.5-46.088*[BLR_4_HPS_GEN]+0.4828*[BLR_4_HPS_GEN]^2)/1000)
BLR_4_FD_FAN_STEAM_WARMUP | if([BLR_4_FD_FAN_STEAM_RAW]>100&&[BLR_4_FD_FAN_STEAM_RAW]<8000&&[BLR_4_STATUS]==0,[BLR_4_FD_FAN_STEAM_RAW]/1000,0)
BLR_4_FD_FAN_STEAM | if([BLR_4_FD_FAN_STEAM_RAW]<500,0,[BLR_4_FD_FAN_STEAM_RAW]/1000)
BLR_5_BOILER_LOAD | [BLR_5_STEAM_FLOW_RAW]/150000*100
BLR_5_STATUS | if([BLR_5_BOILER_LOAD]>25&&[BLR_5_DESUPERHEATER_OUTLET_TEMP]>370&&[BLR_5_HP_STEAM_PRESSURE]>40,1,0)
BLR_5_FUEL_COMP_TOTAL | ([UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]+[UN.UO.BOILER_FG_CH4_CONCENTRATION]+[UN.UO.BOILER_FG_ETHANE_CONCENTRATION]+[UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]+[UN.UO.BOILER_FG_PROPANE_CONCENTRATION]+[UN.UO.BOILER_FG_NC4_CONCENTRATION]+[UN.UO.BOILER_FG_IC4_CONCENTRATION]+[UN.UO.BOILER_FG_NC5_CONCENTRATION]+[UN.UO.BOILER_FG_IC5_CONCENTRATION]+[UN.UO.BOILER_FG_N2_CONCENTRATION])
BLR_5_FG_NORM_CH4 | [UN.UO.BOILER_FG_CH4_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_ETHANE | [UN.UO.BOILER_FG_ETHANE_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_ETHYLENE | [UN.UO.BOILER_FG_ETHYLENE_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_PROPANE | [UN.UO.BOILER_FG_PROPANE_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_CO2 | 0
BLR_5_FG_NORM_IC4 | [UN.UO.BOILER_FG_IC4_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_NC4 | [UN.UO.BOILER_FG_NC4_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_NC5 | [UN.UO.BOILER_FG_NC5_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_IC5 | [UN.UO.BOILER_FG_IC5_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_N2 | [UN.UO.BOILER_FG_N2_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_NORM_H2 | [UN.UO.BOILER_FG_HYDROGEN_CONCENTRATION]/[BLR_5_FUEL_COMP_TOTAL]*100
BLR_5_FG_MW | ([BLR_5_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]+[BLR_5_FG_NORM_CH4]*[COMPONENT_METHANE_MW]+[BLR_5_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]+[BLR_5_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]+[BLR_5_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]+[BLR_5_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]+[BLR_5_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]+[BLR_5_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]+[BLR_5_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]+[BLR_5_FG_NORM_N2]*[COMPONENT_NITROGEN_MW])/100
BLR_5_FG_DENSITY | [BLR_5_FG_MW]/22.414
BLR_5_LHV_DESIGN | ([LHV_FG]/[BLR_5_FG_DENSITY])/1000
BLR_5_FG_CH4_MASS_PCT | [BLR_5_FG_NORM_CH4]*[COMPONENT_METHANE_MW]/[BLR_5_FG_MW]
BLR_5_FG_ETHANE_MASS_PCT | [BLR_5_FG_NORM_ETHANE]*[COMPONENT_ETHANE_MW]/[BLR_5_FG_MW]
BLR_5_FG_ETHYLENE_MASS_PCT | [BLR_5_FG_NORM_ETHYLENE]*[COMPONENT_ETHYLENE_MW]/[BLR_5_FG_MW]
BLR_5_FG_PROPANE_MASS_PCT | [BLR_5_FG_NORM_PROPANE]*[COMPONENT_PROPANE_MW]/[BLR_5_FG_MW]
BLR_5_FG_N2_MASS_PCT | [BLR_5_FG_NORM_N2]*[COMPONENT_NITROGEN_MW]/[BLR_5_FG_MW]
BLR_5_FG_H2_MASS_PCT | [BLR_5_FG_NORM_H2]*[COMPONENT_HYDROGEN_MW]/[BLR_5_FG_MW]
BLR_5_FG_IC4_MASS_PCT | [BLR_5_FG_NORM_IC4]*[COMPONENT_BUTANE_MW]/[BLR_5_FG_MW]
BLR_5_FG_NC4_MASS_PCT | [BLR_5_FG_NORM_NC4]*[COMPONENT_BUTANE_MW]/[BLR_5_FG_MW]
BLR_5_FG_NC5_MASS_PCT | [BLR_5_FG_NORM_NC5]*[COMPONENT_PENTANE_MW]/[BLR_5_FG_MW]
BLR_5_FG_IC5_MASS_PCT | [BLR_5_FG_NORM_IC5]*[COMPONENT_PENTANE_MW]/[BLR_5_FG_MW]
BLR_5_FG_CH4_MASS_FRAC | [BLR_5_FG_CH4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_ETHANE_MASS_FRAC | [BLR_5_FG_ETHANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_ETHYLENE_MASS_FRAC | [BLR_5_FG_ETHYLENE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_PROPANE_MASS_FRAC | [BLR_5_FG_PROPANE_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_N2_MASS_FRAC | [BLR_5_FG_N2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_H2_MASS_FRAC | [BLR_5_FG_H2_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_IC4_MASS_FRAC | [BLR_5_FG_IC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_NC4_MASS_FRAC | [BLR_5_FG_NC4_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_NC5_MASS_FRAC | [BLR_5_FG_NC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_IC5_MASS_FRAC | [BLR_5_FG_IC5_MASS_PCT]/[TOTAL_FUEL_COMPOSTION_MASS]
BLR_5_FG_FLOW_RATE_TPH | [BLR_5_FUEL_GAS_FLOW]/1000
BLR_5_AIR_REQ_H2 | [BLR_5_FG_H2_MASS_FRAC]*34.344
BLR_5_AIR_REQ_CH4 | [BLR_5_FG_CH4_MASS_FRAC]*17.265
BLR_5_AIR_REQ_ETHANE | [BLR_5_FG_ETHANE_MASS_FRAC]*16.119
BLR_5_AIR_REQ_ETHYLENE | [BLR_5_FG_ETHYLENE_MASS_FRAC]*14.807
BLR_5_AIR_REQ_PROPANE | [BLR_5_FG_PROPANE_MASS_FRAC]*15.703
BLR_5_AIR_REQ_NC4 | [BLR_5_FG_NC4_MASS_FRAC]*15.487
BLR_5_AIR_REQ_IC4 | [BLR_5_FG_IC4_MASS_FRAC]*15.487
BLR_5_AIR_REQ_NC5 | [BLR_5_FG_NC5_MASS_FRAC]*15.353
BLR_5_AIR_REQ_IC5 | [BLR_5_FG_IC5_MASS_FRAC]*15.353
BLR_5_CO2_COMB_H2 | [BLR_5_FG_H2_MASS_FRAC]*0
BLR_5_CO2_COMB_CH4 | [BLR_5_FG_CH4_MASS_FRAC]*2.744
BLR_5_CO2_COMB_ETHANE | [BLR_5_FG_ETHANE_MASS_FRAC]*2.927
BLR_5_CO2_COMB_ETHYLENE | [BLR_5_FG_ETHYLENE_MASS_FRAC]*3.138
BLR_5_CO2_COMB_PROPANE | [BLR_5_FG_PROPANE_MASS_FRAC]*2.994
BLR_5_CO2_COMB_NC4 | [BLR_5_FG_NC4_MASS_FRAC]*3.029
BLR_5_CO2_COMB_IC4 | [BLR_5_FG_IC4_MASS_FRAC]*3.029
BLR_5_CO2_COMB_NC5 | [BLR_5_FG_NC5_MASS_FRAC]*3.05
BLR_5_CO2_COMB_IC5 | [BLR_5_FG_IC5_MASS_FRAC]*3.05
BLR_5_N2_COMB_H2 | [BLR_5_FG_H2_MASS_FRAC]*26.407
BLR_5_N2_COMB_CH4 | [BLR_5_FG_CH4_MASS_FRAC]*13.275
BLR_5_N2_COMB_ETHANE | [BLR_5_FG_ETHANE_MASS_FRAC]*12.394
BLR_5_N2_COMB_ETHYLENE | [BLR_5_FG_ETHYLENE_MASS_FRAC]*11.385
BLR_5_N2_COMB_PROPANE | [BLR_5_FG_PROPANE_MASS_FRAC]*12.074
BLR_5_N2_COMB_IC4 | [BLR_5_FG_IC4_MASS_FRAC]*11.908
BLR_5_N2_COMB_NC4 | [BLR_5_FG_NC4_MASS_FRAC]*11.908
BLR_5_N2_COMB_IC5 | [BLR_5_FG_IC5_MASS_FRAC]*11.805
BLR_5_N2_COMB_NC5 | [BLR_5_FG_NC5_MASS_FRAC]*11.805
BLR_5_H2O_COMB_H2 | [BLR_5_FG_H2_MASS_FRAC]*8.937
BLR_5_H2O_COMB_CH4 | [BLR_5_FG_CH4_MASS_FRAC]*2.246
BLR_5_H2O_COMB_ETHANE | [BLR_5_FG_ETHANE_MASS_FRAC]*1.798
BLR_5_H2O_COMB_ETHYLENE | [BLR_5_FG_ETHYLENE_MASS_FRAC]*1.285
BLR_5_H2O_COMB_PROPANE | [BLR_5_FG_PROPANE_MASS_FRAC]*1.634
BLR_5_H2O_COMB_IC4 | [BLR_5_FG_NC4_MASS_FRAC]*1.55
BLR_5_H2O_COMB_NC4 | [BLR_5_FG_IC4_MASS_FRAC]*1.55
BLR_5_H2O_COMB_IC5 | [BLR_5_FG_IC5_MASS_FRAC]*1.498
BLR_5_H2O_COMB_NC5 | [BLR_5_FG_NC5_MASS_FRAC]*1.498
BLR_5_AIR_REQ_COMPLETE | [BLR_5_AIR_REQ_H2]+[BLR_5_AIR_REQ_CH4]+[BLR_5_AIR_REQ_ETHANE]+[BLR_5_AIR_REQ_ETHYLENE]+[BLR_5_AIR_REQ_PROPANE]+[BLR_5_AIR_REQ_NC4]+[BLR_5_AIR_REQ_IC4]+[BLR_5_AIR_REQ_NC5]+[BLR_5_AIR_REQ_IC5]
BLR_5_CO2_FORMED | [BLR_5_CO2_COMB_CH4]+[BLR_5_CO2_COMB_ETHANE]+[BLR_5_CO2_COMB_ETHYLENE]+[BLR_5_CO2_COMB_PROPANE]+[BLR_5_CO2_COMB_NC4]+[BLR_5_CO2_COMB_IC4]+[BLR_5_CO2_COMB_NC5]+[BLR_5_CO2_COMB_IC5]
BLR_5_N2_FORMED | [BLR_5_N2_COMB_H2]+[BLR_5_N2_COMB_CH4]+[BLR_5_N2_COMB_ETHANE]+[BLR_5_N2_COMB_ETHYLENE]+[BLR_5_N2_COMB_PROPANE]+[BLR_5_N2_COMB_IC4]+[BLR_5_N2_COMB_NC4]+[BLR_5_N2_COMB_IC5]+[BLR_5_N2_COMB_NC5]
BLR_5_H2O_FORMED | [BLR_5_H2O_COMB_H2]+[BLR_5_H2O_COMB_CH4]+[BLR_5_H2O_COMB_ETHANE]+[BLR_5_H2O_COMB_ETHYLENE]+[BLR_5_H2O_COMB_PROPANE]+[BLR_5_H2O_COMB_IC4]+[BLR_5_H2O_COMB_NC4]+[BLR_5_H2O_COMB_IC5]+[BLR_5_H2O_COMB_NC5]
BLR_5_VAPOUR_PRESSURE_H2O | 10^(8.07131-(1730.63/(233.426+[UN.UO.AMBIENT_TEMP])))
BLR_5_AIR_MOISTURE | [BLR_5_VAPOUR_PRESSURE_H2O]/(760-[BLR_5_VAPOUR_PRESSURE_H2O]*[UN.UO.RELATIVE_HUMIDITY_CLEAN])*[UN.UO.RELATIVE_HUMIDITY_CLEAN]*18.015/28.96
BLR_5_CORRECTED_COMBUSTION_AIR | [BLR_5_AIR_REQ_COMPLETE]/(1-[BLR_5_AIR_MOISTURE])
BLR_5_CORRECTED_H2O_FORMED | [BLR_5_H2O_FORMED]+([BLR_5_CORRECTED_COMBUSTION_AIR]-[BLR_5_AIR_REQ_COMPLETE])
BLR_5_EXCESS_AIR | ((28.96*[BLR_5_FLUE_GAS_OXYGEN])*([BLR_5_N2_FORMED]/28.01+[BLR_5_CORRECTED_H2O_FORMED]/18.015+[BLR_5_CO2_FORMED]/44.01)/(20.95-[BLR_5_FLUE_GAS_OXYGEN]))
BLR_5_AIR_FUEL_MASS_RATIO | [BLR_5_EXCESS_AIR]+[BLR_5_CORRECTED_COMBUSTION_AIR]
BLR_5_TOTAL_MOISTURE_WITH_AIR | [BLR_5_AIR_FUEL_MASS_RATIO]*[BLR_5_AIR_MOISTURE]
BLR_5_TOTAL_H2O_PER_KG_FUEL | [BLR_5_TOTAL_MOISTURE_WITH_AIR]+[BLR_5_H2O_FORMED]
BLR_5_DRY_FLUE_GAS_RATIO | [BLR_5_EXCESS_AIR]*(1-[BLR_5_AIR_MOISTURE])+[BLR_5_N2_FORMED]+[BLR_5_CO2_FORMED]
BLR_5_FLUE_GAS_RATIO | [BLR_5_DRY_FLUE_GAS_RATIO]+[BLR_5_TOTAL_H2O_PER_KG_FUEL]
BLR_5_FLUE_GAS_MW | [BLR_5_FLUE_GAS_RATIO]/([BLR_5_CO2_FORMED]/44.01+[BLR_5_TOTAL_H2O_PER_KG_FUEL]/18.015+[BLR_5_N2_FORMED]/28.01+[BLR_5_EXCESS_AIR]/28.96)
BLR_5_AIR_CP_REF_T | 6.96
BLR_5_CP_AT_COMB_TEMP | (((28.98641)+1.85398*(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_5_COMBUSTION_AIR_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_5_AIR_CP_SENSIBLE_CORRECTED | (([BLR_5_AIR_CP_REF_T]+[BLR_5_CP_AT_COMB_TEMP])/2)/28.96
BLR_5_CP_H2_FUEL_TEMP | ((33.066178)-11.363417*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)+11.432816*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-2.772874*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(-0.158558/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_CH4_FUEL_TEMP | ((-0.703029)+108.4773*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-42.52157*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+5.862788*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.678565/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_ETHANE_FUEL_TEMP | (6.08161+173.58246*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-66.91905*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+9.08912*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.129136/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_PROPANE_FUEL_TEMP | (12.66081+232.07025*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-70.34461*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+0.60714*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.026957/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_ETHYLENE_FUEL_TEMP | (-6.38788+184.4019*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-112.9718*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2+28.49593*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+0.31554/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2)*0.239
BLR_5_CP_NC4_FUEL_TEMP | (22.1581+292.5894*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-85.8165*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-1.01394*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.00635/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_IC4_FUEL_TEMP | (8.32666+344.92332*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-141.6499*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-17.40270*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.02600/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_NC5_FUEL_TEMP | (-36.73509+580.37577*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-341.58654*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-78.49965*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(1.08617/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_IC5_FUEL_TEMP | (-16.14269+517.36368*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)-271.31408*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2-56.15662*(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^3+(0.31713/(([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_FUEL_AT_REF_TEMP | (([BLR_5_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*6.876+[BLR_5_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*8.45+([BLR_5_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*10.02+([BLR_5_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*12.52+([BLR_5_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*17.72+([BLR_5_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79)+([BLR_5_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26+[BLR_5_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*23.79+[BLR_5_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*38.26)))*[BLR_5_FG_MW]
BLR_5_CP_FUEL_AT_FUEL_TEMP | (([BLR_5_FG_H2_MASS_FRAC]/[COMPONENT_HYDROGEN_MW])*[BLR_5_CP_H2_FUEL_TEMP]+[BLR_5_FG_CH4_MASS_FRAC]/[COMPONENT_METHANE_MW]*[BLR_5_CP_CH4_FUEL_TEMP]+([BLR_5_FG_ETHYLENE_MASS_FRAC]/[COMPONENT_ETHYLENE_MW])*[BLR_5_CP_ETHYLENE_FUEL_TEMP]+([BLR_5_FG_ETHANE_MASS_FRAC]/[COMPONENT_ETHANE_MW])*[BLR_5_CP_ETHANE_FUEL_TEMP]+([BLR_5_FG_PROPANE_MASS_FRAC]/[COMPONENT_PROPANE_MW]*[BLR_5_CP_PROPANE_FUEL_TEMP]+([BLR_5_FG_NC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_5_CP_NC4_FUEL_TEMP])+([BLR_5_FG_NC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_5_CP_NC5_FUEL_TEMP]+[BLR_5_FG_IC4_MASS_FRAC]/[COMPONENT_BUTANE_MW]*[BLR_5_CP_IC4_FUEL_TEMP]+[BLR_5_FG_IC5_MASS_FRAC]/[COMPONENT_PENTANE_MW]*[BLR_5_CP_IC5_FUEL_TEMP])))*[BLR_5_FG_MW]
BLR_5_AVG_CP_FUEL_SENSIBLE | (([BLR_5_CP_FUEL_AT_REF_TEMP]+[BLR_5_CP_FUEL_AT_FUEL_TEMP])/[BLR_5_FG_MW])/2
BLR_5_CP_AIR_AT_STACK_TEMP | (((28.98641)+1.85398*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)+57.86644*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2-36.50624*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.007374/(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239*0.21)
BLR_5_CP_FLUE_CO2_AT_STACK | ((24.99735)+55.18696*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)-33.69137*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2+7.948387*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^3+(-0.136638/(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_CP_FLUE_H2O_AT_STACK | 8.22+0.00015*([BLR_5_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_5_STACK_TEMPERATURE]+273.15)^2)
BLR_5_CP_FLUE_N2_AT_STACK | ((28.98641)+1.85398*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)-9.647459*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2+16.63537*(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^3+(0.000117/(([BLR_5_STACK_TEMPERATURE]+273.15)/1000)^2))*0.239
BLR_5_AVG_CP_FLUE_AT_STACK | ([BLR_5_CP_FLUE_CO2_AT_STACK]*[BLR_5_CO2_FORMED]/44.01+[BLR_5_CP_FLUE_N2_AT_STACK]*[BLR_5_N2_FORMED]/28.01+[BLR_5_EXCESS_AIR]/28.85*[BLR_5_CP_AIR_AT_STACK_TEMP])/([BLR_5_FLUE_GAS_RATIO]/[BLR_5_FLUE_GAS_MW])/[BLR_5_FLUE_GAS_MW]
BLR_5_CP_H2O_AT_STACK | (8.22+0.00015*([BLR_5_STACK_TEMPERATURE]+273.15)+0.00000134*(([BLR_5_STACK_TEMPERATURE]+273.15)^2))/18.015
BLR_5_SH_CORRECTION_FUEL | if([BLR_5_AVG_CP_FUEL_SENSIBLE]*([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]-15.6)<0,0,[BLR_5_AVG_CP_FUEL_SENSIBLE]*([BLR_5_MAIN_FUEL_GAS_TEMPERATURE]-15.6))
BLR_5_SH_CORRECTION_AIR | [BLR_5_AIR_CP_SENSIBLE_CORRECTED]*([BLR_5_COMBUSTION_AIR_TEMPERATURE]-15.6)*[BLR_5_AIR_FUEL_MASS_RATIO]
BLR_5_MIXED_LHV_PER_KG | [UN.UO.BOILER_LHV]
BLR_5_TOTAL_HEAT_INPUT | if([BLR_5_STATUS]==0,0,[BLR_5_SH_CORRECTION_FUEL]+[BLR_5_SH_CORRECTION_AIR]+[BLR_5_MIXED_LHV_PER_KG])
BLR_5_HEAT_LOSS_L1 | if([BLR_5_STATUS]==0,0,[BLR_5_DRY_FLUE_GAS_RATIO]*([BLR_5_AVG_CP_FLUE_AT_STACK]*([BLR_5_STACK_TEMPERATURE]-15.6)))
BLR_5_HEAT_LOSS_L2 | if([BLR_5_STATUS]==0,0,9*[BLR_5_FG_H2_MASS_FRAC]*(584+[BLR_5_CP_H2O_AT_STACK]*([BLR_5_STACK_TEMPERATURE]-[UN.UO.AMBIENT_TEMP])))
BLR_5_HEAT_LOSS_L3 | if([BLR_5_STATUS]==0,0,[BLR_5_TOTAL_H2O_PER_KG_FUEL]*([BLR_5_STACK_TEMPERATURE]*1.77251246754294+2494.5133413964-2529.43)/4.184)
BLR_5_HEAT_LOSS_L4 | if([BLR_5_STATUS]==0,0,0*10^-6*28*5654*[BLR_5_BOILER_LOAD])
BLR_5_TOTAL_STACK_LOSS_PER_KG | if([BLR_5_STATUS]==0,0,[BLR_5_HEAT_LOSS_L4]+[BLR_5_HEAT_LOSS_L3]+[BLR_5_HEAT_LOSS_L1]+[BLR_5_HEAT_LOSS_L2])
BLR_5_RADIATION_LOSSES | if([BLR_5_STATUS]==0,0,[BLR_5_MIXED_LHV_PER_KG]*(-0.000004*[BLR_5_BOILER_LOAD]^3+0.001*[BLR_5_BOILER_LOAD]^2-0.0899*[BLR_5_BOILER_LOAD]+3.2426)/100)
BLR_5_TOTAL_HEAT_LOSS | if([BLR_5_STATUS]==0,0,[BLR_5_TOTAL_STACK_LOSS_PER_KG]+[BLR_5_RADIATION_LOSSES])
BLR_5_TOTAL_HEAT_ABSORBED | if([BLR_5_STATUS]==0,0,[BLR_5_TOTAL_HEAT_INPUT]-[BLR_5_TOTAL_HEAT_LOSS])
BLR_5_INDIRECT_EFFICIENCY | if([BLR_5_STATUS]==0,0,[BLR_5_TOTAL_HEAT_ABSORBED]/[BLR_5_TOTAL_HEAT_INPUT]*100)
BLR_5_HP_STEAM_ENTHALPY | if([BLR_5_STATUS]==0,0,(2175.54628147543-1.32764297764643*[BLR_5_HP_STEAM_PRESSURE]+2.66244961166282*[BLR_5_DESUPERHEATER_OUTLET_TEMP])*0.239+2)
BLR_5_TOTAL_STEAM_ENERGY | if([BLR_5_STATUS]==0,0,[BLR_5_STEAM_FLOW_RAW]*[BLR_5_HP_STEAM_ENTHALPY]/1000000)
BLR_5_BFW_ENTHALPY | if([BLR_5_STATUS]==0,0,[BLR_5_ECONOMIZER_INLET_TEMP])
BLR_5_CORRECTED_BFW_FLOW | if([BLR_5_STATUS]==0,0,([BLR_5_BFW_TO_ECONOMIZER]+[BLR_5_BFW_TO_DESUPERHEATER]-([BLR_5_BFW_TO_ECONOMIZER]+[BLR_5_BFW_TO_DESUPERHEATER]-[BLR_5_STEAM_FLOW_RAW]-[BLR_5_CBD_BLOWDOWN]))/1000)
BLR_5_BFW_ENERGY | if([BLR_5_STATUS]==0,0,[BLR_5_CORRECTED_BFW_FLOW]*[BLR_5_BFW_ENTHALPY]/1000)
BLR_5_FUEL_GAS_ENERGY_INPUT | if([BLR_5_STATUS]==0,0,[BLR_5_FG_FLOW_RATE_TPH]*1000*[BLR_5_MIXED_LHV_PER_KG]/10^6)
BLR_5_STEAM_DRUM_TEMP | if([BLR_5_STATUS]==0,0,4.02521999671835*log([BLR_5_STEAM_DRUM_PRESSURE]*98.065)^3-4.64392873298701*log([BLR_5_STEAM_DRUM_PRESSURE]*98.065)^2+11.2370106828649*log([BLR_5_STEAM_DRUM_PRESSURE]*98.065)+83.4806425229703)
BLR_5_BLOWDOWN_LOSS | if([BLR_5_STATUS]==0,0,(([BLR_5_CBD_BLOWDOWN]/1000)*(([BLR_5_STEAM_DRUM_PRESSURE]*2.11087739028321+[BLR_5_SUPERHEATER_INLET_TEMP]*2.94757709065418+278.050085762461)*0.2390006-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.0678913878546345+[BLR_5_SUPERHEATER_INLET_TEMP]*4.22416911685416-3.01717714574329)*0.2390006))/1000)
BLR_5_TOTAL_FLUE_GAS_GENERATED | if([BLR_5_STATUS]==0,0,[BLR_5_FUEL_GAS_FLOW]/1000*[BLR_5_FLUE_GAS_RATIO])
BLR_5_STACK_LOSS | if([BLR_5_STATUS]==0,0,[BLR_5_TOTAL_STACK_LOSS_PER_KG]*[BLR_5_FUEL_GAS_FLOW]/(1000*1000))
BLR_5_CORRECTED_FUEL_FLOW | if([BLR_5_STATUS]==0,0,[BLR_5_FUEL_GAS_FLOW]-(([BLR_5_FUEL_GAS_ENERGY_INPUT]-([BLR_5_TOTAL_STEAM_ENERGY]-[BLR_5_BFW_ENERGY]+[BLR_5_BLOWDOWN_LOSS]+[BLR_5_STACK_LOSS]+[BLR_5_FUEL_GAS_ENERGY_INPUT]*0.0112+[BLR_5_FUEL_GAS_ENERGY_INPUT]*(-0.000004*[BLR_5_BOILER_LOAD]^3+0.001*[BLR_5_BOILER_LOAD]^2-0.0899*[BLR_5_BOILER_LOAD]+3.2426)/100+([BLR_5_HEAT_LOSS_L3]*([BLR_5_FUEL_GAS_FLOW]/1000)*0.239006/1000)))/[BLR_5_MIXED_LHV_PER_KG]/1000))
BLR_5_FUEL_CONSUMPTION_GCAL | if([BLR_5_STATUS]==0,0,[BLR_5_CORRECTED_FUEL_FLOW]*[BLR_5_MIXED_LHV_PER_KG]/10^6)
BLR_5_SEC_GCAL_T | if([BLR_5_STATUS]==0,0,[BLR_5_FUEL_CONSUMPTION_GCAL]/([BLR_5_STEAM_FLOW_RAW]/1000))
BLR_5_SEC_GJ_T | if([BLR_5_STATUS]==0,0,[BLR_5_FUEL_CONSUMPTION_GCAL]/([BLR_5_STEAM_FLOW_RAW]/1000)*4.184)
BLR_5_CORRECTED_FUEL_ENERGY_INPUT | if([BLR_5_STATUS]==0,0,[BLR_5_CORRECTED_FUEL_FLOW]*[BLR_5_MIXED_LHV_PER_KG]/10^6)
BLR_5_THERMAL_EFFICIENCY | if([BLR_5_STATUS]==0,0,([BLR_5_TOTAL_STEAM_ENERGY]-[BLR_5_BFW_ENERGY])/[BLR_5_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_5_FUEL_GAS_CORRECTED_TPH | if([BLR_5_STATUS]==0,0,[BLR_5_CORRECTED_FUEL_FLOW]/1000)
BLR_5_TOTAL_FLUE_GAS_CORRECTED | if([BLR_5_STATUS]==0,0,[BLR_5_FUEL_GAS_CORRECTED_TPH]*[BLR_5_FLUE_GAS_RATIO])
BLR_5_STACK_LOSS_CORRECTED | if([BLR_5_STATUS]==0,0,[BLR_5_TOTAL_STACK_LOSS_PER_KG]*[BLR_5_FUEL_GAS_CORRECTED_TPH]/1000)
BLR_5_BFW_STEAM_RATIO | if([BLR_5_STATUS]==0,0,([BLR_5_STEAM_FLOW_RAW]+[BLR_5_CBD_BLOWDOWN])/([BLR_5_CORRECTED_BFW_FLOW]*1000))
BLR_5_CO2_EMISSIONS | if([BLR_5_STATUS]==0,0,[BLR_5_CO2_FORMED]*[BLR_5_FUEL_GAS_CORRECTED_TPH])
BLR_5_CALCULATED_AIRFLOW_NM3H | if([BLR_5_STATUS]==0,0,[BLR_5_AIR_FUEL_MASS_RATIO]*[BLR_5_CORRECTED_FUEL_FLOW]/(28.96/22.414)/1000)
BLR_5_STEAM_TO_FIRE_RATIO | if([BLR_5_STATUS]==0,0,[BLR_5_STEAM_FLOW_RAW]/([BLR_5_FG_FLOW_RATE_TPH]*[BLR_5_MIXED_LHV_PER_KG])*1000)
BLR_5_ECONOMIZER_DUTY | if([BLR_5_STATUS]==0,0,[BLR_5_CORRECTED_BFW_FLOW]*(([BLR_5_STEAM_DRUM_PRESSURE]*0.033652+[BLR_5_ECONOMIZER_OUTLET_TEMP]*4.52730-53.56679)-([UN.UO.BFW_PRESSURE_TO_BOILER]*0.067891+[BLR_5_ECONOMIZER_INLET_TEMP]*4.22417-3.01718))*0.239006/1000)
BLR_5_LMTD_ECONOMIZER | if([BLR_5_STATUS]==0,0,((673-[BLR_5_ECONOMIZER_OUTLET_TEMP])-([BLR_5_STACK_TEMPERATURE]-[BLR_5_ECONOMIZER_INLET_TEMP]))/ln((673-[BLR_5_ECONOMIZER_OUTLET_TEMP])/(-[BLR_5_ECONOMIZER_INLET_TEMP]+[BLR_5_STACK_TEMPERATURE])))
BLR_5_UA_ECONOMIZER | if([BLR_5_STATUS]==0,0,[BLR_5_ECONOMIZER_DUTY]/[BLR_5_LMTD_ECONOMIZER])
BLR_5_FOULING_INDEX | if([BLR_5_STATUS]==0,0,1/[BLR_5_UA_ECONOMIZER])
BLR_5_SH_DUTY | if([BLR_5_STATUS]==0,0,[BLR_5_STEAM_FLOW_RAW]*(([BLR_5_STEAM_DRUM_PRESSURE]*-2.64315+[BLR_5_DESUPERHEATER_TEMPERATURE]*3.58096+1939.73413)-([BLR_5_STEAM_DRUM_PRESSURE]*-4.27591+[BLR_5_SUPERHEATER_INLET_TEMP]*3.45878+2082.10231))*0.239006/1000000)
BLR_5_SH_SPECIFIC_DUTY | if([BLR_5_STATUS]==0,0,[BLR_5_SH_DUTY]/[BLR_5_STEAM_FLOW_RAW]*1000)
BLR_5_SH_PERFORMANCE | if([BLR_5_STATUS]==0,0,[BLR_5_SH_SPECIFIC_DUTY]/0.128049016*100)
BLR_5_ENERGY_GAINED | if([BLR_5_STATUS]==0,0,[BLR_5_TOTAL_STEAM_ENERGY]-[BLR_5_BFW_ENERGY])
BLR_5_CONVECTION_DUTY | if([BLR_5_STATUS]==0,0,[BLR_5_ECONOMIZER_DUTY]+[BLR_5_SH_DUTY]+[BLR_5_STACK_LOSS_CORRECTED])
BLR_5_RADIATION_DUTY | if([BLR_5_STATUS]==0,0,[BLR_5_ENERGY_GAINED]-[BLR_5_CONVECTION_DUTY])
BLR_5_PCT_DUTY_CONVECTION | if([BLR_5_STATUS]==0,0,[BLR_5_CONVECTION_DUTY]/[BLR_5_ENERGY_GAINED]*100)
BLR_5_PCT_DUTY_RADIANT | if([BLR_5_STATUS]==0,0,[BLR_5_RADIATION_DUTY]/[BLR_5_ENERGY_GAINED]*100)
BLR_5_DUTY_RATIO_RAD_CONV | if([BLR_5_STATUS]==0,0,[BLR_5_PCT_DUTY_RADIANT]/[BLR_5_PCT_DUTY_CONVECTION])
BLR_5_RADIATION_SECTION_EFF | if([BLR_5_STATUS]==0,0,[BLR_5_RADIATION_DUTY]/[BLR_5_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_5_CONVECTION_SECTION_EFF | if([BLR_5_STATUS]==0,0,[BLR_5_CONVECTION_DUTY]/[BLR_5_CORRECTED_FUEL_ENERGY_INPUT]*100)
BLR_5_HPS_GEN | if([BLR_5_STEAM_FLOW_RAW]<0,0,[BLR_5_STEAM_FLOW_RAW]/1000)
BLR_5_FUEL_FLOW | [BLR_5_FUEL_GAS_FLOW]*[BLR_5_STATUS]/1000
BLR_5_CAPACITY | 150
BLR_5_SPEC_EN_CONS | if([BLR_5_HPS_GEN]==0,0,[BLR_5_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_5_HPS_GEN])
BLR_5_SPEC_EN_CONS_OPT | (8e-06*[BLR_5_HPS_GEN]^2+-0.0017*[BLR_5_HPS_GEN]+3.0167)*[BLR_5_STATUS]
BLR_5_SPEC_EN_CONS_DEV | if([BLR_5_STATUS]==0,0,([BLR_5_SPEC_EN_CONS_OPT]-[BLR_5_SPEC_EN_CONS])/[BLR_5_SPEC_EN_CONS_OPT])
BLR_5_HPS_GEN_WARMUP | if([BLR_5_STATUS]==0,[BLR_5_HPS_GEN],0)
BLR_5_FD_FAN_STEAM_REG | ((4772.4+9.2624*[BLR_5_HPS_GEN]+0.0843*[BLR_5_HPS_GEN]^2)/1000)
BLR_5_FD_FAN_STEAM_WARMUP | if([BLR_5_FD_FAN_STEAM_RAW]>100&&[BLR_5_FD_FAN_STEAM_RAW]<8000&&[BLR_5_STATUS]==0,[BLR_5_FD_FAN_STEAM_RAW]/1000,0)
BLR_5_FD_FAN_STEAM | if([BLR_5_FD_FAN_STEAM_RAW]<500,0,[BLR_5_FD_FAN_STEAM_RAW]/1000)

## variables
tag_name | lower_bound_value | lower_bound_expression | upper_bound_value | upper_bound_expression | flag_integer | source_flag
BLR_1_STATUS | 0 | 0 | 1 | [BLR_1_STATUS] | 1 | GENERIC_TEMPLATE
BLR_1_HPS_GEN | 0 | [BLR_1_STATUS]*50 | 150 | [BLR_1_STATUS]*150 | 0 | GENERIC_TEMPLATE
BLR_1_FUEL_FLOW | 0 | 0 | 12 | max(12,[BLR_1_FUEL_FLOW]) | 0 | GENERIC_TEMPLATE
BLR_1_FD_FAN_STEAM | 0 | 0 | 8 | max([BLR_1_FD_FAN_STEAM],8) | 0 | GENERIC_TEMPLATE
BLR_2_STATUS | 0 | 0 | 1 | [BLR_2_STATUS] | 1 | GENERIC_TEMPLATE
BLR_2_HPS_GEN | 0 | [BLR_2_STATUS]*50 | 150 | [BLR_2_STATUS]*150 | 0 | GENERIC_TEMPLATE
BLR_2_FUEL_FLOW | 0 | 0 | 12 | max(12,[BLR_2_FUEL_FLOW]) | 0 | GENERIC_TEMPLATE
BLR_2_FD_FAN_STEAM | 0 | 0 | 8 | max([BLR_2_FD_FAN_STEAM],8) | 0 | GENERIC_TEMPLATE
BLR_3_STATUS | 0 | 0 | 1 | [BLR_3_STATUS] | 1 | GENERIC_TEMPLATE
BLR_3_HPS_GEN | 0 | [BLR_3_STATUS]*50 | 150 | [BLR_3_STATUS]*150 | 0 | GENERIC_TEMPLATE
BLR_3_FUEL_FLOW | 0 | 0 | 12 | max(12,[BLR_3_FUEL_FLOW]) | 0 | GENERIC_TEMPLATE
BLR_3_FD_FAN_STEAM | 0 | 0 | 8 | max([BLR_3_FD_FAN_STEAM],8) | 0 | GENERIC_TEMPLATE
BLR_4_STATUS | 0 | 0 | 1 | [BLR_4_STATUS] | 1 | GENERIC_TEMPLATE
BLR_4_HPS_GEN | 0 | [BLR_4_STATUS]*50 | 150 | [BLR_4_STATUS]*150 | 0 | GENERIC_TEMPLATE
BLR_4_FUEL_FLOW | 0 | 0 | 12 | max(12,[BLR_4_FUEL_FLOW]) | 0 | GENERIC_TEMPLATE
BLR_4_FD_FAN_STEAM | 0 | 0 | 8 | max([BLR_4_FD_FAN_STEAM],8) | 0 | GENERIC_TEMPLATE
BLR_5_STATUS | 0 | 0 | 1 | [BLR_5_STATUS] | 1 | GENERIC_TEMPLATE
BLR_5_HPS_GEN | 0 | [BLR_5_STATUS]*50 | 150 | [BLR_5_STATUS]*150 | 0 | GENERIC_TEMPLATE
BLR_5_FUEL_FLOW | 0 | 0 | 12 | max(12,[BLR_5_FUEL_FLOW]) | 0 | GENERIC_TEMPLATE
BLR_5_FD_FAN_STEAM | 0 | 0 | 8 | max([BLR_5_FD_FAN_STEAM],8) | 0 | GENERIC_TEMPLATE

## derived_equations
tag_name | formula_expression | active | source_flag
BLR_1_HPS_GEN | [BLR_1_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_1_SPEC_EN_CONS]*[BLR_1_STATUS]+(1-[BLR_1_STATUS])*[BLR_1_HPS_GEN_WARMUP] | 1 | GENERIC_TEMPLATE
BLR_1_FUEL_FLOW | [BLR_1_FUEL_FLOW]*[BLR_1_STATUS] | 1 | GENERIC_TEMPLATE
BLR_1_SPEC_EN_CONS | ([BLR_1_SPEC_EN_CONS_OPT]*(1-[BLR_1_SPEC_EN_CONS_DEV]))*[BLR_1_STATUS]+(1-[BLR_1_STATUS])*5 | 1 | GENERIC_TEMPLATE
BLR_1_FD_FAN_STEAM | if([BLR_1_FD_FAN_STEAM_RAW]<500,0,[BLR_1_FD_FAN_STEAM_RAW]/1000) | 1 | GENERIC_TEMPLATE
BLR_2_HPS_GEN | [BLR_2_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_2_SPEC_EN_CONS]*[BLR_2_STATUS]+(1-[BLR_2_STATUS])*[BLR_2_HPS_GEN_WARMUP] | 1 | GENERIC_TEMPLATE
BLR_2_FUEL_FLOW | [BLR_2_FUEL_FLOW]*[BLR_2_STATUS] | 1 | GENERIC_TEMPLATE
BLR_2_SPEC_EN_CONS | ([BLR_2_SPEC_EN_CONS_OPT]*(1-[BLR_2_SPEC_EN_CONS_DEV]))*[BLR_2_STATUS]+(1-[BLR_2_STATUS])*5 | 1 | GENERIC_TEMPLATE
BLR_2_FD_FAN_STEAM | if([BLR_2_FD_FAN_STEAM_RAW]<500,0,[BLR_2_FD_FAN_STEAM_RAW]/1000) | 1 | GENERIC_TEMPLATE
BLR_3_HPS_GEN | [BLR_3_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_3_SPEC_EN_CONS]*[BLR_3_STATUS]+(1-[BLR_3_STATUS])*[BLR_3_HPS_GEN_WARMUP] | 1 | GENERIC_TEMPLATE
BLR_3_FUEL_FLOW | [BLR_3_FUEL_FLOW]*[BLR_3_STATUS] | 1 | GENERIC_TEMPLATE
BLR_3_SPEC_EN_CONS | ([BLR_3_SPEC_EN_CONS_OPT]*(1-[BLR_3_SPEC_EN_CONS_DEV]))*[BLR_3_STATUS]+(1-[BLR_3_STATUS])*5 | 1 | GENERIC_TEMPLATE
BLR_3_FD_FAN_STEAM | if([BLR_3_FD_FAN_STEAM_RAW]<500,0,[BLR_3_FD_FAN_STEAM_RAW]/1000) | 1 | GENERIC_TEMPLATE
BLR_4_HPS_GEN | [BLR_4_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_4_SPEC_EN_CONS]*[BLR_4_STATUS]+(1-[BLR_4_STATUS])*[BLR_4_HPS_GEN_WARMUP] | 1 | GENERIC_TEMPLATE
BLR_4_FUEL_FLOW | [BLR_4_FUEL_FLOW]*[BLR_4_STATUS] | 1 | GENERIC_TEMPLATE
BLR_4_SPEC_EN_CONS | ([BLR_4_SPEC_EN_CONS_OPT]*(1-[BLR_4_SPEC_EN_CONS_DEV]))*[BLR_4_STATUS]+(1-[BLR_4_STATUS])*5 | 1 | GENERIC_TEMPLATE
BLR_4_FD_FAN_STEAM | if([BLR_4_FD_FAN_STEAM_RAW]<500,0,[BLR_4_FD_FAN_STEAM_RAW]/1000) | 1 | GENERIC_TEMPLATE
BLR_5_HPS_GEN | [BLR_5_FUEL_FLOW]*[UN.UO.BOILER_LHV]/[BLR_5_SPEC_EN_CONS]*[BLR_5_STATUS]+(1-[BLR_5_STATUS])*[BLR_5_HPS_GEN_WARMUP] | 1 | GENERIC_TEMPLATE
BLR_5_FUEL_FLOW | [BLR_5_FUEL_FLOW]*[BLR_5_STATUS] | 1 | GENERIC_TEMPLATE
BLR_5_SPEC_EN_CONS | ([BLR_5_SPEC_EN_CONS_OPT]*(1-[BLR_5_SPEC_EN_CONS_DEV]))*[BLR_5_STATUS]+(1-[BLR_5_STATUS])*5 | 1 | GENERIC_TEMPLATE
BLR_5_FD_FAN_STEAM | if([BLR_5_FD_FAN_STEAM_RAW]<500,0,[BLR_5_FD_FAN_STEAM_RAW]/1000) | 1 | GENERIC_TEMPLATE

## derived_equation_post_optimizer
tag_name | formula_expression | active
BLR_1_STACK_TEMP_CLIPPED | if([BLR_1_FLUE_GAS_OXYGEN]==0¦¦[BLR_1_STACK_TEMPERATURE]==0,[BLR_1_STACK_TEMPERATURE],min([BLR_1_STACK_TEMPERATURE],(0.368798*[BLR_1_HPS_GEN]+0.356735*[BLR_1_FLUE_GAS_OXYGEN]+117.092))*[BLR_1_STATUS]) | 1
BLR_2_STACK_TEMP_CLIPPED | if([BLR_2_FLUE_GAS_OXYGEN]==0¦¦[BLR_2_STACK_TEMPERATURE]==0,[BLR_2_STACK_TEMPERATURE],min([BLR_2_STACK_TEMPERATURE],(0.446276*[BLR_2_HPS_GEN]+0.310062*[BLR_2_FLUE_GAS_OXYGEN]+110.239))*[BLR_2_STATUS]) | 1
BLR_3_STACK_TEMP_CLIPPED | if([BLR_3_FLUE_GAS_OXYGEN]==0¦¦[BLR_3_STACK_TEMPERATURE]==0,[BLR_3_STACK_TEMPERATURE],min([BLR_3_STACK_TEMPERATURE],(0.399051*[BLR_3_HPS_GEN]-0.176072*[BLR_3_FLUE_GAS_OXYGEN]+116.397))*[BLR_3_STATUS]) | 1
BLR_4_STACK_TEMP_CLIPPED | if([BLR_4_FLUE_GAS_OXYGEN]==0¦¦[BLR_4_STACK_TEMPERATURE]==0,[BLR_4_STACK_TEMPERATURE],min([BLR_4_STACK_TEMPERATURE],(0.39909*[BLR_4_HPS_GEN]-0.482676*[BLR_4_FLUE_GAS_OXYGEN]+114.659))*[BLR_4_STATUS]) | 1
BLR_5_STACK_TEMP_CLIPPED | if([BLR_5_FLUE_GAS_OXYGEN]==0¦¦[BLR_5_STACK_TEMPERATURE]==0,[BLR_5_STACK_TEMPERATURE],min([BLR_5_STACK_TEMPERATURE],(0.313556*[BLR_5_HPS_GEN]+0.475168*[BLR_5_FLUE_GAS_OXYGEN]+132.57))*[BLR_5_STATUS]) | 1

## constraints
system | expression | active | source_flag
Boilers | [BLR_1_HPS_GEN] >= 50*[BLR_1_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_1_FUEL_FLOW] >= 0.000001*[BLR_1_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_2_HPS_GEN] >= 50*[BLR_2_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_2_FUEL_FLOW] >= 0.000001*[BLR_2_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_3_HPS_GEN] >= 50*[BLR_3_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_3_FUEL_FLOW] >= 0.000001*[BLR_3_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_4_HPS_GEN] >= 50*[BLR_4_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_4_FUEL_FLOW] >= 0.000001*[BLR_4_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_5_HPS_GEN] >= 50*[BLR_5_STATUS] | 1 | GENERIC_TEMPLATE
Boilers | [BLR_5_FUEL_FLOW] >= 0.000001*[BLR_5_STATUS] | 1 | GENERIC_TEMPLATE

## inferred_tag_rm_block_mapping
model_id | tag_name | data_enrichment_inferred_calculation | post_optimizer_inferred_calculation | pre_optimizer_iterative_inferred | data_ingestion_seu_seec_inferred_calc | data_enrichment_peeo_adjusted_inferred | whatif_inferred
1 | BLR_1_BOILER_LOAD | 1
1 | BLR_1_STATUS | 1
1 | BLR_1_FUEL_COMP_TOTAL | 1
1 | BLR_1_FG_NORM_CH4 | 1
1 | BLR_1_FG_NORM_ETHANE | 1
1 | BLR_1_FG_NORM_ETHYLENE | 1
1 | BLR_1_FG_NORM_PROPANE | 1
1 | BLR_1_FG_NORM_CO2 | 1
1 | BLR_1_FG_NORM_IC4 | 1
1 | BLR_1_FG_NORM_NC4 | 1
1 | BLR_1_FG_NORM_NC5 | 1
1 | BLR_1_FG_NORM_IC5 | 1
1 | BLR_1_FG_NORM_N2 | 1
1 | BLR_1_FG_NORM_H2 | 1
1 | BLR_1_FG_MW | 1
1 | BLR_1_FG_DENSITY | 1
1 | BLR_1_LHV_DESIGN | 1
1 | BLR_1_FG_CH4_MASS_PCT | 1
1 | BLR_1_FG_ETHANE_MASS_PCT | 1
1 | BLR_1_FG_ETHYLENE_MASS_PCT | 1
1 | BLR_1_FG_PROPANE_MASS_PCT | 1
1 | BLR_1_FG_N2_MASS_PCT | 1
1 | BLR_1_FG_H2_MASS_PCT | 1
1 | BLR_1_FG_IC4_MASS_PCT | 1
1 | BLR_1_FG_NC4_MASS_PCT | 1
1 | BLR_1_FG_NC5_MASS_PCT | 1
1 | BLR_1_FG_IC5_MASS_PCT | 1
1 | BLR_1_FG_CH4_MASS_FRAC | 1
1 | BLR_1_FG_ETHANE_MASS_FRAC | 1
1 | BLR_1_FG_ETHYLENE_MASS_FRAC | 1
1 | BLR_1_FG_PROPANE_MASS_FRAC | 1
1 | BLR_1_FG_N2_MASS_FRAC | 1
1 | BLR_1_FG_H2_MASS_FRAC | 1
1 | BLR_1_FG_IC4_MASS_FRAC | 1
1 | BLR_1_FG_NC4_MASS_FRAC | 1
1 | BLR_1_FG_NC5_MASS_FRAC | 1
1 | BLR_1_FG_IC5_MASS_FRAC | 1
1 | BLR_1_FG_FLOW_RATE_TPH | 1
1 | BLR_1_AIR_REQ_H2 | 1
1 | BLR_1_AIR_REQ_CH4 | 1
1 | BLR_1_AIR_REQ_ETHANE | 1
1 | BLR_1_AIR_REQ_ETHYLENE | 1
1 | BLR_1_AIR_REQ_PROPANE | 1
1 | BLR_1_AIR_REQ_NC4 | 1
1 | BLR_1_AIR_REQ_IC4 | 1
1 | BLR_1_AIR_REQ_NC5 | 1
1 | BLR_1_AIR_REQ_IC5 | 1
1 | BLR_1_CO2_COMB_H2 | 1
1 | BLR_1_CO2_COMB_CH4 | 1
1 | BLR_1_CO2_COMB_ETHANE | 1
1 | BLR_1_CO2_COMB_ETHYLENE | 1
1 | BLR_1_CO2_COMB_PROPANE | 1
1 | BLR_1_CO2_COMB_NC4 | 1
1 | BLR_1_CO2_COMB_IC4 | 1
1 | BLR_1_CO2_COMB_NC5 | 1
1 | BLR_1_CO2_COMB_IC5 | 1
1 | BLR_1_N2_COMB_H2 | 1
1 | BLR_1_N2_COMB_CH4 | 1
1 | BLR_1_N2_COMB_ETHANE | 1
1 | BLR_1_N2_COMB_ETHYLENE | 1
1 | BLR_1_N2_COMB_PROPANE | 1
1 | BLR_1_N2_COMB_IC4 | 1
1 | BLR_1_N2_COMB_NC4 | 1
1 | BLR_1_N2_COMB_IC5 | 1
1 | BLR_1_N2_COMB_NC5 | 1
1 | BLR_1_H2O_COMB_H2 | 1
1 | BLR_1_H2O_COMB_CH4 | 1
1 | BLR_1_H2O_COMB_ETHANE | 1
1 | BLR_1_H2O_COMB_ETHYLENE | 1
1 | BLR_1_H2O_COMB_PROPANE | 1
1 | BLR_1_H2O_COMB_IC4 | 1
1 | BLR_1_H2O_COMB_NC4 | 1
1 | BLR_1_H2O_COMB_IC5 | 1
1 | BLR_1_H2O_COMB_NC5 | 1
1 | BLR_1_AIR_REQ_COMPLETE | 1
1 | BLR_1_CO2_FORMED | 1
1 | BLR_1_N2_FORMED | 1
1 | BLR_1_H2O_FORMED | 1
1 | BLR_1_VAPOUR_PRESSURE_H2O | 1
1 | BLR_1_AIR_MOISTURE | 1
1 | BLR_1_CORRECTED_COMBUSTION_AIR | 1
1 | BLR_1_CORRECTED_H2O_FORMED | 1
1 | BLR_1_EXCESS_AIR | 1
1 | BLR_1_AIR_FUEL_MASS_RATIO | 1
1 | BLR_1_TOTAL_MOISTURE_WITH_AIR | 1
1 | BLR_1_TOTAL_H2O_PER_KG_FUEL | 1
1 | BLR_1_DRY_FLUE_GAS_RATIO | 1
1 | BLR_1_FLUE_GAS_RATIO | 1
1 | BLR_1_FLUE_GAS_MW | 1
1 | BLR_1_AIR_CP_REF_T | 1
1 | BLR_1_CP_AT_COMB_TEMP | 1
1 | BLR_1_AIR_CP_SENSIBLE_CORRECTED | 1
1 | BLR_1_CP_H2_FUEL_TEMP | 1
1 | BLR_1_CP_CH4_FUEL_TEMP | 1
1 | BLR_1_CP_ETHANE_FUEL_TEMP | 1
1 | BLR_1_CP_PROPANE_FUEL_TEMP | 1
1 | BLR_1_CP_ETHYLENE_FUEL_TEMP | 1
1 | BLR_1_CP_NC4_FUEL_TEMP | 1
1 | BLR_1_CP_IC4_FUEL_TEMP | 1
1 | BLR_1_CP_NC5_FUEL_TEMP | 1
1 | BLR_1_CP_IC5_FUEL_TEMP | 1
1 | BLR_1_CP_FUEL_AT_REF_TEMP | 1
1 | BLR_1_CP_FUEL_AT_FUEL_TEMP | 1
1 | BLR_1_AVG_CP_FUEL_SENSIBLE | 1
1 | BLR_1_CP_AIR_AT_STACK_TEMP | 1
1 | BLR_1_CP_FLUE_CO2_AT_STACK | 1
1 | BLR_1_CP_FLUE_H2O_AT_STACK | 1
1 | BLR_1_CP_FLUE_N2_AT_STACK | 1
1 | BLR_1_AVG_CP_FLUE_AT_STACK | 1
1 | BLR_1_CP_H2O_AT_STACK | 1
1 | BLR_1_SH_CORRECTION_FUEL | 1
1 | BLR_1_SH_CORRECTION_AIR | 1
1 | BLR_1_MIXED_LHV_PER_KG | 1
1 | BLR_1_TOTAL_HEAT_INPUT | 1
1 | BLR_1_HEAT_LOSS_L1 | 1
1 | BLR_1_HEAT_LOSS_L2 | 1
1 | BLR_1_HEAT_LOSS_L3 | 1
1 | BLR_1_HEAT_LOSS_L4 | 1
1 | BLR_1_TOTAL_STACK_LOSS_PER_KG | 1
1 | BLR_1_RADIATION_LOSSES | 1
1 | BLR_1_TOTAL_HEAT_LOSS | 1
1 | BLR_1_TOTAL_HEAT_ABSORBED | 1
1 | BLR_1_INDIRECT_EFFICIENCY | 1
1 | BLR_1_HP_STEAM_ENTHALPY | 1
1 | BLR_1_TOTAL_STEAM_ENERGY | 1
1 | BLR_1_BFW_ENTHALPY | 1
1 | BLR_1_CORRECTED_BFW_FLOW | 1
1 | BLR_1_BFW_ENERGY | 1
1 | BLR_1_FUEL_GAS_ENERGY_INPUT | 1
1 | BLR_1_STEAM_DRUM_TEMP | 1
1 | BLR_1_BLOWDOWN_LOSS | 1
1 | BLR_1_TOTAL_FLUE_GAS_GENERATED | 1
1 | BLR_1_STACK_LOSS | 1
1 | BLR_1_CORRECTED_FUEL_FLOW | 1
1 | BLR_1_FUEL_CONSUMPTION_GCAL | 1
1 | BLR_1_SEC_GCAL_T | 1
1 | BLR_1_SEC_GJ_T | 1
1 | BLR_1_CORRECTED_FUEL_ENERGY_INPUT | 1
1 | BLR_1_THERMAL_EFFICIENCY | 1
1 | BLR_1_FUEL_GAS_CORRECTED_TPH | 1
1 | BLR_1_TOTAL_FLUE_GAS_CORRECTED | 1
1 | BLR_1_STACK_LOSS_CORRECTED | 1
1 | BLR_1_BFW_STEAM_RATIO | 1
1 | BLR_1_CO2_EMISSIONS | 1
1 | BLR_1_CALCULATED_AIRFLOW_NM3H | 1
1 | BLR_1_STEAM_TO_FIRE_RATIO | 1
1 | BLR_1_ECONOMIZER_DUTY | 1
1 | BLR_1_LMTD_ECONOMIZER | 1
1 | BLR_1_UA_ECONOMIZER | 1
1 | BLR_1_FOULING_INDEX | 1
1 | BLR_1_SH_DUTY | 1
1 | BLR_1_SH_SPECIFIC_DUTY | 1
1 | BLR_1_SH_PERFORMANCE | 1
1 | BLR_1_ENERGY_GAINED | 1
1 | BLR_1_CONVECTION_DUTY | 1
1 | BLR_1_RADIATION_DUTY | 1
1 | BLR_1_PCT_DUTY_CONVECTION | 1
1 | BLR_1_PCT_DUTY_RADIANT | 1
1 | BLR_1_DUTY_RATIO_RAD_CONV | 1
1 | BLR_1_RADIATION_SECTION_EFF | 1
1 | BLR_1_CONVECTION_SECTION_EFF | 1
1 | BLR_1_HPS_GEN | 1
1 | BLR_1_FUEL_FLOW | 1
1 | BLR_1_CAPACITY | 1
1 | BLR_1_SPEC_EN_CONS | 1
1 | BLR_1_SPEC_EN_CONS_OPT | 1
1 | BLR_1_SPEC_EN_CONS_DEV | 1
1 | BLR_1_HPS_GEN_WARMUP | 1
1 | BLR_1_FD_FAN_STEAM_REG | 1
1 | BLR_1_FD_FAN_STEAM_WARMUP | 1
1 | BLR_1_FD_FAN_STEAM | 1
1 | BLR_2_BOILER_LOAD | 1
1 | BLR_2_STATUS | 1
1 | BLR_2_FUEL_COMP_TOTAL | 1
1 | BLR_2_FG_NORM_CH4 | 1
1 | BLR_2_FG_NORM_ETHANE | 1
1 | BLR_2_FG_NORM_ETHYLENE | 1
1 | BLR_2_FG_NORM_PROPANE | 1
1 | BLR_2_FG_NORM_CO2 | 1
1 | BLR_2_FG_NORM_IC4 | 1
1 | BLR_2_FG_NORM_NC4 | 1
1 | BLR_2_FG_NORM_NC5 | 1
1 | BLR_2_FG_NORM_IC5 | 1
1 | BLR_2_FG_NORM_N2 | 1
1 | BLR_2_FG_NORM_H2 | 1
1 | BLR_2_FG_MW | 1
1 | BLR_2_FG_DENSITY | 1
1 | BLR_2_LHV_DESIGN | 1
1 | BLR_2_FG_CH4_MASS_PCT | 1
1 | BLR_2_FG_ETHANE_MASS_PCT | 1
1 | BLR_2_FG_ETHYLENE_MASS_PCT | 1
1 | BLR_2_FG_PROPANE_MASS_PCT | 1
1 | BLR_2_FG_N2_MASS_PCT | 1
1 | BLR_2_FG_H2_MASS_PCT | 1
1 | BLR_2_FG_IC4_MASS_PCT | 1
1 | BLR_2_FG_NC4_MASS_PCT | 1
1 | BLR_2_FG_NC5_MASS_PCT | 1
1 | BLR_2_FG_IC5_MASS_PCT | 1
1 | BLR_2_FG_CH4_MASS_FRAC | 1
1 | BLR_2_FG_ETHANE_MASS_FRAC | 1
1 | BLR_2_FG_ETHYLENE_MASS_FRAC | 1
1 | BLR_2_FG_PROPANE_MASS_FRAC | 1
1 | BLR_2_FG_N2_MASS_FRAC | 1
1 | BLR_2_FG_H2_MASS_FRAC | 1
1 | BLR_2_FG_IC4_MASS_FRAC | 1
1 | BLR_2_FG_NC4_MASS_FRAC | 1
1 | BLR_2_FG_NC5_MASS_FRAC | 1
1 | BLR_2_FG_IC5_MASS_FRAC | 1
1 | BLR_2_FG_FLOW_RATE_TPH | 1
1 | BLR_2_AIR_REQ_H2 | 1
1 | BLR_2_AIR_REQ_CH4 | 1
1 | BLR_2_AIR_REQ_ETHANE | 1
1 | BLR_2_AIR_REQ_ETHYLENE | 1
1 | BLR_2_AIR_REQ_PROPANE | 1
1 | BLR_2_AIR_REQ_NC4 | 1
1 | BLR_2_AIR_REQ_IC4 | 1
1 | BLR_2_AIR_REQ_NC5 | 1
1 | BLR_2_AIR_REQ_IC5 | 1
1 | BLR_2_CO2_COMB_H2 | 1
1 | BLR_2_CO2_COMB_CH4 | 1
1 | BLR_2_CO2_COMB_ETHANE | 1
1 | BLR_2_CO2_COMB_ETHYLENE | 1
1 | BLR_2_CO2_COMB_PROPANE | 1
1 | BLR_2_CO2_COMB_NC4 | 1
1 | BLR_2_CO2_COMB_IC4 | 1
1 | BLR_2_CO2_COMB_NC5 | 1
1 | BLR_2_CO2_COMB_IC5 | 1
1 | BLR_2_N2_COMB_H2 | 1
1 | BLR_2_N2_COMB_CH4 | 1
1 | BLR_2_N2_COMB_ETHANE | 1
1 | BLR_2_N2_COMB_ETHYLENE | 1
1 | BLR_2_N2_COMB_PROPANE | 1
1 | BLR_2_N2_COMB_IC4 | 1
1 | BLR_2_N2_COMB_NC4 | 1
1 | BLR_2_N2_COMB_IC5 | 1
1 | BLR_2_N2_COMB_NC5 | 1
1 | BLR_2_H2O_COMB_H2 | 1
1 | BLR_2_H2O_COMB_CH4 | 1
1 | BLR_2_H2O_COMB_ETHANE | 1
1 | BLR_2_H2O_COMB_ETHYLENE | 1
1 | BLR_2_H2O_COMB_PROPANE | 1
1 | BLR_2_H2O_COMB_IC4 | 1
1 | BLR_2_H2O_COMB_NC4 | 1
1 | BLR_2_H2O_COMB_IC5 | 1
1 | BLR_2_H2O_COMB_NC5 | 1
1 | BLR_2_AIR_REQ_COMPLETE | 1
1 | BLR_2_CO2_FORMED | 1
1 | BLR_2_N2_FORMED | 1
1 | BLR_2_H2O_FORMED | 1
1 | BLR_2_VAPOUR_PRESSURE_H2O | 1
1 | BLR_2_AIR_MOISTURE | 1
1 | BLR_2_CORRECTED_COMBUSTION_AIR | 1
1 | BLR_2_CORRECTED_H2O_FORMED | 1
1 | BLR_2_EXCESS_AIR | 1
1 | BLR_2_AIR_FUEL_MASS_RATIO | 1
1 | BLR_2_TOTAL_MOISTURE_WITH_AIR | 1
1 | BLR_2_TOTAL_H2O_PER_KG_FUEL | 1
1 | BLR_2_DRY_FLUE_GAS_RATIO | 1
1 | BLR_2_FLUE_GAS_RATIO | 1
1 | BLR_2_FLUE_GAS_MW | 1
1 | BLR_2_AIR_CP_REF_T | 1
1 | BLR_2_CP_AT_COMB_TEMP | 1
1 | BLR_2_AIR_CP_SENSIBLE_CORRECTED | 1
1 | BLR_2_CP_H2_FUEL_TEMP | 1
1 | BLR_2_CP_CH4_FUEL_TEMP | 1
1 | BLR_2_CP_ETHANE_FUEL_TEMP | 1
1 | BLR_2_CP_PROPANE_FUEL_TEMP | 1
1 | BLR_2_CP_ETHYLENE_FUEL_TEMP | 1
1 | BLR_2_CP_NC4_FUEL_TEMP | 1
1 | BLR_2_CP_IC4_FUEL_TEMP | 1
1 | BLR_2_CP_NC5_FUEL_TEMP | 1
1 | BLR_2_CP_IC5_FUEL_TEMP | 1
1 | BLR_2_CP_FUEL_AT_REF_TEMP | 1
1 | BLR_2_CP_FUEL_AT_FUEL_TEMP | 1
1 | BLR_2_AVG_CP_FUEL_SENSIBLE | 1
1 | BLR_2_CP_AIR_AT_STACK_TEMP | 1
1 | BLR_2_CP_FLUE_CO2_AT_STACK | 1
1 | BLR_2_CP_FLUE_H2O_AT_STACK | 1
1 | BLR_2_CP_FLUE_N2_AT_STACK | 1
1 | BLR_2_AVG_CP_FLUE_AT_STACK | 1
1 | BLR_2_CP_H2O_AT_STACK | 1
1 | BLR_2_SH_CORRECTION_FUEL | 1
1 | BLR_2_SH_CORRECTION_AIR | 1
1 | BLR_2_MIXED_LHV_PER_KG | 1
1 | BLR_2_TOTAL_HEAT_INPUT | 1
1 | BLR_2_HEAT_LOSS_L1 | 1
1 | BLR_2_HEAT_LOSS_L2 | 1
1 | BLR_2_HEAT_LOSS_L3 | 1
1 | BLR_2_HEAT_LOSS_L4 | 1
1 | BLR_2_TOTAL_STACK_LOSS_PER_KG | 1
1 | BLR_2_RADIATION_LOSSES | 1
1 | BLR_2_TOTAL_HEAT_LOSS | 1
1 | BLR_2_TOTAL_HEAT_ABSORBED | 1
1 | BLR_2_INDIRECT_EFFICIENCY | 1
1 | BLR_2_HP_STEAM_ENTHALPY | 1
1 | BLR_2_TOTAL_STEAM_ENERGY | 1
1 | BLR_2_BFW_ENTHALPY | 1
1 | BLR_2_CORRECTED_BFW_FLOW | 1
1 | BLR_2_BFW_ENERGY | 1
1 | BLR_2_FUEL_GAS_ENERGY_INPUT | 1
1 | BLR_2_STEAM_DRUM_TEMP | 1
1 | BLR_2_BLOWDOWN_LOSS | 1
1 | BLR_2_TOTAL_FLUE_GAS_GENERATED | 1
1 | BLR_2_STACK_LOSS | 1
1 | BLR_2_CORRECTED_FUEL_FLOW | 1
1 | BLR_2_FUEL_CONSUMPTION_GCAL | 1
1 | BLR_2_SEC_GCAL_T | 1
1 | BLR_2_SEC_GJ_T | 1
1 | BLR_2_CORRECTED_FUEL_ENERGY_INPUT | 1
1 | BLR_2_THERMAL_EFFICIENCY | 1
1 | BLR_2_FUEL_GAS_CORRECTED_TPH | 1
1 | BLR_2_TOTAL_FLUE_GAS_CORRECTED | 1
1 | BLR_2_STACK_LOSS_CORRECTED | 1
1 | BLR_2_BFW_STEAM_RATIO | 1
1 | BLR_2_CO2_EMISSIONS | 1
1 | BLR_2_CALCULATED_AIRFLOW_NM3H | 1
1 | BLR_2_STEAM_TO_FIRE_RATIO | 1
1 | BLR_2_ECONOMIZER_DUTY | 1
1 | BLR_2_LMTD_ECONOMIZER | 1
1 | BLR_2_UA_ECONOMIZER | 1
1 | BLR_2_FOULING_INDEX | 1
1 | BLR_2_SH_DUTY | 1
1 | BLR_2_SH_SPECIFIC_DUTY | 1
1 | BLR_2_SH_PERFORMANCE | 1
1 | BLR_2_ENERGY_GAINED | 1
1 | BLR_2_CONVECTION_DUTY | 1
1 | BLR_2_RADIATION_DUTY | 1
1 | BLR_2_PCT_DUTY_CONVECTION | 1
1 | BLR_2_PCT_DUTY_RADIANT | 1
1 | BLR_2_DUTY_RATIO_RAD_CONV | 1
1 | BLR_2_RADIATION_SECTION_EFF | 1
1 | BLR_2_CONVECTION_SECTION_EFF | 1
1 | BLR_2_HPS_GEN | 1
1 | BLR_2_FUEL_FLOW | 1
1 | BLR_2_CAPACITY | 1
1 | BLR_2_SPEC_EN_CONS | 1
1 | BLR_2_SPEC_EN_CONS_OPT | 1
1 | BLR_2_SPEC_EN_CONS_DEV | 1
1 | BLR_2_HPS_GEN_WARMUP | 1
1 | BLR_2_FD_FAN_STEAM_REG | 1
1 | BLR_2_FD_FAN_STEAM_WARMUP | 1
1 | BLR_2_FD_FAN_STEAM | 1
1 | BLR_3_BOILER_LOAD | 1
1 | BLR_3_STATUS | 1
1 | BLR_3_FUEL_COMP_TOTAL | 1
1 | BLR_3_FG_NORM_CH4 | 1
1 | BLR_3_FG_NORM_ETHANE | 1
1 | BLR_3_FG_NORM_ETHYLENE | 1
1 | BLR_3_FG_NORM_PROPANE | 1
1 | BLR_3_FG_NORM_CO2 | 1
1 | BLR_3_FG_NORM_IC4 | 1
1 | BLR_3_FG_NORM_NC4 | 1
1 | BLR_3_FG_NORM_NC5 | 1
1 | BLR_3_FG_NORM_IC5 | 1
1 | BLR_3_FG_NORM_N2 | 1
1 | BLR_3_FG_NORM_H2 | 1
1 | BLR_3_FG_MW | 1
1 | BLR_3_FG_DENSITY | 1
1 | BLR_3_LHV_DESIGN | 1
1 | BLR_3_FG_CH4_MASS_PCT | 1
1 | BLR_3_FG_ETHANE_MASS_PCT | 1
1 | BLR_3_FG_ETHYLENE_MASS_PCT | 1
1 | BLR_3_FG_PROPANE_MASS_PCT | 1
1 | BLR_3_FG_N2_MASS_PCT | 1
1 | BLR_3_FG_H2_MASS_PCT | 1
1 | BLR_3_FG_IC4_MASS_PCT | 1
1 | BLR_3_FG_NC4_MASS_PCT | 1
1 | BLR_3_FG_NC5_MASS_PCT | 1
1 | BLR_3_FG_IC5_MASS_PCT | 1
1 | BLR_3_FG_CH4_MASS_FRAC | 1
1 | BLR_3_FG_ETHANE_MASS_FRAC | 1
1 | BLR_3_FG_ETHYLENE_MASS_FRAC | 1
1 | BLR_3_FG_PROPANE_MASS_FRAC | 1
1 | BLR_3_FG_N2_MASS_FRAC | 1
1 | BLR_3_FG_H2_MASS_FRAC | 1
1 | BLR_3_FG_IC4_MASS_FRAC | 1
1 | BLR_3_FG_NC4_MASS_FRAC | 1
1 | BLR_3_FG_NC5_MASS_FRAC | 1
1 | BLR_3_FG_IC5_MASS_FRAC | 1
1 | BLR_3_FG_FLOW_RATE_TPH | 1
1 | BLR_3_AIR_REQ_H2 | 1
1 | BLR_3_AIR_REQ_CH4 | 1
1 | BLR_3_AIR_REQ_ETHANE | 1
1 | BLR_3_AIR_REQ_ETHYLENE | 1
1 | BLR_3_AIR_REQ_PROPANE | 1
1 | BLR_3_AIR_REQ_NC4 | 1
1 | BLR_3_AIR_REQ_IC4 | 1
1 | BLR_3_AIR_REQ_NC5 | 1
1 | BLR_3_AIR_REQ_IC5 | 1
1 | BLR_3_CO2_COMB_H2 | 1
1 | BLR_3_CO2_COMB_CH4 | 1
1 | BLR_3_CO2_COMB_ETHANE | 1
1 | BLR_3_CO2_COMB_ETHYLENE | 1
1 | BLR_3_CO2_COMB_PROPANE | 1
1 | BLR_3_CO2_COMB_NC4 | 1
1 | BLR_3_CO2_COMB_IC4 | 1
1 | BLR_3_CO2_COMB_NC5 | 1
1 | BLR_3_CO2_COMB_IC5 | 1
1 | BLR_3_N2_COMB_H2 | 1
1 | BLR_3_N2_COMB_CH4 | 1
1 | BLR_3_N2_COMB_ETHANE | 1
1 | BLR_3_N2_COMB_ETHYLENE | 1
1 | BLR_3_N2_COMB_PROPANE | 1
1 | BLR_3_N2_COMB_IC4 | 1
1 | BLR_3_N2_COMB_NC4 | 1
1 | BLR_3_N2_COMB_IC5 | 1
1 | BLR_3_N2_COMB_NC5 | 1
1 | BLR_3_H2O_COMB_H2 | 1
1 | BLR_3_H2O_COMB_CH4 | 1
1 | BLR_3_H2O_COMB_ETHANE | 1
1 | BLR_3_H2O_COMB_ETHYLENE | 1
1 | BLR_3_H2O_COMB_PROPANE | 1
1 | BLR_3_H2O_COMB_IC4 | 1
1 | BLR_3_H2O_COMB_NC4 | 1
1 | BLR_3_H2O_COMB_IC5 | 1
1 | BLR_3_H2O_COMB_NC5 | 1
1 | BLR_3_AIR_REQ_COMPLETE | 1
1 | BLR_3_CO2_FORMED | 1
1 | BLR_3_N2_FORMED | 1
1 | BLR_3_H2O_FORMED | 1
1 | BLR_3_VAPOUR_PRESSURE_H2O | 1
1 | BLR_3_AIR_MOISTURE | 1
1 | BLR_3_CORRECTED_COMBUSTION_AIR | 1
1 | BLR_3_CORRECTED_H2O_FORMED | 1
1 | BLR_3_EXCESS_AIR | 1
1 | BLR_3_AIR_FUEL_MASS_RATIO | 1
1 | BLR_3_TOTAL_MOISTURE_WITH_AIR | 1
1 | BLR_3_TOTAL_H2O_PER_KG_FUEL | 1
1 | BLR_3_DRY_FLUE_GAS_RATIO | 1
1 | BLR_3_FLUE_GAS_RATIO | 1
1 | BLR_3_FLUE_GAS_MW | 1
1 | BLR_3_AIR_CP_REF_T | 1
1 | BLR_3_CP_AT_COMB_TEMP | 1
1 | BLR_3_AIR_CP_SENSIBLE_CORRECTED | 1
1 | BLR_3_CP_H2_FUEL_TEMP | 1
1 | BLR_3_CP_CH4_FUEL_TEMP | 1
1 | BLR_3_CP_ETHANE_FUEL_TEMP | 1
1 | BLR_3_CP_PROPANE_FUEL_TEMP | 1
1 | BLR_3_CP_ETHYLENE_FUEL_TEMP | 1
1 | BLR_3_CP_NC4_FUEL_TEMP | 1
1 | BLR_3_CP_IC4_FUEL_TEMP | 1
1 | BLR_3_CP_NC5_FUEL_TEMP | 1
1 | BLR_3_CP_IC5_FUEL_TEMP | 1
1 | BLR_3_CP_FUEL_AT_REF_TEMP | 1
1 | BLR_3_CP_FUEL_AT_FUEL_TEMP | 1
1 | BLR_3_AVG_CP_FUEL_SENSIBLE | 1
1 | BLR_3_CP_AIR_AT_STACK_TEMP | 1
1 | BLR_3_CP_FLUE_CO2_AT_STACK | 1
1 | BLR_3_CP_FLUE_H2O_AT_STACK | 1
1 | BLR_3_CP_FLUE_N2_AT_STACK | 1
1 | BLR_3_AVG_CP_FLUE_AT_STACK | 1
1 | BLR_3_CP_H2O_AT_STACK | 1
1 | BLR_3_SH_CORRECTION_FUEL | 1
1 | BLR_3_SH_CORRECTION_AIR | 1
1 | BLR_3_MIXED_LHV_PER_KG | 1
1 | BLR_3_TOTAL_HEAT_INPUT | 1
1 | BLR_3_HEAT_LOSS_L1 | 1
1 | BLR_3_HEAT_LOSS_L2 | 1
1 | BLR_3_HEAT_LOSS_L3 | 1
1 | BLR_3_HEAT_LOSS_L4 | 1
1 | BLR_3_TOTAL_STACK_LOSS_PER_KG | 1
1 | BLR_3_RADIATION_LOSSES | 1
1 | BLR_3_TOTAL_HEAT_LOSS | 1
1 | BLR_3_TOTAL_HEAT_ABSORBED | 1
1 | BLR_3_INDIRECT_EFFICIENCY | 1
1 | BLR_3_HP_STEAM_ENTHALPY | 1
1 | BLR_3_TOTAL_STEAM_ENERGY | 1
1 | BLR_3_BFW_ENTHALPY | 1
1 | BLR_3_CORRECTED_BFW_FLOW | 1
1 | BLR_3_BFW_ENERGY | 1
1 | BLR_3_FUEL_GAS_ENERGY_INPUT | 1
1 | BLR_3_STEAM_DRUM_TEMP | 1
1 | BLR_3_BLOWDOWN_LOSS | 1
1 | BLR_3_TOTAL_FLUE_GAS_GENERATED | 1
1 | BLR_3_STACK_LOSS | 1
1 | BLR_3_CORRECTED_FUEL_FLOW | 1
1 | BLR_3_FUEL_CONSUMPTION_GCAL | 1
1 | BLR_3_SEC_GCAL_T | 1
1 | BLR_3_SEC_GJ_T | 1
1 | BLR_3_CORRECTED_FUEL_ENERGY_INPUT | 1
1 | BLR_3_THERMAL_EFFICIENCY | 1
1 | BLR_3_FUEL_GAS_CORRECTED_TPH | 1
1 | BLR_3_TOTAL_FLUE_GAS_CORRECTED | 1
1 | BLR_3_STACK_LOSS_CORRECTED | 1
1 | BLR_3_BFW_STEAM_RATIO | 1
1 | BLR_3_CO2_EMISSIONS | 1
1 | BLR_3_CALCULATED_AIRFLOW_NM3H | 1
1 | BLR_3_STEAM_TO_FIRE_RATIO | 1
1 | BLR_3_ECONOMIZER_DUTY | 1
1 | BLR_3_LMTD_ECONOMIZER | 1
1 | BLR_3_UA_ECONOMIZER | 1
1 | BLR_3_FOULING_INDEX | 1
1 | BLR_3_SH_DUTY | 1
1 | BLR_3_SH_SPECIFIC_DUTY | 1
1 | BLR_3_SH_PERFORMANCE | 1
1 | BLR_3_ENERGY_GAINED | 1
1 | BLR_3_CONVECTION_DUTY | 1
1 | BLR_3_RADIATION_DUTY | 1
1 | BLR_3_PCT_DUTY_CONVECTION | 1
1 | BLR_3_PCT_DUTY_RADIANT | 1
1 | BLR_3_DUTY_RATIO_RAD_CONV | 1
1 | BLR_3_RADIATION_SECTION_EFF | 1
1 | BLR_3_CONVECTION_SECTION_EFF | 1
1 | BLR_3_HPS_GEN | 1
1 | BLR_3_FUEL_FLOW | 1
1 | BLR_3_CAPACITY | 1
1 | BLR_3_SPEC_EN_CONS | 1
1 | BLR_3_SPEC_EN_CONS_OPT | 1
1 | BLR_3_SPEC_EN_CONS_DEV | 1
1 | BLR_3_HPS_GEN_WARMUP | 1
1 | BLR_3_FD_FAN_STEAM_REG | 1
1 | BLR_3_FD_FAN_STEAM_WARMUP | 1
1 | BLR_3_FD_FAN_STEAM | 1
1 | BLR_4_BOILER_LOAD | 1
1 | BLR_4_STATUS | 1
1 | BLR_4_FUEL_COMP_TOTAL | 1
1 | BLR_4_FG_NORM_CH4 | 1
1 | BLR_4_FG_NORM_ETHANE | 1
1 | BLR_4_FG_NORM_ETHYLENE | 1
1 | BLR_4_FG_NORM_PROPANE | 1
1 | BLR_4_FG_NORM_CO2 | 1
1 | BLR_4_FG_NORM_IC4 | 1
1 | BLR_4_FG_NORM_NC4 | 1
1 | BLR_4_FG_NORM_NC5 | 1
1 | BLR_4_FG_NORM_IC5 | 1
1 | BLR_4_FG_NORM_N2 | 1
1 | BLR_4_FG_NORM_H2 | 1
1 | BLR_4_FG_MW | 1
1 | BLR_4_FG_DENSITY | 1
1 | BLR_4_LHV_DESIGN | 1
1 | BLR_4_FG_CH4_MASS_PCT | 1
1 | BLR_4_FG_ETHANE_MASS_PCT | 1
1 | BLR_4_FG_ETHYLENE_MASS_PCT | 1
1 | BLR_4_FG_PROPANE_MASS_PCT | 1
1 | BLR_4_FG_N2_MASS_PCT | 1
1 | BLR_4_FG_H2_MASS_PCT | 1
1 | BLR_4_FG_IC4_MASS_PCT | 1
1 | BLR_4_FG_NC4_MASS_PCT | 1
1 | BLR_4_FG_NC5_MASS_PCT | 1
1 | BLR_4_FG_IC5_MASS_PCT | 1
1 | BLR_4_FG_CH4_MASS_FRAC | 1
1 | BLR_4_FG_ETHANE_MASS_FRAC | 1
1 | BLR_4_FG_ETHYLENE_MASS_FRAC | 1
1 | BLR_4_FG_PROPANE_MASS_FRAC | 1
1 | BLR_4_FG_N2_MASS_FRAC | 1
1 | BLR_4_FG_H2_MASS_FRAC | 1
1 | BLR_4_FG_IC4_MASS_FRAC | 1
1 | BLR_4_FG_NC4_MASS_FRAC | 1
1 | BLR_4_FG_NC5_MASS_FRAC | 1
1 | BLR_4_FG_IC5_MASS_FRAC | 1
1 | BLR_4_FG_FLOW_RATE_TPH | 1
1 | BLR_4_AIR_REQ_H2 | 1
1 | BLR_4_AIR_REQ_CH4 | 1
1 | BLR_4_AIR_REQ_ETHANE | 1
1 | BLR_4_AIR_REQ_ETHYLENE | 1
1 | BLR_4_AIR_REQ_PROPANE | 1
1 | BLR_4_AIR_REQ_NC4 | 1
1 | BLR_4_AIR_REQ_IC4 | 1
1 | BLR_4_AIR_REQ_NC5 | 1
1 | BLR_4_AIR_REQ_IC5 | 1
1 | BLR_4_CO2_COMB_H2 | 1
1 | BLR_4_CO2_COMB_CH4 | 1
1 | BLR_4_CO2_COMB_ETHANE | 1
1 | BLR_4_CO2_COMB_ETHYLENE | 1
1 | BLR_4_CO2_COMB_PROPANE | 1
1 | BLR_4_CO2_COMB_NC4 | 1
1 | BLR_4_CO2_COMB_IC4 | 1
1 | BLR_4_CO2_COMB_NC5 | 1
1 | BLR_4_CO2_COMB_IC5 | 1
1 | BLR_4_N2_COMB_H2 | 1
1 | BLR_4_N2_COMB_CH4 | 1
1 | BLR_4_N2_COMB_ETHANE | 1
1 | BLR_4_N2_COMB_ETHYLENE | 1
1 | BLR_4_N2_COMB_PROPANE | 1
1 | BLR_4_N2_COMB_IC4 | 1
1 | BLR_4_N2_COMB_NC4 | 1
1 | BLR_4_N2_COMB_IC5 | 1
1 | BLR_4_N2_COMB_NC5 | 1
1 | BLR_4_H2O_COMB_H2 | 1
1 | BLR_4_H2O_COMB_CH4 | 1
1 | BLR_4_H2O_COMB_ETHANE | 1
1 | BLR_4_H2O_COMB_ETHYLENE | 1
1 | BLR_4_H2O_COMB_PROPANE | 1
1 | BLR_4_H2O_COMB_IC4 | 1
1 | BLR_4_H2O_COMB_NC4 | 1
1 | BLR_4_H2O_COMB_IC5 | 1
1 | BLR_4_H2O_COMB_NC5 | 1
1 | BLR_4_AIR_REQ_COMPLETE | 1
1 | BLR_4_CO2_FORMED | 1
1 | BLR_4_N2_FORMED | 1
1 | BLR_4_H2O_FORMED | 1
1 | BLR_4_VAPOUR_PRESSURE_H2O | 1
1 | BLR_4_AIR_MOISTURE | 1
1 | BLR_4_CORRECTED_COMBUSTION_AIR | 1
1 | BLR_4_CORRECTED_H2O_FORMED | 1
1 | BLR_4_EXCESS_AIR | 1
1 | BLR_4_AIR_FUEL_MASS_RATIO | 1
1 | BLR_4_TOTAL_MOISTURE_WITH_AIR | 1
1 | BLR_4_TOTAL_H2O_PER_KG_FUEL | 1
1 | BLR_4_DRY_FLUE_GAS_RATIO | 1
1 | BLR_4_FLUE_GAS_RATIO | 1
1 | BLR_4_FLUE_GAS_MW | 1
1 | BLR_4_AIR_CP_REF_T | 1
1 | BLR_4_CP_AT_COMB_TEMP | 1
1 | BLR_4_AIR_CP_SENSIBLE_CORRECTED | 1
1 | BLR_4_CP_H2_FUEL_TEMP | 1
1 | BLR_4_CP_CH4_FUEL_TEMP | 1
1 | BLR_4_CP_ETHANE_FUEL_TEMP | 1
1 | BLR_4_CP_PROPANE_FUEL_TEMP | 1
1 | BLR_4_CP_ETHYLENE_FUEL_TEMP | 1
1 | BLR_4_CP_NC4_FUEL_TEMP | 1
1 | BLR_4_CP_IC4_FUEL_TEMP | 1
1 | BLR_4_CP_NC5_FUEL_TEMP | 1
1 | BLR_4_CP_IC5_FUEL_TEMP | 1
1 | BLR_4_CP_FUEL_AT_REF_TEMP | 1
1 | BLR_4_CP_FUEL_AT_FUEL_TEMP | 1
1 | BLR_4_AVG_CP_FUEL_SENSIBLE | 1
1 | BLR_4_CP_AIR_AT_STACK_TEMP | 1
1 | BLR_4_CP_FLUE_CO2_AT_STACK | 1
1 | BLR_4_CP_FLUE_H2O_AT_STACK | 1
1 | BLR_4_CP_FLUE_N2_AT_STACK | 1
1 | BLR_4_AVG_CP_FLUE_AT_STACK | 1
1 | BLR_4_CP_H2O_AT_STACK | 1
1 | BLR_4_SH_CORRECTION_FUEL | 1
1 | BLR_4_SH_CORRECTION_AIR | 1
1 | BLR_4_MIXED_LHV_PER_KG | 1
1 | BLR_4_TOTAL_HEAT_INPUT | 1
1 | BLR_4_HEAT_LOSS_L1 | 1
1 | BLR_4_HEAT_LOSS_L2 | 1
1 | BLR_4_HEAT_LOSS_L3 | 1
1 | BLR_4_HEAT_LOSS_L4 | 1
1 | BLR_4_TOTAL_STACK_LOSS_PER_KG | 1
1 | BLR_4_RADIATION_LOSSES | 1
1 | BLR_4_TOTAL_HEAT_LOSS | 1
1 | BLR_4_TOTAL_HEAT_ABSORBED | 1
1 | BLR_4_INDIRECT_EFFICIENCY | 1
1 | BLR_4_HP_STEAM_ENTHALPY | 1
1 | BLR_4_TOTAL_STEAM_ENERGY | 1
1 | BLR_4_BFW_ENTHALPY | 1
1 | BLR_4_CORRECTED_BFW_FLOW | 1
1 | BLR_4_BFW_ENERGY | 1
1 | BLR_4_FUEL_GAS_ENERGY_INPUT | 1
1 | BLR_4_STEAM_DRUM_TEMP | 1
1 | BLR_4_BLOWDOWN_LOSS | 1
1 | BLR_4_TOTAL_FLUE_GAS_GENERATED | 1
1 | BLR_4_STACK_LOSS | 1
1 | BLR_4_CORRECTED_FUEL_FLOW | 1
1 | BLR_4_FUEL_CONSUMPTION_GCAL | 1
1 | BLR_4_SEC_GCAL_T | 1
1 | BLR_4_SEC_GJ_T | 1
1 | BLR_4_CORRECTED_FUEL_ENERGY_INPUT | 1
1 | BLR_4_THERMAL_EFFICIENCY | 1
1 | BLR_4_FUEL_GAS_CORRECTED_TPH | 1
1 | BLR_4_TOTAL_FLUE_GAS_CORRECTED | 1
1 | BLR_4_STACK_LOSS_CORRECTED | 1
1 | BLR_4_BFW_STEAM_RATIO | 1
1 | BLR_4_CO2_EMISSIONS | 1
1 | BLR_4_CALCULATED_AIRFLOW_NM3H | 1
1 | BLR_4_STEAM_TO_FIRE_RATIO | 1
1 | BLR_4_ECONOMIZER_DUTY | 1
1 | BLR_4_LMTD_ECONOMIZER | 1
1 | BLR_4_UA_ECONOMIZER | 1
1 | BLR_4_FOULING_INDEX | 1
1 | BLR_4_SH_DUTY | 1
1 | BLR_4_SH_SPECIFIC_DUTY | 1
1 | BLR_4_SH_PERFORMANCE | 1
1 | BLR_4_ENERGY_GAINED | 1
1 | BLR_4_CONVECTION_DUTY | 1
1 | BLR_4_RADIATION_DUTY | 1
1 | BLR_4_PCT_DUTY_CONVECTION | 1
1 | BLR_4_PCT_DUTY_RADIANT | 1
1 | BLR_4_DUTY_RATIO_RAD_CONV | 1
1 | BLR_4_RADIATION_SECTION_EFF | 1
1 | BLR_4_CONVECTION_SECTION_EFF | 1
1 | BLR_4_HPS_GEN | 1
1 | BLR_4_FUEL_FLOW | 1
1 | BLR_4_CAPACITY | 1
1 | BLR_4_SPEC_EN_CONS | 1
1 | BLR_4_SPEC_EN_CONS_OPT | 1
1 | BLR_4_SPEC_EN_CONS_DEV | 1
1 | BLR_4_HPS_GEN_WARMUP | 1
1 | BLR_4_FD_FAN_STEAM_REG | 1
1 | BLR_4_FD_FAN_STEAM_WARMUP | 1
1 | BLR_4_FD_FAN_STEAM | 1
1 | BLR_5_BOILER_LOAD | 1
1 | BLR_5_STATUS | 1
1 | BLR_5_FUEL_COMP_TOTAL | 1
1 | BLR_5_FG_NORM_CH4 | 1
1 | BLR_5_FG_NORM_ETHANE | 1
1 | BLR_5_FG_NORM_ETHYLENE | 1
1 | BLR_5_FG_NORM_PROPANE | 1
1 | BLR_5_FG_NORM_CO2 | 1
1 | BLR_5_FG_NORM_IC4 | 1
1 | BLR_5_FG_NORM_NC4 | 1
1 | BLR_5_FG_NORM_NC5 | 1
1 | BLR_5_FG_NORM_IC5 | 1
1 | BLR_5_FG_NORM_N2 | 1
1 | BLR_5_FG_NORM_H2 | 1
1 | BLR_5_FG_MW | 1
1 | BLR_5_FG_DENSITY | 1
1 | BLR_5_LHV_DESIGN | 1
1 | BLR_5_FG_CH4_MASS_PCT | 1
1 | BLR_5_FG_ETHANE_MASS_PCT | 1
1 | BLR_5_FG_ETHYLENE_MASS_PCT | 1
1 | BLR_5_FG_PROPANE_MASS_PCT | 1
1 | BLR_5_FG_N2_MASS_PCT | 1
1 | BLR_5_FG_H2_MASS_PCT | 1
1 | BLR_5_FG_IC4_MASS_PCT | 1
1 | BLR_5_FG_NC4_MASS_PCT | 1
1 | BLR_5_FG_NC5_MASS_PCT | 1
1 | BLR_5_FG_IC5_MASS_PCT | 1
1 | BLR_5_FG_CH4_MASS_FRAC | 1
1 | BLR_5_FG_ETHANE_MASS_FRAC | 1
1 | BLR_5_FG_ETHYLENE_MASS_FRAC | 1
1 | BLR_5_FG_PROPANE_MASS_FRAC | 1
1 | BLR_5_FG_N2_MASS_FRAC | 1
1 | BLR_5_FG_H2_MASS_FRAC | 1
1 | BLR_5_FG_IC4_MASS_FRAC | 1
1 | BLR_5_FG_NC4_MASS_FRAC | 1
1 | BLR_5_FG_NC5_MASS_FRAC | 1
1 | BLR_5_FG_IC5_MASS_FRAC | 1
1 | BLR_5_FG_FLOW_RATE_TPH | 1
1 | BLR_5_AIR_REQ_H2 | 1
1 | BLR_5_AIR_REQ_CH4 | 1
1 | BLR_5_AIR_REQ_ETHANE | 1
1 | BLR_5_AIR_REQ_ETHYLENE | 1
1 | BLR_5_AIR_REQ_PROPANE | 1
1 | BLR_5_AIR_REQ_NC4 | 1
1 | BLR_5_AIR_REQ_IC4 | 1
1 | BLR_5_AIR_REQ_NC5 | 1
1 | BLR_5_AIR_REQ_IC5 | 1
1 | BLR_5_CO2_COMB_H2 | 1
1 | BLR_5_CO2_COMB_CH4 | 1
1 | BLR_5_CO2_COMB_ETHANE | 1
1 | BLR_5_CO2_COMB_ETHYLENE | 1
1 | BLR_5_CO2_COMB_PROPANE | 1
1 | BLR_5_CO2_COMB_NC4 | 1
1 | BLR_5_CO2_COMB_IC4 | 1
1 | BLR_5_CO2_COMB_NC5 | 1
1 | BLR_5_CO2_COMB_IC5 | 1
1 | BLR_5_N2_COMB_H2 | 1
1 | BLR_5_N2_COMB_CH4 | 1
1 | BLR_5_N2_COMB_ETHANE | 1
1 | BLR_5_N2_COMB_ETHYLENE | 1
1 | BLR_5_N2_COMB_PROPANE | 1
1 | BLR_5_N2_COMB_IC4 | 1
1 | BLR_5_N2_COMB_NC4 | 1
1 | BLR_5_N2_COMB_IC5 | 1
1 | BLR_5_N2_COMB_NC5 | 1
1 | BLR_5_H2O_COMB_H2 | 1
1 | BLR_5_H2O_COMB_CH4 | 1
1 | BLR_5_H2O_COMB_ETHANE | 1
1 | BLR_5_H2O_COMB_ETHYLENE | 1
1 | BLR_5_H2O_COMB_PROPANE | 1
1 | BLR_5_H2O_COMB_IC4 | 1
1 | BLR_5_H2O_COMB_NC4 | 1
1 | BLR_5_H2O_COMB_IC5 | 1
1 | BLR_5_H2O_COMB_NC5 | 1
1 | BLR_5_AIR_REQ_COMPLETE | 1
1 | BLR_5_CO2_FORMED | 1
1 | BLR_5_N2_FORMED | 1
1 | BLR_5_H2O_FORMED | 1
1 | BLR_5_VAPOUR_PRESSURE_H2O | 1
1 | BLR_5_AIR_MOISTURE | 1
1 | BLR_5_CORRECTED_COMBUSTION_AIR | 1
1 | BLR_5_CORRECTED_H2O_FORMED | 1
1 | BLR_5_EXCESS_AIR | 1
1 | BLR_5_AIR_FUEL_MASS_RATIO | 1
1 | BLR_5_TOTAL_MOISTURE_WITH_AIR | 1
1 | BLR_5_TOTAL_H2O_PER_KG_FUEL | 1
1 | BLR_5_DRY_FLUE_GAS_RATIO | 1
1 | BLR_5_FLUE_GAS_RATIO | 1
1 | BLR_5_FLUE_GAS_MW | 1
1 | BLR_5_AIR_CP_REF_T | 1
1 | BLR_5_CP_AT_COMB_TEMP | 1
1 | BLR_5_AIR_CP_SENSIBLE_CORRECTED | 1
1 | BLR_5_CP_H2_FUEL_TEMP | 1
1 | BLR_5_CP_CH4_FUEL_TEMP | 1
1 | BLR_5_CP_ETHANE_FUEL_TEMP | 1
1 | BLR_5_CP_PROPANE_FUEL_TEMP | 1
1 | BLR_5_CP_ETHYLENE_FUEL_TEMP | 1
1 | BLR_5_CP_NC4_FUEL_TEMP | 1
1 | BLR_5_CP_IC4_FUEL_TEMP | 1
1 | BLR_5_CP_NC5_FUEL_TEMP | 1
1 | BLR_5_CP_IC5_FUEL_TEMP | 1
1 | BLR_5_CP_FUEL_AT_REF_TEMP | 1
1 | BLR_5_CP_FUEL_AT_FUEL_TEMP | 1
1 | BLR_5_AVG_CP_FUEL_SENSIBLE | 1
1 | BLR_5_CP_AIR_AT_STACK_TEMP | 1
1 | BLR_5_CP_FLUE_CO2_AT_STACK | 1
1 | BLR_5_CP_FLUE_H2O_AT_STACK | 1
1 | BLR_5_CP_FLUE_N2_AT_STACK | 1
1 | BLR_5_AVG_CP_FLUE_AT_STACK | 1
1 | BLR_5_CP_H2O_AT_STACK | 1
1 | BLR_5_SH_CORRECTION_FUEL | 1
1 | BLR_5_SH_CORRECTION_AIR | 1
1 | BLR_5_MIXED_LHV_PER_KG | 1
1 | BLR_5_TOTAL_HEAT_INPUT | 1
1 | BLR_5_HEAT_LOSS_L1 | 1
1 | BLR_5_HEAT_LOSS_L2 | 1
1 | BLR_5_HEAT_LOSS_L3 | 1
1 | BLR_5_HEAT_LOSS_L4 | 1
1 | BLR_5_TOTAL_STACK_LOSS_PER_KG | 1
1 | BLR_5_RADIATION_LOSSES | 1
1 | BLR_5_TOTAL_HEAT_LOSS | 1
1 | BLR_5_TOTAL_HEAT_ABSORBED | 1
1 | BLR_5_INDIRECT_EFFICIENCY | 1
1 | BLR_5_HP_STEAM_ENTHALPY | 1
1 | BLR_5_TOTAL_STEAM_ENERGY | 1
1 | BLR_5_BFW_ENTHALPY | 1
1 | BLR_5_CORRECTED_BFW_FLOW | 1
1 | BLR_5_BFW_ENERGY | 1
1 | BLR_5_FUEL_GAS_ENERGY_INPUT | 1
1 | BLR_5_STEAM_DRUM_TEMP | 1
1 | BLR_5_BLOWDOWN_LOSS | 1
1 | BLR_5_TOTAL_FLUE_GAS_GENERATED | 1
1 | BLR_5_STACK_LOSS | 1
1 | BLR_5_CORRECTED_FUEL_FLOW | 1
1 | BLR_5_FUEL_CONSUMPTION_GCAL | 1
1 | BLR_5_SEC_GCAL_T | 1
1 | BLR_5_SEC_GJ_T | 1
1 | BLR_5_CORRECTED_FUEL_ENERGY_INPUT | 1
1 | BLR_5_THERMAL_EFFICIENCY | 1
1 | BLR_5_FUEL_GAS_CORRECTED_TPH | 1
1 | BLR_5_TOTAL_FLUE_GAS_CORRECTED | 1
1 | BLR_5_STACK_LOSS_CORRECTED | 1
1 | BLR_5_BFW_STEAM_RATIO | 1
1 | BLR_5_CO2_EMISSIONS | 1
1 | BLR_5_CALCULATED_AIRFLOW_NM3H | 1
1 | BLR_5_STEAM_TO_FIRE_RATIO | 1
1 | BLR_5_ECONOMIZER_DUTY | 1
1 | BLR_5_LMTD_ECONOMIZER | 1
1 | BLR_5_UA_ECONOMIZER | 1
1 | BLR_5_FOULING_INDEX | 1
1 | BLR_5_SH_DUTY | 1
1 | BLR_5_SH_SPECIFIC_DUTY | 1
1 | BLR_5_SH_PERFORMANCE | 1
1 | BLR_5_ENERGY_GAINED | 1
1 | BLR_5_CONVECTION_DUTY | 1
1 | BLR_5_RADIATION_DUTY | 1
1 | BLR_5_PCT_DUTY_CONVECTION | 1
1 | BLR_5_PCT_DUTY_RADIANT | 1
1 | BLR_5_DUTY_RATIO_RAD_CONV | 1
1 | BLR_5_RADIATION_SECTION_EFF | 1
1 | BLR_5_CONVECTION_SECTION_EFF | 1
1 | BLR_5_HPS_GEN | 1
1 | BLR_5_FUEL_FLOW | 1
1 | BLR_5_CAPACITY | 1
1 | BLR_5_SPEC_EN_CONS | 1
1 | BLR_5_SPEC_EN_CONS_OPT | 1
1 | BLR_5_SPEC_EN_CONS_DEV | 1
1 | BLR_5_HPS_GEN_WARMUP | 1
1 | BLR_5_FD_FAN_STEAM_REG | 1
1 | BLR_5_FD_FAN_STEAM_WARMUP | 1
1 | BLR_5_FD_FAN_STEAM | 1