## Summary
Metric | Value
Hierarchy sensor IDs | 133
Hierarchy sensors with PEEO values | 12
Hierarchy sensors NOT in PEEO | 59
──────────────────────────────────────── | ─────
calc_blueprint.json — total outputs (18×5) | 90
calc_blueprint — COMPUTED | 5
calc_blueprint — NOT COMPUTED | 85
calc_blueprint — Coverage % | 5.6%
──────────────────────────────────────── | ─────
energy_kev boiler_template — total tags | 95
energy_kev — COMPUTED | 15
energy_kev — NOT COMPUTED | 80
energy_kev — Coverage % | 15.8%
──────────────────────────────────────── | ─────
BLOCKING — hps_gen_raw NOT in hierarchy | BLR_1–5_HPS_Gen_raw (master_pi_data name) ≠ hierarchy attr name
BLOCKING — fuel_flow_raw NOT in hierarchy | Fuel_BLR_n_raw = PEEO_CALC_OUTPUT, not a raw DCS sensor
BLOCKING — flue_o2_pct NOT in hierarchy | 5 sensors known but not added to hierarchy yet
BLOCKING — LHV not configured | No LHV constant in system_config or instantiated_attributes

## Calc_Blueprint_90_out
boiler | attribute | formula | status | value | missing_inputs | note
BLR_1 | BOILER_LOAD | STEAM_FLOW_RAW / RATED_STEAM_KGH * 100 | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_1 | HPS_GEN | if(STEAM_FLOW_RAW < 0, 0, STEAM_FLOW_RAW / 1000) | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_1 | STATUS | if((BOILER_LOAD > MIN_LOAD_PCT) && (DESUPERHEATER_OUTLET_TEMP > STEAM_TEMP_ON_THRESH) && (HP_STEAM_PRESSURE > STEAM_PRESS_ON_THRESH), 1, 0) | NOT COMPUTED |  | HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP | Missing: HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP
BLR_1 | FUEL_FLOW | FUEL_GAS_FLOW * STATUS / 1000 | NOT COMPUTED |  | FUEL_GAS_FLOW | Missing: FUEL_GAS_FLOW
BLR_1 | CAPACITY | CAPACITY_T_H | COMPUTED | 150
BLR_1 | SPEC_EN_CONS | if(HPS_GEN == 0, 0, FUEL_FLOW * plant.BOILER_LHV / HPS_GEN) | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_1 | SPEC_EN_CONS_OPT | (SEC_OPT_A * HPS_GEN ** 2 + SEC_OPT_B * HPS_GEN + SEC_OPT_C) * STATUS | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | SPEC_EN_CONS_DEV | if(STATUS == 0, 0, (SPEC_EN_CONS_OPT - SPEC_EN_CONS) / SPEC_EN_CONS_OPT) | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | HPS_GEN_WARMUP | if(STATUS == 0, HPS_GEN, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | FD_FAN_STEAM | if(FD_FAN_STEAM_RAW < FD_FAN_NOISE_KGH, 0, FD_FAN_STEAM_RAW / 1000) | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | FD_FAN_STEAM_REG | (FD_FAN_C0 + FD_FAN_C1 * HPS_GEN + FD_FAN_C2 * HPS_GEN ** 2) / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | FD_FAN_STEAM_WARMUP | if((FD_FAN_STEAM_RAW > 100) && (FD_FAN_STEAM_RAW < FD_FAN_MAX_KGH) && (STATUS == 0), FD_FAN_STEAM_RAW / 1000, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | STACK_TEMP_REG | STACK_TEMP_A * HPS_GEN + STACK_TEMP_B * FLUE_GAS_OXYGEN + STACK_TEMP_C | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | STACK_TEMP_CLIPPED | if((FLUE_GAS_OXYGEN == 0) ¦¦ (STACK_TEMPERATURE == 0), STACK_TEMPERATURE, min(STACK_TEMPERATURE, STACK_TEMP_REG) * STATUS) | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | FUEL_INPUT_GJ_H | FUEL_FLOW * plant.BOILER_LHV * 4.184 / 1000 | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_1 | USEFUL_HEAT_GJ_H | HPS_GEN * 2.8 | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | EFFICIENCY_PCT | if(FUEL_INPUT_GJ_H == 0, 0, USEFUL_HEAT_GJ_H / FUEL_INPUT_GJ_H * 100) | NOT COMPUTED |  |  | eval failed / NaN
BLR_1 | CO2_T_PER_H | FUEL_INPUT_GJ_H * CO2_KG_PER_GJ / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | BOILER_LOAD | STEAM_FLOW_RAW / RATED_STEAM_KGH * 100 | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_2 | HPS_GEN | if(STEAM_FLOW_RAW < 0, 0, STEAM_FLOW_RAW / 1000) | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_2 | STATUS | if((BOILER_LOAD > MIN_LOAD_PCT) && (DESUPERHEATER_OUTLET_TEMP > STEAM_TEMP_ON_THRESH) && (HP_STEAM_PRESSURE > STEAM_PRESS_ON_THRESH), 1, 0) | NOT COMPUTED |  | HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP | Missing: HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP
BLR_2 | FUEL_FLOW | FUEL_GAS_FLOW * STATUS / 1000 | NOT COMPUTED |  | FUEL_GAS_FLOW | Missing: FUEL_GAS_FLOW
BLR_2 | CAPACITY | CAPACITY_T_H | COMPUTED | 150
BLR_2 | SPEC_EN_CONS | if(HPS_GEN == 0, 0, FUEL_FLOW * plant.BOILER_LHV / HPS_GEN) | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_2 | SPEC_EN_CONS_OPT | (SEC_OPT_A * HPS_GEN ** 2 + SEC_OPT_B * HPS_GEN + SEC_OPT_C) * STATUS | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | SPEC_EN_CONS_DEV | if(STATUS == 0, 0, (SPEC_EN_CONS_OPT - SPEC_EN_CONS) / SPEC_EN_CONS_OPT) | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | HPS_GEN_WARMUP | if(STATUS == 0, HPS_GEN, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | FD_FAN_STEAM | if(FD_FAN_STEAM_RAW < FD_FAN_NOISE_KGH, 0, FD_FAN_STEAM_RAW / 1000) | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | FD_FAN_STEAM_REG | (FD_FAN_C0 + FD_FAN_C1 * HPS_GEN + FD_FAN_C2 * HPS_GEN ** 2) / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | FD_FAN_STEAM_WARMUP | if((FD_FAN_STEAM_RAW > 100) && (FD_FAN_STEAM_RAW < FD_FAN_MAX_KGH) && (STATUS == 0), FD_FAN_STEAM_RAW / 1000, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | STACK_TEMP_REG | STACK_TEMP_A * HPS_GEN + STACK_TEMP_B * FLUE_GAS_OXYGEN + STACK_TEMP_C | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | STACK_TEMP_CLIPPED | if((FLUE_GAS_OXYGEN == 0) ¦¦ (STACK_TEMPERATURE == 0), STACK_TEMPERATURE, min(STACK_TEMPERATURE, STACK_TEMP_REG) * STATUS) | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | FUEL_INPUT_GJ_H | FUEL_FLOW * plant.BOILER_LHV * 4.184 / 1000 | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_2 | USEFUL_HEAT_GJ_H | HPS_GEN * 2.8 | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | EFFICIENCY_PCT | if(FUEL_INPUT_GJ_H == 0, 0, USEFUL_HEAT_GJ_H / FUEL_INPUT_GJ_H * 100) | NOT COMPUTED |  |  | eval failed / NaN
BLR_2 | CO2_T_PER_H | FUEL_INPUT_GJ_H * CO2_KG_PER_GJ / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | BOILER_LOAD | STEAM_FLOW_RAW / RATED_STEAM_KGH * 100 | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_3 | HPS_GEN | if(STEAM_FLOW_RAW < 0, 0, STEAM_FLOW_RAW / 1000) | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_3 | STATUS | if((BOILER_LOAD > MIN_LOAD_PCT) && (DESUPERHEATER_OUTLET_TEMP > STEAM_TEMP_ON_THRESH) && (HP_STEAM_PRESSURE > STEAM_PRESS_ON_THRESH), 1, 0) | NOT COMPUTED |  | HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP | Missing: HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP
BLR_3 | FUEL_FLOW | FUEL_GAS_FLOW * STATUS / 1000 | NOT COMPUTED |  | FUEL_GAS_FLOW | Missing: FUEL_GAS_FLOW
BLR_3 | CAPACITY | CAPACITY_T_H | COMPUTED | 150
BLR_3 | SPEC_EN_CONS | if(HPS_GEN == 0, 0, FUEL_FLOW * plant.BOILER_LHV / HPS_GEN) | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_3 | SPEC_EN_CONS_OPT | (SEC_OPT_A * HPS_GEN ** 2 + SEC_OPT_B * HPS_GEN + SEC_OPT_C) * STATUS | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | SPEC_EN_CONS_DEV | if(STATUS == 0, 0, (SPEC_EN_CONS_OPT - SPEC_EN_CONS) / SPEC_EN_CONS_OPT) | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | HPS_GEN_WARMUP | if(STATUS == 0, HPS_GEN, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | FD_FAN_STEAM | if(FD_FAN_STEAM_RAW < FD_FAN_NOISE_KGH, 0, FD_FAN_STEAM_RAW / 1000) | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | FD_FAN_STEAM_REG | (FD_FAN_C0 + FD_FAN_C1 * HPS_GEN + FD_FAN_C2 * HPS_GEN ** 2) / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | FD_FAN_STEAM_WARMUP | if((FD_FAN_STEAM_RAW > 100) && (FD_FAN_STEAM_RAW < FD_FAN_MAX_KGH) && (STATUS == 0), FD_FAN_STEAM_RAW / 1000, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | STACK_TEMP_REG | STACK_TEMP_A * HPS_GEN + STACK_TEMP_B * FLUE_GAS_OXYGEN + STACK_TEMP_C | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | STACK_TEMP_CLIPPED | if((FLUE_GAS_OXYGEN == 0) ¦¦ (STACK_TEMPERATURE == 0), STACK_TEMPERATURE, min(STACK_TEMPERATURE, STACK_TEMP_REG) * STATUS) | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | FUEL_INPUT_GJ_H | FUEL_FLOW * plant.BOILER_LHV * 4.184 / 1000 | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_3 | USEFUL_HEAT_GJ_H | HPS_GEN * 2.8 | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | EFFICIENCY_PCT | if(FUEL_INPUT_GJ_H == 0, 0, USEFUL_HEAT_GJ_H / FUEL_INPUT_GJ_H * 100) | NOT COMPUTED |  |  | eval failed / NaN
BLR_3 | CO2_T_PER_H | FUEL_INPUT_GJ_H * CO2_KG_PER_GJ / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | BOILER_LOAD | STEAM_FLOW_RAW / RATED_STEAM_KGH * 100 | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_4 | HPS_GEN | if(STEAM_FLOW_RAW < 0, 0, STEAM_FLOW_RAW / 1000) | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_4 | STATUS | if((BOILER_LOAD > MIN_LOAD_PCT) && (DESUPERHEATER_OUTLET_TEMP > STEAM_TEMP_ON_THRESH) && (HP_STEAM_PRESSURE > STEAM_PRESS_ON_THRESH), 1, 0) | NOT COMPUTED |  | HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP | Missing: HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP
BLR_4 | FUEL_FLOW | FUEL_GAS_FLOW * STATUS / 1000 | NOT COMPUTED |  | FUEL_GAS_FLOW | Missing: FUEL_GAS_FLOW
BLR_4 | CAPACITY | CAPACITY_T_H | COMPUTED | 150
BLR_4 | SPEC_EN_CONS | if(HPS_GEN == 0, 0, FUEL_FLOW * plant.BOILER_LHV / HPS_GEN) | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_4 | SPEC_EN_CONS_OPT | (SEC_OPT_A * HPS_GEN ** 2 + SEC_OPT_B * HPS_GEN + SEC_OPT_C) * STATUS | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | SPEC_EN_CONS_DEV | if(STATUS == 0, 0, (SPEC_EN_CONS_OPT - SPEC_EN_CONS) / SPEC_EN_CONS_OPT) | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | HPS_GEN_WARMUP | if(STATUS == 0, HPS_GEN, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | FD_FAN_STEAM | if(FD_FAN_STEAM_RAW < FD_FAN_NOISE_KGH, 0, FD_FAN_STEAM_RAW / 1000) | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | FD_FAN_STEAM_REG | (FD_FAN_C0 + FD_FAN_C1 * HPS_GEN + FD_FAN_C2 * HPS_GEN ** 2) / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | FD_FAN_STEAM_WARMUP | if((FD_FAN_STEAM_RAW > 100) && (FD_FAN_STEAM_RAW < FD_FAN_MAX_KGH) && (STATUS == 0), FD_FAN_STEAM_RAW / 1000, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | STACK_TEMP_REG | STACK_TEMP_A * HPS_GEN + STACK_TEMP_B * FLUE_GAS_OXYGEN + STACK_TEMP_C | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | STACK_TEMP_CLIPPED | if((FLUE_GAS_OXYGEN == 0) ¦¦ (STACK_TEMPERATURE == 0), STACK_TEMPERATURE, min(STACK_TEMPERATURE, STACK_TEMP_REG) * STATUS) | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | FUEL_INPUT_GJ_H | FUEL_FLOW * plant.BOILER_LHV * 4.184 / 1000 | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_4 | USEFUL_HEAT_GJ_H | HPS_GEN * 2.8 | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | EFFICIENCY_PCT | if(FUEL_INPUT_GJ_H == 0, 0, USEFUL_HEAT_GJ_H / FUEL_INPUT_GJ_H * 100) | NOT COMPUTED |  |  | eval failed / NaN
BLR_4 | CO2_T_PER_H | FUEL_INPUT_GJ_H * CO2_KG_PER_GJ / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | BOILER_LOAD | STEAM_FLOW_RAW / RATED_STEAM_KGH * 100 | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_5 | HPS_GEN | if(STEAM_FLOW_RAW < 0, 0, STEAM_FLOW_RAW / 1000) | NOT COMPUTED |  | STEAM_FLOW_RAW | Missing: STEAM_FLOW_RAW
BLR_5 | STATUS | if((BOILER_LOAD > MIN_LOAD_PCT) && (DESUPERHEATER_OUTLET_TEMP > STEAM_TEMP_ON_THRESH) && (HP_STEAM_PRESSURE > STEAM_PRESS_ON_THRESH), 1, 0) | NOT COMPUTED |  | HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP | Missing: HP_STEAM_PRESSURE, DESUPERHEATER_OUTLET_TEMP
BLR_5 | FUEL_FLOW | FUEL_GAS_FLOW * STATUS / 1000 | NOT COMPUTED |  | FUEL_GAS_FLOW | Missing: FUEL_GAS_FLOW
BLR_5 | CAPACITY | CAPACITY_T_H | COMPUTED | 150
BLR_5 | SPEC_EN_CONS | if(HPS_GEN == 0, 0, FUEL_FLOW * plant.BOILER_LHV / HPS_GEN) | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_5 | SPEC_EN_CONS_OPT | (SEC_OPT_A * HPS_GEN ** 2 + SEC_OPT_B * HPS_GEN + SEC_OPT_C) * STATUS | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | SPEC_EN_CONS_DEV | if(STATUS == 0, 0, (SPEC_EN_CONS_OPT - SPEC_EN_CONS) / SPEC_EN_CONS_OPT) | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | HPS_GEN_WARMUP | if(STATUS == 0, HPS_GEN, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | FD_FAN_STEAM | if(FD_FAN_STEAM_RAW < FD_FAN_NOISE_KGH, 0, FD_FAN_STEAM_RAW / 1000) | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | FD_FAN_STEAM_REG | (FD_FAN_C0 + FD_FAN_C1 * HPS_GEN + FD_FAN_C2 * HPS_GEN ** 2) / 1000 | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | FD_FAN_STEAM_WARMUP | if((FD_FAN_STEAM_RAW > 100) && (FD_FAN_STEAM_RAW < FD_FAN_MAX_KGH) && (STATUS == 0), FD_FAN_STEAM_RAW / 1000, 0) | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | STACK_TEMP_REG | STACK_TEMP_A * HPS_GEN + STACK_TEMP_B * FLUE_GAS_OXYGEN + STACK_TEMP_C | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | STACK_TEMP_CLIPPED | if((FLUE_GAS_OXYGEN == 0) ¦¦ (STACK_TEMPERATURE == 0), STACK_TEMPERATURE, min(STACK_TEMPERATURE, STACK_TEMP_REG) * STATUS) | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | FUEL_INPUT_GJ_H | FUEL_FLOW * plant.BOILER_LHV * 4.184 / 1000 | NOT COMPUTED |  | BOILER_LHV | Missing: BOILER_LHV
BLR_5 | USEFUL_HEAT_GJ_H | HPS_GEN * 2.8 | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | EFFICIENCY_PCT | if(FUEL_INPUT_GJ_H == 0, 0, USEFUL_HEAT_GJ_H / FUEL_INPUT_GJ_H * 100) | NOT COMPUTED |  |  | eval failed / NaN
BLR_5 | CO2_T_PER_H | FUEL_INPUT_GJ_H * CO2_KG_PER_GJ / 1000 | NOT COMPUTED |  |  | eval failed / NaN

## KEV_Template_Tags
boiler | tag | type | status | requires | missing
BLR_1 | BLR_1_HPS_Gen | core (always emitted) | NOT COMPUTED | raw→t/hr conversion | hps_gen_raw
BLR_1 | BLR_1_Status | core (always emitted) | NOT COMPUTED | if(HPS_Gen>=50,1,0) | hps_gen_raw
BLR_1 | BLR_1_Fuel_Flow | core (always emitted) | NOT COMPUTED | fuel_raw*Status/1000 | fuel_flow_raw
BLR_1 | BLR_1_Capacity | core (always emitted) | COMPUTED | constant 140 t/h
BLR_1 | BLR_1_Spec_En_Cons | core (always emitted) | NOT COMPUTED | if(HPS_Gen==0,0,Fuel*LHV/HPS) | LHV missing
BLR_1 | BLR_1_HPS_Gen_warmup | core (always emitted) | NOT COMPUTED | if(Status==0,HPS_Gen,0) | hps_gen_raw
BLR_1 | BLR_1_useful_heat_gj_h | core (always emitted) | NOT COMPUTED | HPS_Gen*2.7 | hps_gen_raw
BLR_1 | BLR_1_fuel_input_gj_h | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV | LHV missing
BLR_1 | BLR_1_efficiency_pct | core (always emitted) | NOT COMPUTED | useful_heat/fuel_input*100 | LHV missing
BLR_1 | BLR_1_sec_gj_per_t_steam | core (always emitted) | NOT COMPUTED | fuel_input/HPS_Gen | LHV missing
BLR_1 | BLR_1_co2_t_per_h | core (always emitted) | NOT COMPUTED | fuel_input*56.1/1000 | LHV missing
BLR_1 | BLR_1_fuel_cost_per_hr | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV*cost | LHV missing
BLR_1 | BLR_1_FD_Fan_Steam_reg | optional (PI-dependent) | NOT COMPUTED | curve(HPS_Gen) | fd_fan_steam_raw not in hierarchy
BLR_1 | BLR_1_FD_Fan_Steam_warmup | optional (PI-dependent) | NOT COMPUTED | if(raw>100&&Status==0,...) | fd_fan_steam_raw not in hierarchy
BLR_1 | BLR_1_FD_Fan_Steam | optional (PI-dependent) | NOT COMPUTED | noise-clip passthrough | fd_fan_steam_raw not in hierarchy
BLR_1 | BLR_1_excess_air_pct | optional (PI-dependent) | COMPUTED | O2/(21-O2)*100
BLR_1 | BLR_1_stack_loss_pct | optional (PI-dependent) | NOT COMPUTED | Siegert formula | flue_o2_pct not in hierarchy
BLR_1 | BLR_1_indirect_efficiency_pct | optional (PI-dependent) | NOT COMPUTED | 100-stack_loss-1% | flue_o2_pct not in hierarchy
BLR_1 | BLR_1_stack_temp_c_clipped | optional (PI-dependent) | COMPUTED | min(actual,regression)*S
BLR_2 | BLR_2_HPS_Gen | core (always emitted) | NOT COMPUTED | raw→t/hr conversion | hps_gen_raw
BLR_2 | BLR_2_Status | core (always emitted) | NOT COMPUTED | if(HPS_Gen>=50,1,0) | hps_gen_raw
BLR_2 | BLR_2_Fuel_Flow | core (always emitted) | NOT COMPUTED | fuel_raw*Status/1000 | fuel_flow_raw
BLR_2 | BLR_2_Capacity | core (always emitted) | COMPUTED | constant 140 t/h
BLR_2 | BLR_2_Spec_En_Cons | core (always emitted) | NOT COMPUTED | if(HPS_Gen==0,0,Fuel*LHV/HPS) | LHV missing
BLR_2 | BLR_2_HPS_Gen_warmup | core (always emitted) | NOT COMPUTED | if(Status==0,HPS_Gen,0) | hps_gen_raw
BLR_2 | BLR_2_useful_heat_gj_h | core (always emitted) | NOT COMPUTED | HPS_Gen*2.7 | hps_gen_raw
BLR_2 | BLR_2_fuel_input_gj_h | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV | LHV missing
BLR_2 | BLR_2_efficiency_pct | core (always emitted) | NOT COMPUTED | useful_heat/fuel_input*100 | LHV missing
BLR_2 | BLR_2_sec_gj_per_t_steam | core (always emitted) | NOT COMPUTED | fuel_input/HPS_Gen | LHV missing
BLR_2 | BLR_2_co2_t_per_h | core (always emitted) | NOT COMPUTED | fuel_input*56.1/1000 | LHV missing
BLR_2 | BLR_2_fuel_cost_per_hr | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV*cost | LHV missing
BLR_2 | BLR_2_FD_Fan_Steam_reg | optional (PI-dependent) | NOT COMPUTED | curve(HPS_Gen) | fd_fan_steam_raw not in hierarchy
BLR_2 | BLR_2_FD_Fan_Steam_warmup | optional (PI-dependent) | NOT COMPUTED | if(raw>100&&Status==0,...) | fd_fan_steam_raw not in hierarchy
BLR_2 | BLR_2_FD_Fan_Steam | optional (PI-dependent) | NOT COMPUTED | noise-clip passthrough | fd_fan_steam_raw not in hierarchy
BLR_2 | BLR_2_excess_air_pct | optional (PI-dependent) | COMPUTED | O2/(21-O2)*100
BLR_2 | BLR_2_stack_loss_pct | optional (PI-dependent) | NOT COMPUTED | Siegert formula | flue_o2_pct not in hierarchy
BLR_2 | BLR_2_indirect_efficiency_pct | optional (PI-dependent) | NOT COMPUTED | 100-stack_loss-1% | flue_o2_pct not in hierarchy
BLR_2 | BLR_2_stack_temp_c_clipped | optional (PI-dependent) | COMPUTED | min(actual,regression)*S
BLR_3 | BLR_3_HPS_Gen | core (always emitted) | NOT COMPUTED | raw→t/hr conversion | hps_gen_raw
BLR_3 | BLR_3_Status | core (always emitted) | NOT COMPUTED | if(HPS_Gen>=50,1,0) | hps_gen_raw
BLR_3 | BLR_3_Fuel_Flow | core (always emitted) | NOT COMPUTED | fuel_raw*Status/1000 | fuel_flow_raw
BLR_3 | BLR_3_Capacity | core (always emitted) | COMPUTED | constant 140 t/h
BLR_3 | BLR_3_Spec_En_Cons | core (always emitted) | NOT COMPUTED | if(HPS_Gen==0,0,Fuel*LHV/HPS) | LHV missing
BLR_3 | BLR_3_HPS_Gen_warmup | core (always emitted) | NOT COMPUTED | if(Status==0,HPS_Gen,0) | hps_gen_raw
BLR_3 | BLR_3_useful_heat_gj_h | core (always emitted) | NOT COMPUTED | HPS_Gen*2.7 | hps_gen_raw
BLR_3 | BLR_3_fuel_input_gj_h | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV | LHV missing
BLR_3 | BLR_3_efficiency_pct | core (always emitted) | NOT COMPUTED | useful_heat/fuel_input*100 | LHV missing
BLR_3 | BLR_3_sec_gj_per_t_steam | core (always emitted) | NOT COMPUTED | fuel_input/HPS_Gen | LHV missing
BLR_3 | BLR_3_co2_t_per_h | core (always emitted) | NOT COMPUTED | fuel_input*56.1/1000 | LHV missing
BLR_3 | BLR_3_fuel_cost_per_hr | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV*cost | LHV missing
BLR_3 | BLR_3_FD_Fan_Steam_reg | optional (PI-dependent) | NOT COMPUTED | curve(HPS_Gen) | fd_fan_steam_raw not in hierarchy
BLR_3 | BLR_3_FD_Fan_Steam_warmup | optional (PI-dependent) | NOT COMPUTED | if(raw>100&&Status==0,...) | fd_fan_steam_raw not in hierarchy
BLR_3 | BLR_3_FD_Fan_Steam | optional (PI-dependent) | NOT COMPUTED | noise-clip passthrough | fd_fan_steam_raw not in hierarchy
BLR_3 | BLR_3_excess_air_pct | optional (PI-dependent) | COMPUTED | O2/(21-O2)*100
BLR_3 | BLR_3_stack_loss_pct | optional (PI-dependent) | NOT COMPUTED | Siegert formula | flue_o2_pct not in hierarchy
BLR_3 | BLR_3_indirect_efficiency_pct | optional (PI-dependent) | NOT COMPUTED | 100-stack_loss-1% | flue_o2_pct not in hierarchy
BLR_3 | BLR_3_stack_temp_c_clipped | optional (PI-dependent) | COMPUTED | min(actual,regression)*S
BLR_4 | BLR_4_HPS_Gen | core (always emitted) | NOT COMPUTED | raw→t/hr conversion | hps_gen_raw
BLR_4 | BLR_4_Status | core (always emitted) | NOT COMPUTED | if(HPS_Gen>=50,1,0) | hps_gen_raw
BLR_4 | BLR_4_Fuel_Flow | core (always emitted) | NOT COMPUTED | fuel_raw*Status/1000 | fuel_flow_raw
BLR_4 | BLR_4_Capacity | core (always emitted) | COMPUTED | constant 140 t/h
BLR_4 | BLR_4_Spec_En_Cons | core (always emitted) | NOT COMPUTED | if(HPS_Gen==0,0,Fuel*LHV/HPS) | LHV missing
BLR_4 | BLR_4_HPS_Gen_warmup | core (always emitted) | NOT COMPUTED | if(Status==0,HPS_Gen,0) | hps_gen_raw
BLR_4 | BLR_4_useful_heat_gj_h | core (always emitted) | NOT COMPUTED | HPS_Gen*2.7 | hps_gen_raw
BLR_4 | BLR_4_fuel_input_gj_h | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV | LHV missing
BLR_4 | BLR_4_efficiency_pct | core (always emitted) | NOT COMPUTED | useful_heat/fuel_input*100 | LHV missing
BLR_4 | BLR_4_sec_gj_per_t_steam | core (always emitted) | NOT COMPUTED | fuel_input/HPS_Gen | LHV missing
BLR_4 | BLR_4_co2_t_per_h | core (always emitted) | NOT COMPUTED | fuel_input*56.1/1000 | LHV missing
BLR_4 | BLR_4_fuel_cost_per_hr | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV*cost | LHV missing
BLR_4 | BLR_4_FD_Fan_Steam_reg | optional (PI-dependent) | NOT COMPUTED | curve(HPS_Gen) | fd_fan_steam_raw not in hierarchy
BLR_4 | BLR_4_FD_Fan_Steam_warmup | optional (PI-dependent) | NOT COMPUTED | if(raw>100&&Status==0,...) | fd_fan_steam_raw not in hierarchy
BLR_4 | BLR_4_FD_Fan_Steam | optional (PI-dependent) | NOT COMPUTED | noise-clip passthrough | fd_fan_steam_raw not in hierarchy
BLR_4 | BLR_4_excess_air_pct | optional (PI-dependent) | COMPUTED | O2/(21-O2)*100
BLR_4 | BLR_4_stack_loss_pct | optional (PI-dependent) | NOT COMPUTED | Siegert formula | flue_o2_pct not in hierarchy
BLR_4 | BLR_4_indirect_efficiency_pct | optional (PI-dependent) | NOT COMPUTED | 100-stack_loss-1% | flue_o2_pct not in hierarchy
BLR_4 | BLR_4_stack_temp_c_clipped | optional (PI-dependent) | COMPUTED | min(actual,regression)*S
BLR_5 | BLR_5_HPS_Gen | core (always emitted) | NOT COMPUTED | raw→t/hr conversion | hps_gen_raw
BLR_5 | BLR_5_Status | core (always emitted) | NOT COMPUTED | if(HPS_Gen>=50,1,0) | hps_gen_raw
BLR_5 | BLR_5_Fuel_Flow | core (always emitted) | NOT COMPUTED | fuel_raw*Status/1000 | fuel_flow_raw
BLR_5 | BLR_5_Capacity | core (always emitted) | COMPUTED | constant 140 t/h
BLR_5 | BLR_5_Spec_En_Cons | core (always emitted) | NOT COMPUTED | if(HPS_Gen==0,0,Fuel*LHV/HPS) | LHV missing
BLR_5 | BLR_5_HPS_Gen_warmup | core (always emitted) | NOT COMPUTED | if(Status==0,HPS_Gen,0) | hps_gen_raw
BLR_5 | BLR_5_useful_heat_gj_h | core (always emitted) | NOT COMPUTED | HPS_Gen*2.7 | hps_gen_raw
BLR_5 | BLR_5_fuel_input_gj_h | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV | LHV missing
BLR_5 | BLR_5_efficiency_pct | core (always emitted) | NOT COMPUTED | useful_heat/fuel_input*100 | LHV missing
BLR_5 | BLR_5_sec_gj_per_t_steam | core (always emitted) | NOT COMPUTED | fuel_input/HPS_Gen | LHV missing
BLR_5 | BLR_5_co2_t_per_h | core (always emitted) | NOT COMPUTED | fuel_input*56.1/1000 | LHV missing
BLR_5 | BLR_5_fuel_cost_per_hr | core (always emitted) | NOT COMPUTED | Fuel_Flow*LHV*cost | LHV missing
BLR_5 | BLR_5_FD_Fan_Steam_reg | optional (PI-dependent) | NOT COMPUTED | curve(HPS_Gen) | fd_fan_steam_raw not in hierarchy
BLR_5 | BLR_5_FD_Fan_Steam_warmup | optional (PI-dependent) | NOT COMPUTED | if(raw>100&&Status==0,...) | fd_fan_steam_raw not in hierarchy
BLR_5 | BLR_5_FD_Fan_Steam | optional (PI-dependent) | NOT COMPUTED | noise-clip passthrough | fd_fan_steam_raw not in hierarchy
BLR_5 | BLR_5_excess_air_pct | optional (PI-dependent) | COMPUTED | O2/(21-O2)*100
BLR_5 | BLR_5_stack_loss_pct | optional (PI-dependent) | NOT COMPUTED | Siegert formula | flue_o2_pct not in hierarchy
BLR_5 | BLR_5_indirect_efficiency_pct | optional (PI-dependent) | NOT COMPUTED | 100-stack_loss-1% | flue_o2_pct not in hierarchy
BLR_5 | BLR_5_stack_temp_c_clipped | optional (PI-dependent) | COMPUTED | min(actual,regression)*S

## Sensor_Coverage
scope | attribute | sensor_name | sensor_id | in_hierarchy | has_value | value
plant | AMBIENT_TEMP | Ambient_Temperature_1 | NOT_IN_PEEO | NO | NO
plant | RELATIVE_HUMIDITY | Relative_Humidity_Clean | NOT_IN_PEEO | NO | NO
plant | BOILER_LHV | LHV_Raw | NOT_IN_PEEO | NO | NO
plant | BFW_PRESSURE | BFW_Pressure | NOT_IN_PEEO | NO | NO
plant | FG_CH4 | BOILER_FG_CH4_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51211.PV | YES | YES | 3.788
plant | FG_ETHANE | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51212.PV | YES | YES | 0.062
BLR_1 | STEAM_FLOW_RAW | BLR_1_HPS_Gen_raw | NOT_IN_PEEO | NO | NO
BLR_1 | FUEL_GAS_FLOW | Fuel_BLR_1_raw | NOT_IN_PEEO | NO | NO
BLR_1 | FD_FAN_STEAM_RAW | FD_Fan_BLR_1_Steam_raw | NOT_IN_PEEO | NO | NO
BLR_1 | BFW_TO_ECONOMIZER | BFW_TO_BOILER_A | NOT_IN_PEEO | NO | NO
BLR_1 | BFW_TO_DESUPERHEATER | DSP_BFW_TO_BOILER_A | NOT_IN_PEEO | NO | NO
BLR_1 | STACK_TEMPERATURE | BOILER_A_STACK_TEMPERATURE | UN.UO.71TI1107.PV | YES | YES | 5.907
BLR_1 | COMBUSTION_AIR_TEMP | Boiler_A_Combustion_Air_Temperature | NOT_IN_PEEO | NO | NO
BLR_1 | FUEL_GAS_TEMP | Boiler_A_Main_Fuel_Gas_Temperature | NOT_IN_PEEO | NO | NO
BLR_1 | FLUE_GAS_OXYGEN | BOILER_A_FLUE_GAS_OXGYGEN | UN.UO.71AC1104.PV | NO | YES | 0.149
BLR_1 | CBD_BLOWDOWN | BOILER_A_CBD | NOT_IN_PEEO | NO | NO
BLR_1 | DESUPERHEATER_OUTLET_TEMP | Boiler_A_DSP_outlet_Temp | NOT_IN_PEEO | NO | NO
BLR_1 | HP_STEAM_PRESSURE | Boiler_A_DSP_outlet_Pressure | NOT_IN_PEEO | NO | NO
BLR_2 | STEAM_FLOW_RAW | BLR_2_HPS_Gen_raw | NOT_IN_PEEO | NO | NO
BLR_2 | FUEL_GAS_FLOW | Fuel_BLR_2_raw | NOT_IN_PEEO | NO | NO
BLR_2 | FD_FAN_STEAM_RAW | FD_Fan_BLR_2_Steam_raw | NOT_IN_PEEO | NO | NO
BLR_2 | BFW_TO_ECONOMIZER | BFW_TO_BOILER_B | NOT_IN_PEEO | NO | NO
BLR_2 | BFW_TO_DESUPERHEATER | DSP_BFW_TO_BOILER_B | NOT_IN_PEEO | NO | NO
BLR_2 | STACK_TEMPERATURE | BOILER_B_STACK_TEMPERATURE | UN.UO.71TI1207.PV | YES | YES | 5.891
BLR_2 | COMBUSTION_AIR_TEMP | Boiler_B_Combustion_Air_Temperature | NOT_IN_PEEO | NO | NO
BLR_2 | FUEL_GAS_TEMP | Boiler_B_Main_Fuel_Gas_Temperature | NOT_IN_PEEO | NO | NO
BLR_2 | FLUE_GAS_OXYGEN | BOILER_B_FLUE_GAS_OXGYGEN | UN.UO.71AC1204.PV | NO | YES | 0.147
BLR_2 | CBD_BLOWDOWN | BOILER_B_CBD | NOT_IN_PEEO | NO | NO
BLR_2 | DESUPERHEATER_OUTLET_TEMP | Boiler_B_DSP_outlet_Temp | NOT_IN_PEEO | NO | NO
BLR_2 | HP_STEAM_PRESSURE | Boiler_B_DSP_outlet_Pressure | NOT_IN_PEEO | NO | NO
BLR_3 | STEAM_FLOW_RAW | BLR_3_HPS_Gen_raw | NOT_IN_PEEO | NO | NO
BLR_3 | FUEL_GAS_FLOW | Fuel_BLR_3_raw | NOT_IN_PEEO | NO | NO
BLR_3 | FD_FAN_STEAM_RAW | FD_Fan_BLR_3_Steam_raw | NOT_IN_PEEO | NO | NO
BLR_3 | BFW_TO_ECONOMIZER | BFW_TO_BOILER_C | NOT_IN_PEEO | NO | NO
BLR_3 | BFW_TO_DESUPERHEATER | DSP_BFW_TO_BOILER_C | NOT_IN_PEEO | NO | NO
BLR_3 | STACK_TEMPERATURE | BOILER_C_STACK_TEMPERATURE | UN.UO.71TI1307.PV | YES | YES | 5.934
BLR_3 | COMBUSTION_AIR_TEMP | Boiler_C_Combustion_Air_Temperature | NOT_IN_PEEO | NO | NO
BLR_3 | FUEL_GAS_TEMP | Boiler_C_Main_Fuel_Gas_Temperature | NOT_IN_PEEO | NO | NO
BLR_3 | FLUE_GAS_OXYGEN | BOILER_C_FLUE_GAS_OXGYGEN | UN.UO.71AC1304.PV | NO | YES | 0.149
BLR_3 | CBD_BLOWDOWN | BOILER_C_CBD | NOT_IN_PEEO | NO | NO
BLR_3 | DESUPERHEATER_OUTLET_TEMP | Boiler_C_DSP_outlet_Temp | NOT_IN_PEEO | NO | NO
BLR_3 | HP_STEAM_PRESSURE | Boiler_C_DSP_outlet_Pressure | NOT_IN_PEEO | NO | NO
BLR_4 | STEAM_FLOW_RAW | BLR_4_HPS_Gen_raw | NOT_IN_PEEO | NO | NO
BLR_4 | FUEL_GAS_FLOW | Fuel_BLR_4_raw | NOT_IN_PEEO | NO | NO
BLR_4 | FD_FAN_STEAM_RAW | FD_Fan_BLR_4_Steam_raw | NOT_IN_PEEO | NO | NO
BLR_4 | BFW_TO_ECONOMIZER | BFW_TO_BOILER_D | NOT_IN_PEEO | NO | NO
BLR_4 | BFW_TO_DESUPERHEATER | DSP_BFW_TO_BOILER_D | NOT_IN_PEEO | NO | NO
BLR_4 | STACK_TEMPERATURE | BOILER_D_STACK_TEMPERATURE | UN.UO.71TI1407.PV | YES | YES | 5.755
BLR_4 | COMBUSTION_AIR_TEMP | Boiler_D_Combustion_Air_Temperature | NOT_IN_PEEO | NO | NO
BLR_4 | FUEL_GAS_TEMP | Boiler_D_Main_Fuel_Gas_Temperature | NOT_IN_PEEO | NO | NO
BLR_4 | FLUE_GAS_OXYGEN | BOILER_D_FLUE_GAS_OXGYGEN | UN.UO.71AC1404.PV | NO | YES | 0.146
BLR_4 | CBD_BLOWDOWN | BOILER_D_CBD | NOT_IN_PEEO | NO | NO
BLR_4 | DESUPERHEATER_OUTLET_TEMP | Boiler_D_DSP_outlet_Temp | NOT_IN_PEEO | NO | NO
BLR_4 | HP_STEAM_PRESSURE | Boiler_D_DSP_outlet_Pressure | NOT_IN_PEEO | NO | NO
BLR_5 | STEAM_FLOW_RAW | BLR_5_HPS_Gen_raw | NOT_IN_PEEO | NO | NO
BLR_5 | FUEL_GAS_FLOW | Fuel_BLR_5_raw | NOT_IN_PEEO | NO | NO
BLR_5 | FD_FAN_STEAM_RAW | FD_Fan_BLR_5_Steam_raw | NOT_IN_PEEO | NO | NO
BLR_5 | BFW_TO_ECONOMIZER | BFW_TO_BOILER_E | NOT_IN_PEEO | NO | NO
BLR_5 | BFW_TO_DESUPERHEATER | DSP_BFW_TO_BOILER_E | NOT_IN_PEEO | NO | NO
BLR_5 | STACK_TEMPERATURE | BOILER_E_STACK_TEMPERATURE | UN.UO.71TI1507.PV | YES | YES | 6.509
BLR_5 | COMBUSTION_AIR_TEMP | Boiler_E_Combustion_Air_Temp | NOT_IN_PEEO | NO | NO
BLR_5 | FUEL_GAS_TEMP | Boiler_E_Main_Fuel_Gas_Temperature | NOT_IN_PEEO | NO | NO
BLR_5 | FLUE_GAS_OXYGEN | BOILER_E_FLUE_GAS_OXGYGEN | UN.UO.71AI1501C.PV | NO | YES | 0.086
BLR_5 | CBD_BLOWDOWN | BOILER_E_CBD | NOT_IN_PEEO | NO | NO
BLR_5 | DESUPERHEATER_OUTLET_TEMP | Boiler_E_DSP_outlet_Temp | NOT_IN_PEEO | NO | NO
BLR_5 | HP_STEAM_PRESSURE | Boiler_E_DSP_outlet_Pressure | NOT_IN_PEEO | NO | NO