## Computed_Hierarchy
tag_name | description | category | uom | formula | value
BOILER_A_AIR_CP_REF_T | BOILER A AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_A_AIR_MOISTURE | BOILER A AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_A_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_A_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_A_BOILER_LOAD | BOILER A BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_OUTLET_STEAM_FLOW/150000*100 | 1.7975
BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER A CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6499
BOILER_A_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER A CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER A CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_A_CP_OF_AIR_AT_STACK_TEMP | BOILER A CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_A_STACK_TEMPERATURE+273.15)/ | 6.9676
BOILER_A_CP_OF_H2O_AT_STACK_TEMP | BOILER A CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_A_FG_FLOW_RATE | BOILER A FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_A_FUEL_GAS_FLOW/1000 | 0.17548
BOILER_A_VAPOUR_PRESSURE_OF_H2O | BOILER A VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_B_AIR_CP_REF_T | BOILER B AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_B_AIR_MOISTURE | BOILER B AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_B_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_B_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_B_BOILER_LOAD | BOILER B BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_B_OUTLET_STEAM_FLOW/150000*100 | 1.8401
BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER B CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6497
BOILER_B_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER B CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER B CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_B_CP_OF_AIR_AT_STACK_TEMP | BOILER B CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_B_STACK_TEMPERATURE+273.15)/ | 6.9675
BOILER_B_CP_OF_H2O_AT_STACK_TEMP | BOILER B CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_B_VAPOUR_PRESSURE_OF_H2O | BOILER B VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_C_AIR_CP_REF_T | BOILER C AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_C_AIR_MOISTURE | BOILER C AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_C_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_C_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_C_BOILER_LOAD | BOILER C BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_C_OUTLET_STEAM_FLOW/150000*100 | 1.7993
BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER C CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6502
BOILER_C_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER C CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER C CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_C_CP_OF_AIR_AT_STACK_TEMP | BOILER C CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_C_STACK_TEMPERATURE+273.15)/ | 6.9676
BOILER_C_CP_OF_H2O_AT_STACK_TEMP | BOILER C CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_C_FG_FLOW_RATE | BOILER C FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_C_FUEL_GAS_FLOW/1000 | 0.1755
BOILER_C_VAPOUR_PRESSURE_OF_H2O | BOILER C VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_D_AIR_CP_REF_T | BOILER D AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_D_AIR_MOISTURE | BOILER D AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_D_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_D_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_D_BOILER_LOAD | BOILER D BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_D_OUTLET_STEAM_FLOW/150000*100 | 1.8534
BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER D CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6481
BOILER_D_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER D CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2) | 8.3661
BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER D CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_D_CP_OF_AIR_AT_STACK_TEMP | BOILER D CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_D_STACK_TEMPERATURE+273.15)/ | 6.9675
BOILER_D_CP_OF_H2O_AT_STACK_TEMP | BOILER D CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_D_FG_FLOW_RATE | BOILER D FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_D_FUEL_GAS_FLOW/1000 | 0.17549
BOILER_D_VAPOUR_PRESSURE_OF_H2O | BOILER D VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_E_AIR_CP_REF_T | BOILER E AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_E_AIR_MOISTURE | BOILER E AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_E_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_E_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_E_BOILER_LOAD | BOILER E BOILER LOAD | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | DESUPERHEATER_E_OUTLET_STEAM_FLOW/150000*100 | 1.8692
BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER E CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6572
BOILER_E_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER E CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2) | 8.3667
BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER E CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9587
BOILER_E_CP_OF_AIR_AT_STACK_TEMP | BOILER E CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_STACK_TEMPERATURE+273.15)/ | 6.9677
BOILER_E_CP_OF_H2O_AT_STACK_TEMP | BOILER E CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.46443
BOILER_E_FG_FLOW_RATE | BOILER E FG FLOW RATE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | TPH | BOILER_E_FUEL_GAS_FLOW/1.295/1000 | 0.17993
BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER E HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,0*10^-6*28*5654*BOILER_E_BOILER_LOAD) | 0
BOILER_E_SH_DUTY | BOILER E SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_E_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_E_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_E_STEAM_DRUM_TEMP*3.45877718874616+2082.10231045632))*0.239006/10000 | 0
BOILER_E_SH_PERFORMANCE | BOILER E SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,(BOILER_E_SH_SPECIFIC_DUTY)/0.110075721*100) | 0
BOILER_E_SH_SPECIFIC_DUTY | BOILER E SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_E_STATUS==0,0,BOILER_E_SH_DUTY/DESUPERHEATER_E_OUTLET_STEAM_FLOW*1000) | 0
BOILER_E_STATUS | BOILER E STATUS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | if(BOILER_E_BOILER_LOAD>25&&DESUPERHEATER_E_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_E>40,1,0) | 0
BOILER_E_STEAM_DRUM_PRESSURE | BOILER E STEAM DRUM PRESSURE | LBM_preprocessing_inferred_tags_main | nan | if(HP_STEAM_PRESSURE_FROM_DS_E==MISSING_NUMERIC,0,HP_STEAM_PRESSURE_FROM_DS_E) | 1.884
BOILER_E_STEAM_DRUM_TEMP | BOILER E STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_E_STATUS==0,0,4.02521999671835*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0
BOILER_E_VAPOUR_PRESSURE_OF_H2O | BOILER E VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_FG_ETHYLENE_CONCENTRATION | BOILER FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 0 | 0
COMPONENT_BUTANE_MW | COMPONENT BUTANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 58.12 | 58.12
COMPONENT_CO_MW | COMPONENT CO MW | LBM_preprocessing_inferred_tags_main | g/gmol | 28.01 | 28.01
COMPONENT_ETHANE_MW | COMPONENT ETHANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 30.07 | 30.07
COMPONENT_ETHYLENE_MW | COMPONENT ETHYLENE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 28.051 | 28.051
COMPONENT_HYDROGEN_MW | COMPONENT HYDROGEN MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 2.016 | 2.016
COMPONENT_METHANE_MW | COMPONENT METHANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 16.04 | 16.04
COMPONENT_NITROGEN_MW | COMPONENT NITROGEN MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 28.016 | 28.016
COMPONENT_PENTANE_MW | COMPONENT PENTANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 72.15 | 72.15
COMPONENT_PROPANE_MW | COMPONENT PROPANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 44.09 | 44.09
Calc_capacity | CALC CAPACITY | LBM_preprocessing_inferred_tags_main,LBM_postprocessing_capacity_utilization_inferred,LBM_optimum_inferred_tags_main | MT/ HR | (DESUPERHEATER_OUTLET_STEAM_FLOW+DESUPERHEATER_B_OUTLET_STEAM_FLOW+DESUPERHEATER_C_OUTLET_STEAM_FLOW+DESUPERHEATER_D_OUTLET_STEAM_FLOW+DESUPERHEATER_E_OUTLET_STEAM_FLOW) | 13739.292
LHV_BUTANE | LHV BUTANE | LBM_preprocessing_inferred_tags_main | MJ/KG | 45.689 | 45.689
LHV_C2H4_ETHYLENE | LHV C2H4 ETHYLENE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 47.178 | 47.178
LHV_C2H6_ETHANE | LHV C2H6 ETHANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 47.497 | 47.497
LHV_C3H8_PROPANE | LHV C3H8 PROPANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 46.362 | 46.362
LHV_CH4_METHANE | LHV CH4 METHANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 50.026 | 50.026
LHV_CO | LHV CO | LBM_preprocessing_inferred_tags_main | MJ/KG | 10.105 | 10.105
LHV_FG | LHV FG | LBM_preprocessing_inferred_tags_main | MJ/KG | 31316 | 31316
LHV_FG_E_DESIGN | LHV FG E | LBM_preprocessing_inferred_tags_main | - | 45108 | 45108
LHV_H2O_WATER | LHV H2O WATER | LBM_preprocessing_inferred_tags_main | MJ/KG | 0 | 0
LHV_H2_HYDROGEN | LHV H2 HYDROGEN | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 120.004 | 120.004
LHV_IC4 | LHV IC4 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.613 | 45.613
LHV_IC5 | LHV IC5 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.241 | 45.241
LHV_N2_NITROGEN | LHV N2 NITROGEN | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 0 | 0
LHV_NC4 | LHV NC4 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.75 | 45.75
LHV_NC5 | LHV NC5 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.36 | 45.36
LHV_PENTANE | LHV PENTANE | LBM_preprocessing_inferred_tags_main | MJ/KG | 45.35 | 45.35
RELATIVE_HUMIDITY_CLEAN | RELATIVE HUMIDITY | LBM_preprocessing_inferred_tags_main | % | if((abs(RELATIVE_HUMIDITY)<1 && abs(RELATIVE_HUMIDITY)>0),abs(RELATIVE_HUMIDITY),0.6) | 0.17
VAPOUR_PRESSURE_OF_WATER | VAPOUR PRESSURE OF WATER | LBM_preprocessing_inferred_tags_main | mmhg | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631

## Not_Computed
tag_name | description | category | uom | formula | full_potential_value | reason_if_not | missing_inputs
ARRAZI_PLANT_LOAD_1 | ARRAZI PLANT LOAD 1 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | if(ARRAZI_PLANT_LOAD==MISSING_NUMERIC,0,ARRAZI_PLANT_LOAD) | 0 | Missing inputs (not in hierarchy): ARRAZI_PLANT_LOAD | ARRAZI_PLANT_LOAD
ARRAZI_PLANT_STATUS | ARRAZI PLANT STATUS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_LOAD_1<70,0,1) | 0 | Missing inputs (not in hierarchy): ARRAZI_PLANT_LOAD_1 | ARRAZI_PLANT_LOAD_1
BFW_QUALITY_RATE | BFW QUALITY RATE | TRG_compute_inferred_post_pta | % | FLAG_BFW_QUALITY_PTA_actual*100/24 |  | eval_error: name 'FLAG_BFW_QUALITY_PTA_actual' is not defined
BLOWDOWN_CONDUCTIVITY | BLOWDOWN CONDUCTIVITY | LBM_preprocessing_inferred_tags_main | US/ CM | ((BOILER_A_CONDUCTIVITY*BOILER_A_STATUS)+(BOILER_B_CONDUCTIVITY*BOILER_B_STATUS)+(BOILER_C_CONDUCTIVITY*BOILER_C_STATUS)+(BOILER_D_CONDUCTIVITY*BOILER_D_STATUS)+(BOILER_E_CONDUCTIVITY*BOILER_E_STATUS))/BOILERS_ONLINE |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_CONDUCTIVITY; BOILER_A_STATUS; BOILER_B_CONDUCTIVITY; BOILER_B_STATUS; BOILER_C_CONDUCTIVITY (+4 more) | BOILERS_ONLINE; BOILER_A_CONDUCTIVITY; BOILER_A_STATUS; BOILER_B_CONDUCTIVITY; BOILER_B_STATUS; BOILER_C_CONDUCTIVITY; BOILER_C_STATUS; BOILER_D_CONDUCTIVITY; BOILER_D_STATUS; BOILER_E_CONDUCTIVITY
BOILERS_ONLINE | BOILERS ONLINE | LBM_preprocessing_inferred_tags_main | - | BOILER_A_STATUS+BOILER_B_STATUS+BOILER_C_STATUS+BOILER_D_STATUS+BOILER_E_STATUS | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
BOILER_A_ACTUAL_SP_ENERGY_DELTA | BOILER A ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) |  | eval_error: name 'BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER A AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_A_AIR_CP_REF_T+BOILER_A_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044 | Missing inputs (not in hierarchy): BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER_A_CP_AT_COMBUSTION_TEMPERATURE
BOILER_A_AIR_FUEL_MASS_RATIO | BOILER A AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_EXCESS_AIR+BOILER_A_CORRECTED_COMBUSTION_AIR | 14.5295 | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_EXCESS_AIR | BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_EXCESS_AIR
BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER A AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*17.265 | 13.7122 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER A AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058 | Missing inputs (not in hierarchy): BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*14.807 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER A AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*34.344 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER A AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*15.487 | 0.04938 | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER A AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*15.353 | 0.020674 | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER A AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*15.487 | 0.058544 | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER A AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*15.353 | 0.000626 | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER A AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431 | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER A AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_A_CO2_FORMED/44.01+BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.85*BOILER_A_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_A_FLUE_GAS_MW)/BOILER_A_FLUE_GAS_MW | 0.21039 | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_MW; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_MW; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED
BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER A AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_A_FG_MW)/2 | 0.4367 | Missing inputs (not in hierarchy): BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_A_FG_MW | BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_A_FG_MW
BOILER_A_BFW_ENERGY | BOILER A BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*BOILER_A_BFW_ENTHALPY/1000) | 0 | Missing inputs (not in hierarchy): BOILER_A_BFW_ENTHALPY; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS | BOILER_A_BFW_ENTHALPY; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS
BOILER_A_BFW_ENTHALPY | BOILER A BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_A_INLET_TEMPERATURE) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_A_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_A_INLET_TEMPERATURE
BOILER_A_BLOWDOWN_LOSS | BOILER A BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,((BOILER_A_CBD_BD/1000)*((STEAM_DRUM_A_PRESSURE*2.11087739028321+SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_A_CBD_BD; BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_A_CBD_BD; BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE
BOILER_A_BOILER_INDIRECT_EFFICIENCY | BOILER A BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_A_CALCULATED_AIRFLOW_NM3H | BOILER A CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_A_STATUS==0,0,BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0 | Missing inputs (not in hierarchy): BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS | BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS
BOILER_A_CH4_CO2_COMBUSTION | BOILER A CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*2.744 | 2.1793 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_CH4_H2O_COMBUSTION | BOILER A CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*2.246 | 1.7838 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_CH4_N2_COMBUSTION | BOILER A CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*13.275 | 10.5432 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_CO2_EMISSIONS | BOILER A CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_CO2_FORMED*BOILER_A_FUEL_GAS_CORRECTED_TPH) | 0 | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS | BOILER_A_CO2_FORMED; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS
BOILER_A_CO2_FORMED | BOILER A CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_CH4_CO2_COMBUSTION+BOILER_A_ETHANE_CO2_COMBUSTION+BOILER_A_ETHYLENE_CO2_COMBUSTION+BOILER_A_PROPANE_CO2_COMBUSTION+BOILER_A_NC4_CO2_COMBUSTION+BOILER_A_IC4_CO2_COMBUSTION+BOILER_A_NC5_CO2_COMBUSTION+BOILER_A_IC5_CO2_COMBUSTION | 2.3084 | Missing inputs (not in hierarchy): BOILER_A_CH4_CO2_COMBUSTION; BOILER_A_ETHANE_CO2_COMBUSTION; BOILER_A_ETHYLENE_CO2_COMBUSTION; BOILER_A_IC4_CO2_COMBUSTION; BOILER_A_IC5_CO2_COMBUSTION; BOILER_A_NC4_CO2_COMBUSTION (+2 more) | BOILER_A_CH4_CO2_COMBUSTION; BOILER_A_ETHANE_CO2_COMBUSTION; BOILER_A_ETHYLENE_CO2_COMBUSTION; BOILER_A_IC4_CO2_COMBUSTION; BOILER_A_IC5_CO2_COMBUSTION; BOILER_A_NC4_CO2_COMBUSTION; BOILER_A_NC5_CO2_COMBUSTION; BOILER_A_PROPANE_CO2_COMBUSTION
BOILER_A_CONVECTION_DUTY | BOILER A CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY+BOILER_A_SH_DUTY+BOILER_A_STACK_LOSS_CORRECTED) | 0 | Missing inputs (not in hierarchy): BOILER_A_ECONOMIZER_DUTY; BOILER_A_SH_DUTY; BOILER_A_STACK_LOSS_CORRECTED; BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY; BOILER_A_SH_DUTY; BOILER_A_STACK_LOSS_CORRECTED; BOILER_A_STATUS
BOILER_A_CONVECTION_SECTION_EFFICIENCY | BOILER A CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_A_CONVECTION_DUTY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS
BOILER_A_CORRECTED_BFW_FLOW | BOILER A CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_A_STATUS==0,0,(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-DESUPERHEATER_OUTLET_STEAM_FLOW-BOILER_A_CBD_BD))/1000) | 0 | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_A; BFW_FLOW_TO_ECOMONIZER_A; BOILER_A_CBD_BD; BOILER_A_STATUS | BFW_FLOW_TO_DESUPERHEATER_A; BFW_FLOW_TO_ECOMONIZER_A; BOILER_A_CBD_BD; BOILER_A_STATUS
BOILER_A_CORRECTED_COMBUSTION_AIR | BOILER A CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_A_AIR_MOISTURE) | 14.4151 | Missing inputs (not in hierarchy): BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_A_CORRECTED_COMBUTION_H2O_FORMED | BOILER A CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2O_FORMED+(BOILER_A_CORRECTED_COMBUSTION_AIR-BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679 | Missing inputs (not in hierarchy): BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_H2O_FORMED | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_H2O_FORMED
BOILER_A_CORRECTED_FUEL_FLOW | BOILER A CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW-((BOILER_A_FUEL_GAS_ENERGY_INPUT-(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY+BOILER_A_BLOWDOWN_LOSS+BOILER_A_STACK_LOSS+BOILER_A_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_A_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOA | 0 | Missing inputs (not in hierarchy): BOILER_A_BFW_ENERGY; BOILER_A_BLOWDOWN_LOSS; BOILER_A_FUEL_GAS_ENERGY_INPUT; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STACK_LOSS (+2 more) | BOILER_A_BFW_ENERGY; BOILER_A_BLOWDOWN_LOSS; BOILER_A_FUEL_GAS_ENERGY_INPUT; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STACK_LOSS; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER A CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS
BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER A CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9663 | Missing inputs (not in hierarchy): BOILER_A_COMBUSTION_AIR_TEMPERATURE | BOILER_A_COMBUSTION_AIR_TEMPERATURE
BOILER_A_CP_CH4_FUEL_TEMP | BOILER A CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3614 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_ETHANE_FUEL_TEMP | BOILER A CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0739 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_ETHYLENE_FUEL_TEMP | BOILER A CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6651 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_H2_FUEL_TEMP | BOILER A CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8453 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_IC4_FUEL_TEMP | BOILER A CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1103 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_IC5_FUEL_TEMP | BOILER A CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8823 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_NC4_FUEL_TEMP | BOILER A CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.928 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_NC5_FUEL_TEMP | BOILER A CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1654 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_PROPANE_FUEL_TEMP | BOILER A CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.047 | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER A CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_A_CP_H2_FUEL_TEMP+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_A_CP_CH4_FUEL_TEMP+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_A_CP_ETHYLENE_FUEL_TEMP+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7287 | Missing inputs (not in hierarchy): BOILER_A_CP_CH4_FUEL_TEMP; BOILER_A_CP_ETHANE_FUEL_TEMP; BOILER_A_CP_ETHYLENE_FUEL_TEMP; BOILER_A_CP_H2_FUEL_TEMP; BOILER_A_CP_IC4_FUEL_TEMP; BOILER_A_CP_IC5_FUEL_TEMP (+13 more) | BOILER_A_CP_CH4_FUEL_TEMP; BOILER_A_CP_ETHANE_FUEL_TEMP; BOILER_A_CP_ETHYLENE_FUEL_TEMP; BOILER_A_CP_H2_FUEL_TEMP; BOILER_A_CP_IC4_FUEL_TEMP; BOILER_A_CP_IC5_FUEL_TEMP; BOILER_A_CP_NC4_FUEL_TEMP; BOILER_A_CP_NC5_FUEL_TEMP; BOILER_A_CP_PROPANE_FUEL_TEMP; BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION; BOILER_A_FG_MW; BOILER_A_FG_NC4_MASS_FRACTION; BOILER_A_FG_NC5_MASS_FRACTION; BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER A CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_A_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION (+4 more) | BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION; BOILER_A_FG_MW; BOILER_A_FG_NC4_MASS_FRACTION; BOILER_A_FG_NC5_MASS_FRACTION; BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_A_EXCESS_AIR*(1-BOILER_A_AIR_MOISTURE)+BOILER_A_N2_FORMED+BOILER_A_CO2_FORMED | 13.4993 | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_N2_FORMED
BOILER_A_ECONOMIZER_DUTY | BOILER A ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*((STEAM_DRUM_A_PRESSURE*0.0336523715096497+ECONIMIZER_A_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_A_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE; STEAM_DRUM_A_PRESSURE | BFW_PRESSURE_TO_BOILER; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE; STEAM_DRUM_A_PRESSURE
BOILER_A_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER A EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_BLOWDOWN_LOSS/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_A_BLOWDOWN_LOSS; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS | BOILER_A_BLOWDOWN_LOSS; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS
BOILER_A_ENERGY_GAINED | BOILER A ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY) | 0 | Missing inputs (not in hierarchy): BOILER_A_BFW_ENERGY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_ETHANE_CO2_COMBUSTION | BOILER A ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHANE_H2O_COMBUSTION | BOILER A ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHANE_N2_COMBUSTION | BOILER A ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHYLENE_CO2_COMBUSTION | BOILER A ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*3.138 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_ETHYLENE_H2O_COMBUSTION | BOILER A ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*1.285 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_ETHYLENE_N2_COMBUSTION | BOILER A ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*11.385 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_EXCESS_AIR | BOILER A EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_A_FLUE_GAS_OXGYGEN)*((BOILER_A_N2_FORMED/28.01)+(BOILER_A_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_A_CO2_FORMED/44.01))/(20.95-BOILER_A_FLUE_GAS_OXGYGEN)) | 0.11442 | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_CORRECTED_COMBUTION_H2O_FORMED; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED; BOILER_A_CORRECTED_COMBUTION_H2O_FORMED; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_N2_FORMED
BOILER_A_FG_CH4_MASS_FRACTION | BOILER A FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_CH4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.79422 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_CH4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_CH4_MASS_PERCENTAGE | BOILER A FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_A_FG_MW | 79.4217 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION
BOILER_A_FG_DENSITY | BOILER A FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_A_FG_MW/22.414 | 0.7893 | Missing inputs (not in hierarchy): BOILER_A_FG_MW | BOILER_A_FG_MW
BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER A FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | BOILER_A_FG_ETHANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.026684 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_ETHANE_MASS_PERCENTAGE | BOILER A FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_A_FG_MW | 2.6684 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION
BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER A FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE | BOILER A FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_A_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION
BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER A FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE | BOILER A FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_A_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION
BOILER_A_FG_IC4_MASS_FRACTION | BOILER A FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_IC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.003188 | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_IC4_MASS_PERCENTAGE | BOILER A FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | 0.31885 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION
BOILER_A_FG_IC5_MASS_FRACTION | BOILER A FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_IC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.001347 | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_IC5_MASS_PERCENTAGE | BOILER A FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | 0.13466 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION
BOILER_A_FG_MW | BOILER A FG MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | G/MOL | (NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW+NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_A_FG_PROPANE_CONCEN | 17.6914 | Missing inputs (not in hierarchy): NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_A_FG_N2_CONCENTRATION; NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION
BOILER_A_FG_NC4_MASS_FRACTION | BOILER A FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.00378 | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NC4_MASS_PERCENTAGE | BOILER A FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | 0.37802 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION
BOILER_A_FG_NC5_MASS_FRACTION | BOILER A FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05 | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NC5_MASS_PERCENTAGE | BOILER A FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | 0.004081 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION
BOILER_A_FG_NITROGEN_MASS_FRACTION | BOILER A FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.16219 | Missing inputs (not in hierarchy): BOILER_A_FG_NITROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | BOILER A FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_A_FG_MW | 16.219 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_N2_CONCENTRATION
BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER A FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_PROPANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.008553 | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_PROPANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_PROPANE_MASS_PERCENTAGE | BOILER A FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_A_FG_MW | 0.85531 | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION
BOILER_A_FLUE_GAS_MW | BOILER A FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_A_CO2_FORMED/44.01+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.96) | 27.6617 | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | 15.3673 | Missing inputs (not in hierarchy): BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_FOULING_INDEX | BOILER A FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_A_STATUS==0,0,1/BOILER_A_UA_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_UA_ECONOMIZER | BOILER_A_STATUS; BOILER_A_UA_ECONOMIZER
BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER A FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | (BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942 | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION
BOILER_A_FUEL_CONSUMPTION | BOILER A FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS
BOILER_A_FUEL_GAIN_LOSS | BOILER A FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 |  | eval_error: name 'BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_A_FUEL_GAS_CORRECTED_TPH | BOILER A FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW/1000) | 0 | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS
BOILER_A_FUEL_GAS_ENERGY_INPUT | BOILER A FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_FG_FLOW_RATE*1000*BOILER_A_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS
BOILER_A_H2O_FORMED | BOILER A H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2_H2O_COMBUSTION+BOILER_A_CH4_H2O_COMBUSTION+BOILER_A_ETHANE_H2O_COMBUSTION+BOILER_A_ETHYLENE_H2O_COMBUSTION+BOILER_A_PROPANE_H2O_COMBUSTION+BOILER_A_IC4_H2O_COMBUSTION+BOILER_A_NC4_H2O_COMBUSTION+BOILER_A_IC5_H2O_COMBUSTION+BOILER_A_NC5_H2O_COMBUSTION | 1.8586 | Missing inputs (not in hierarchy): BOILER_A_CH4_H2O_COMBUSTION; BOILER_A_ETHANE_H2O_COMBUSTION; BOILER_A_ETHYLENE_H2O_COMBUSTION; BOILER_A_H2_H2O_COMBUSTION; BOILER_A_IC4_H2O_COMBUSTION; BOILER_A_IC5_H2O_COMBUSTION (+3 more) | BOILER_A_CH4_H2O_COMBUSTION; BOILER_A_ETHANE_H2O_COMBUSTION; BOILER_A_ETHYLENE_H2O_COMBUSTION; BOILER_A_H2_H2O_COMBUSTION; BOILER_A_IC4_H2O_COMBUSTION; BOILER_A_IC5_H2O_COMBUSTION; BOILER_A_NC4_H2O_COMBUSTION; BOILER_A_NC5_H2O_COMBUSTION; BOILER_A_PROPANE_H2O_COMBUSTION
BOILER_A_H2_CO2_COMBUSTION | BOILER A H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*0 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_H2_H2O_COMBUSTION | BOILER A H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*8.937 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_H2_N2_COMBUSTION | BOILER A H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*26.407 | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER A HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_A_STACK_TEMPERATURE-15.6)))) | 0 | Missing inputs (not in hierarchy): BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS | BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER A HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,9*(BOILER_A_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_A_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_A_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0 | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_STATUS | BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER A HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_A_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER A HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,0*10^-6*28*5654*BOILER_A_BOILER_LOAD) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS | BOILER_A_STATUS
BOILER_A_HP_STEAM_ENTHALPY | BOILER A HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS)+2.66244961166282*DESUPERHEATER_OUTLET_TEMPERATURE)*0.239+2) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS
BOILER_A_IC4_CO2_COMBUSTION | BOILER A IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*3.029 | 0.009658 | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_IC4_H2O_COMBUSTION | BOILER A IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*1.55 | 0.005859 | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_IC4_N2_COMBUSTION | BOILER A IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*11.908 | 0.037969 | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_IC5_CO2_COMBUSTION | BOILER A IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*3.05 | 0.004107 | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_IC5_H2O_COMBUSTION | BOILER A IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*1.498 | 0.002017 | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_IC5_N2_COMBUSTION | BOILER A IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*11.805 | 0.015897 | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_LHV_DESIGN | BOILER A LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (LHV_FG/BOILER_A_FG_DENSITY)/1000 | 39.6755 | Missing inputs (not in hierarchy): BOILER_A_FG_DENSITY | BOILER_A_FG_DENSITY
BOILER_A_LMTD_ECONOMIZER | BOILER A LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_A_STATUS==0,0,((673-ECONIMIZER_A_OUTLET_TEMPERATURE)-(BOILER_A_STACK_TEMPERATURE-ECONOMIZER_A_INLET_TEMPERATURE))/ln((673-ECONIMIZER_A_OUTLET_TEMPERATURE)/(-ECONOMIZER_A_INLET_TEMPERATURE+BOILER_A_STACK_TEMPERATURE))) |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE | BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE
BOILER_A_MIXED_LHV_PER_KG | BOILER A MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019 | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV
BOILER_A_N2_FORMED | BOILER A N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2_N2_COMBUSTION+BOILER_A_CH4_N2_COMBUSTION+BOILER_A_ETHANE_N2_COMBUSTION+BOILER_A_ETHYLENE_N2_COMBUSTION+BOILER_A_PROPANE_N2_COMBUSTION+BOILER_A_IC4_N2_COMBUSTION+BOILER_A_NC4_N2_COMBUSTION+BOILER_A_IC5_N2_COMBUSTION+BOILER_A_NC5_N2_COMBUSTION | 11.0766 | Missing inputs (not in hierarchy): BOILER_A_CH4_N2_COMBUSTION; BOILER_A_ETHANE_N2_COMBUSTION; BOILER_A_ETHYLENE_N2_COMBUSTION; BOILER_A_H2_N2_COMBUSTION; BOILER_A_IC4_N2_COMBUSTION; BOILER_A_IC5_N2_COMBUSTION (+3 more) | BOILER_A_CH4_N2_COMBUSTION; BOILER_A_ETHANE_N2_COMBUSTION; BOILER_A_ETHYLENE_N2_COMBUSTION; BOILER_A_H2_N2_COMBUSTION; BOILER_A_IC4_N2_COMBUSTION; BOILER_A_IC5_N2_COMBUSTION; BOILER_A_NC4_N2_COMBUSTION; BOILER_A_NC5_N2_COMBUSTION; BOILER_A_PROPANE_N2_COMBUSTION
BOILER_A_NC4_CO2_COMBUSTION | BOILER A NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*3.029 | 0.01145 | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_NC4_H2O_COMBUSTION | BOILER A NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*1.55 | 0.004942 | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_NC4_N2_COMBUSTION | BOILER A NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*11.908 | 0.045014 | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_NC5_CO2_COMBUSTION | BOILER A NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*3.05 | 0.000124 | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_NC5_H2O_COMBUSTION | BOILER A NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05 | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_NC5_N2_COMBUSTION | BOILER A NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*11.805 | 0.000482 | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER A PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS
BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER A PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_A_ENERGY_GAINED; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS | BOILER_A_ENERGY_GAINED; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS
BOILER_A_PROPANE_CO2_COMBUSTION | BOILER A PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608 | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_PROPANE_H2O_COMBUSTION | BOILER A PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976 | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_PROPANE_N2_COMBUSTION | BOILER A PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327 | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_RADIATION_DUTY | BOILER A RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_ENERGY_GAINED-BOILER_A_CONVECTION_DUTY) | 0 | Missing inputs (not in hierarchy): BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS
BOILER_A_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER A RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_A_STATUS==0,0,BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) |  | Missing inputs (not in hierarchy): BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_A_STATUS | BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_A_STATUS
BOILER_A_RADIATION_LOSSES | BOILER A RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_MIXED_LHV_PER_KG*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOAD^2-0.0899*BOILER_A_BOILER_LOAD+3.2426)/100) | 0 | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS
BOILER_A_RADIATION_SECTION_EFFICIENCY | BOILER A RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS
BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER A SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_A_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_A_AIR_FUEL_MASS_RATIO | -50.8545 | Missing inputs (not in hierarchy): BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_COMBUSTION_AIR_TEMPERATURE | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_COMBUSTION_AIR_TEMPERATURE
BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER A SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0 | Missing inputs (not in hierarchy): BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_A_MAIN_FUEL_GAS_TEMPERATURE
BOILER_A_SH_DUTY | BOILER A SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*((STEAM_DRUM_A_PRESSURE*-2.64315212289699+DESUPERHEATER_TEMPERATURE*3.58096116723573+1939.73413132244)-(STEAM_DRUM_A_PRESSURE*-4.27591051303366+SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; DESUPERHEATER_TEMPERATURE; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE | BOILER_A_STATUS; DESUPERHEATER_TEMPERATURE; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE
BOILER_A_SH_PERFORMANCE | BOILER A SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,(BOILER_A_SH_SPECIFIC_DUTY)/0.128049016*100) | 0 | Missing inputs (not in hierarchy): BOILER_A_SH_SPECIFIC_DUTY; BOILER_A_STATUS | BOILER_A_SH_SPECIFIC_DUTY; BOILER_A_STATUS
BOILER_A_SH_SPECIFIC_DUTY | BOILER A SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_A_STATUS==0,0,BOILER_A_SH_DUTY/DESUPERHEATER_OUTLET_STEAM_FLOW*1000) | 0 | Missing inputs (not in hierarchy): BOILER_A_SH_DUTY; BOILER_A_STATUS | BOILER_A_SH_DUTY; BOILER_A_STATUS
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER A SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)) | 0 | Missing inputs (not in hierarchy): BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER A SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)*4.184) | 0 | Missing inputs (not in hierarchy): BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS
BOILER_A_STACK_LOSS | BOILER A STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_FLOW/(1000*1000)) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_STACK_LOSS_CORRECTED | BOILER A STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_CORRECTED_TPH/1000) | 0 | Missing inputs (not in hierarchy): BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_STATUS | BOILER A STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_A_BOILER_LOAD>25&&DESUPERHEATER_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS>40,1,0) | 0 | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS | HP_STEAM_PRESSURE_FROM_DS
BOILER_A_STEAM_DRUM_TEMP | BOILER A STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_A_STATUS==0,0,4.02521999671835*log(STEAM_DRUM_A_PRESSURE*98.065)^3-4.64392873298701*log(STEAM_DRUM_A_PRESSURE*98.065)^2+11.2370106828649*log(STEAM_DRUM_A_PRESSURE*98.065)+83.4806425229703) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE | BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE
BOILER_A_STEAM_TO_FIRE_DUTY_RATIO | BOILER A STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW/(BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG)*1000) | 0 | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS
BOILER_A_SUPERHEATED_STEAM_BFW_RATIO | BOILER A SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_A_STATUS==0,0,(DESUPERHEATER_OUTLET_STEAM_FLOW+BOILER_A_CBD_BD)/(BOILER_A_CORRECTED_BFW_FLOW*1000)) |  | Missing inputs (not in hierarchy): BOILER_A_CBD_BD; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS | BOILER_A_CBD_BD; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS
BOILER_A_THERMAL_EFFICIENCY | BOILER A THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY)/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_A_BFW_ENERGY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER A TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0 | Missing inputs (not in hierarchy): BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_A_STATUS | BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_A_STATUS
BOILER_A_TOTAL_FLUE_GAS_CORRECTED | BOILER A TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_CORRECTED_TPH*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS
BOILER_A_TOTAL_FLUE_GAS_GENERATED | BOILER A TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW/1000*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS
BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER A TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_TOTAL_MOISTURE_WITH_AIR+BOILER_A_H2O_FORMED | 1.868 | Missing inputs (not in hierarchy): BOILER_A_H2O_FORMED; BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER_A_H2O_FORMED; BOILER_A_TOTAL_MOISTURE_WITH_AIR
BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER A TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER A TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_A_MIXED_LHV_PER_KG) | 0 | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_A_STATUS
BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER A TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_A_RADIATION_LOSSES) | 0 | Missing inputs (not in hierarchy): BOILER_A_RADIATION_LOSSES; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_RADIATION_LOSSES; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER A TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_AIR_MOISTURE | 0.009372 | Missing inputs (not in hierarchy): BOILER_A_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO
BOILER_A_TOTAL_STEAM_ENERGY | BOILER A TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_HP_STEAM_ENTHALPY/1000000) | 0 | Missing inputs (not in hierarchy): BOILER_A_HP_STEAM_ENTHALPY; BOILER_A_STATUS | BOILER_A_HP_STEAM_ENTHALPY; BOILER_A_STATUS
BOILER_A_UA_ECONOMIZER | BOILER A UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY/BOILER_A_LMTD_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_A_ECONOMIZER_DUTY; BOILER_A_LMTD_ECONOMIZER; BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY; BOILER_A_LMTD_ECONOMIZER; BOILER_A_STATUS
BOILER_B_ACTUAL_SP_ENERGY_DELTA | BOILER B ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) |  | eval_error: name 'BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER B AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_B_AIR_CP_REF_T+BOILER_B_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044 | Missing inputs (not in hierarchy): BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER_B_CP_AT_COMBUSTION_TEMPERATURE
BOILER_B_AIR_FUEL_MASS_RATIO | BOILER B AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_EXCESS_AIR+BOILER_B_CORRECTED_COMBUSTION_AIR | 14.528 | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_EXCESS_AIR | BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_EXCESS_AIR
BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER B AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*17.265 | 13.7122 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER B AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058 | Missing inputs (not in hierarchy): BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*14.807 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER B AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*34.344 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER B AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*15.487 | 0.04938 | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER B AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*15.353 | 0.020674 | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER B AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*15.487 | 0.058544 | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER B AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*15.353 | 0.000626 | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER B AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431 | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER B AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_B_CO2_FORMED/44.01+BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.85*BOILER_B_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_B_FLUE_GAS_MW)/BOILER_B_FLUE_GAS_MW | 0.21038 | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_MW; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_MW; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED
BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER B AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_B_FG_MW)/2 | 0.43669 | Missing inputs (not in hierarchy): BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_B_FG_MW | BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_B_FG_MW
BOILER_B_BFW_ENERGY | BOILER B BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*BOILER_B_BFW_ENTHALPY/1000) | 0 | Missing inputs (not in hierarchy): BOILER_B_BFW_ENTHALPY; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS | BOILER_B_BFW_ENTHALPY; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS
BOILER_B_BFW_ENTHALPY | BOILER B BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_B_INLET_TEMPERATURE) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_B_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_B_INLET_TEMPERATURE
BOILER_B_BLOWDOWN_LOSS | BOILER B BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,((CBD_BLOW_DOWN_B/1000)*((BOILER_B_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_B | BFW_PRESSURE_TO_BOILER; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_B
BOILER_B_BOILER_INDIRECT_EFFICIENCY | BOILER B BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_B_CALCULATED_AIRFLOW_NM3H | BOILER B CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_B_STATUS==0,0,BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0 | Missing inputs (not in hierarchy): BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS | BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS
BOILER_B_CH4_CO2_COMBUSTION | BOILER B CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*2.744 | 2.1793 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_CH4_H2O_COMBUSTION | BOILER B CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*2.246 | 1.7838 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_CH4_N2_COMBUSTION | BOILER B CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*13.275 | 10.5432 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_CO2_EMISSIONS | BOILER B CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_CO2_FORMED*BOILER_B_FUEL_GAS_CORRECTED_TPH) | 0 | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS | BOILER_B_CO2_FORMED; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS
BOILER_B_CO2_FORMED | BOILER B CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_CH4_CO2_COMBUSTION+BOILER_B_ETHANE_CO2_COMBUSTION+BOILER_B_ETHYLENE_CO2_COMBUSTION+BOILER_B_PROPANE_CO2_COMBUSTION+BOILER_B_NC4_CO2_COMBUSTION+BOILER_B_IC4_CO2_COMBUSTION+BOILER_B_NC5_CO2_COMBUSTION+BOILER_B_IC5_CO2_COMBUSTION | 2.3084 | Missing inputs (not in hierarchy): BOILER_B_CH4_CO2_COMBUSTION; BOILER_B_ETHANE_CO2_COMBUSTION; BOILER_B_ETHYLENE_CO2_COMBUSTION; BOILER_B_IC4_CO2_COMBUSTION; BOILER_B_IC5_CO2_COMBUSTION; BOILER_B_NC4_CO2_COMBUSTION (+2 more) | BOILER_B_CH4_CO2_COMBUSTION; BOILER_B_ETHANE_CO2_COMBUSTION; BOILER_B_ETHYLENE_CO2_COMBUSTION; BOILER_B_IC4_CO2_COMBUSTION; BOILER_B_IC5_CO2_COMBUSTION; BOILER_B_NC4_CO2_COMBUSTION; BOILER_B_NC5_CO2_COMBUSTION; BOILER_B_PROPANE_CO2_COMBUSTION
BOILER_B_CONVECTION_DUTY | BOILER B CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY+BOILER_B_SH_DUTY+BOILER_B_STACK_LOSS_CORRECTED) | 0 | Missing inputs (not in hierarchy): BOILER_B_ECONOMIZER_DUTY; BOILER_B_SH_DUTY; BOILER_B_STACK_LOSS_CORRECTED; BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY; BOILER_B_SH_DUTY; BOILER_B_STACK_LOSS_CORRECTED; BOILER_B_STATUS
BOILER_B_CONVECTION_SECTION_EFFICIENCY | BOILER B CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_B_CONVECTION_DUTY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS
BOILER_B_CORRECTED_BFW_FLOW | BOILER B CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_B_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-DESUPERHEATER_B_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_B))/1000) | 0 | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_B; BFW_FLOW_TO_ECONOMIZER_B; BOILER_B_STATUS; CBD_BLOW_DOWN_B | BFW_FLOW_TO_DESUPERHEATER_B; BFW_FLOW_TO_ECONOMIZER_B; BOILER_B_STATUS; CBD_BLOW_DOWN_B
BOILER_B_CORRECTED_COMBUSTION_AIR | BOILER B CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_B_AIR_MOISTURE) | 14.4151 | Missing inputs (not in hierarchy): BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_B_CORRECTED_COMBUTION_H2O_FORMED | BOILER B CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2O_FORMED+(BOILER_B_CORRECTED_COMBUSTION_AIR-BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679 | Missing inputs (not in hierarchy): BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_H2O_FORMED | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_H2O_FORMED
BOILER_B_CORRECTED_FUEL_FLOW | BOILER B CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW-((BOILER_B_FUEL_GAS_ENERGY_INPUT-(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY+BOILER_B_BLOWDOWN_LOSS+BOILER_B_STACK_LOSS+BOILER_B_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_B_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOA | 0 | Missing inputs (not in hierarchy): BOILER_B_BFW_ENERGY; BOILER_B_BLOWDOWN_LOSS; BOILER_B_FUEL_GAS_ENERGY_INPUT; BOILER_B_FUEL_GAS_FLOW; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_MIXED_LHV_PER_KG (+3 more) | BOILER_B_BFW_ENERGY; BOILER_B_BLOWDOWN_LOSS; BOILER_B_FUEL_GAS_ENERGY_INPUT; BOILER_B_FUEL_GAS_FLOW; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STACK_LOSS; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER B CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS
BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER B CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9663 | Missing inputs (not in hierarchy): BOILER_B_COMBUSTION_AIR_TEMPERATURE | BOILER_B_COMBUSTION_AIR_TEMPERATURE
BOILER_B_CP_CH4_FUEL_TEMP | BOILER B CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3613 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_ETHANE_FUEL_TEMP | BOILER B CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0729 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_ETHYLENE_FUEL_TEMP | BOILER B CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6644 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_H2_FUEL_TEMP | BOILER B CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8452 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_IC4_FUEL_TEMP | BOILER B CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1072 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_IC5_FUEL_TEMP | BOILER B CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8799 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_NC4_FUEL_TEMP | BOILER B CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9262 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_NC5_FUEL_TEMP | BOILER B CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1634 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_PROPANE_FUEL_TEMP | BOILER B CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0456 | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER B CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_B_CP_H2_FUEL_TEMP+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_B_CP_CH4_FUEL_TEMP+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_B_CP_ETHYLENE_FUEL_TEMP+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7286 | Missing inputs (not in hierarchy): BOILER_B_CP_CH4_FUEL_TEMP; BOILER_B_CP_ETHANE_FUEL_TEMP; BOILER_B_CP_ETHYLENE_FUEL_TEMP; BOILER_B_CP_H2_FUEL_TEMP; BOILER_B_CP_IC4_FUEL_TEMP; BOILER_B_CP_IC5_FUEL_TEMP (+13 more) | BOILER_B_CP_CH4_FUEL_TEMP; BOILER_B_CP_ETHANE_FUEL_TEMP; BOILER_B_CP_ETHYLENE_FUEL_TEMP; BOILER_B_CP_H2_FUEL_TEMP; BOILER_B_CP_IC4_FUEL_TEMP; BOILER_B_CP_IC5_FUEL_TEMP; BOILER_B_CP_NC4_FUEL_TEMP; BOILER_B_CP_NC5_FUEL_TEMP; BOILER_B_CP_PROPANE_FUEL_TEMP; BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_ETHYLENE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_MW; BOILER_B_FG_NC4_MASS_FRACTION; BOILER_B_FG_NC5_MASS_FRACTION; BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER B CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_B_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_ETHYLENE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION (+4 more) | BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_ETHYLENE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_MW; BOILER_B_FG_NC4_MASS_FRACTION; BOILER_B_FG_NC5_MASS_FRACTION; BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_B_EXCESS_AIR*(1-BOILER_B_AIR_MOISTURE)+BOILER_B_N2_FORMED+BOILER_B_CO2_FORMED | 13.4978 | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_N2_FORMED
BOILER_B_ECONOMIZER_DUTY | BOILER B ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_B_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_B_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE
BOILER_B_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER B EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_BLOWDOWN_LOSS/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_B_BLOWDOWN_LOSS; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS | BOILER_B_BLOWDOWN_LOSS; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS
BOILER_B_ENERGY_GAINED | BOILER B ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY) | 0 | Missing inputs (not in hierarchy): BOILER_B_BFW_ENERGY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_ETHANE_CO2_COMBUSTION | BOILER B ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHANE_H2O_COMBUSTION | BOILER B ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHANE_N2_COMBUSTION | BOILER B ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHYLENE_CO2_COMBUSTION | BOILER B ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*3.138 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_ETHYLENE_H2O_COMBUSTION | BOILER B ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*1.285 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_ETHYLENE_N2_COMBUSTION | BOILER B ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*11.385 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_EXCESS_AIR | BOILER B EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_B_FLUE_GAS_OXGYGEN)*((BOILER_B_N2_FORMED/28.01)+(BOILER_B_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_B_CO2_FORMED/44.01))/(20.95-BOILER_B_FLUE_GAS_OXGYGEN)) | 0.11288 | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_CORRECTED_COMBUTION_H2O_FORMED; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED; BOILER_B_CORRECTED_COMBUTION_H2O_FORMED; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_N2_FORMED
BOILER_B_FG_CH4_MASS_FRACTION | BOILER B FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_CH4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.79422 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_CH4_MASS_PERCENTAGE | BOILER B FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_B_FG_MW | 79.4217 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION
BOILER_B_FG_DENSITY | BOILER B FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_B_FG_MW/22.414 | 0.7893 | Missing inputs (not in hierarchy): BOILER_B_FG_MW | BOILER_B_FG_MW
BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER B FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_B_FG_ETHANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.026684 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_ETHANE_MASS_PERCENTAGE | BOILER B FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_B_FG_MW | 2.6684 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION
BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER B FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE | BOILER B FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_B_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION
BOILER_B_FG_FLOW_RATE | BOILER B FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_B_FUEL_GAS_FLOW/1000 | 0.17548 | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_FLOW | BOILER_B_FUEL_GAS_FLOW
BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER B FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE | BOILER B FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_B_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION
BOILER_B_FG_IC4_MASS_FRACTION | BOILER B FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_IC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.003188 | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_IC4_MASS_PERCENTAGE | BOILER B FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | 0.31885 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION
BOILER_B_FG_IC5_MASS_FRACTION | BOILER B FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_IC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.001347 | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_IC5_MASS_PERCENTAGE | BOILER B FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | 0.13466 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION
BOILER_B_FG_MW | BOILER B FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_B_FG_IC4_CONCENTRATIO | 17.6914 | Missing inputs (not in hierarchy): NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_B_FG_N2_CONCENTRATION; NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION
BOILER_B_FG_NC4_MASS_FRACTION | BOILER B FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.00378 | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NC4_MASS_PERCENTAGE | BOILER B FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | 0.37802 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION
BOILER_B_FG_NC5_MASS_FRACTION | BOILER B FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05 | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NC5_MASS_PERCENTAGE | BOILER B FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | 0.004081 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION
BOILER_B_FG_NITROGEN_MASS_FRACTION | BOILER B FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.16219 | Missing inputs (not in hierarchy): BOILER_B_FG_NITROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NITROGEN_MASS_PERCENTAGE | BOILER B FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_B_FG_MW | 16.219 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_N2_CONCENTRATION
BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER B FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_PROPANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.008553 | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_PROPANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_PROPANE_MASS_PERCENTAGE | BOILER B FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_B_FG_MW | 0.85531 | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION
BOILER_B_FLUE_GAS_MW | BOILER B FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_B_CO2_FORMED/44.01+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.96) | 27.6616 | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | 15.3658 | Missing inputs (not in hierarchy): BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_FOULING_INDEX | BOILER B FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_B_STATUS==0,0,1/BOILER_B_UA_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_UA_ECONOMIZER | BOILER_B_STATUS; BOILER_B_UA_ECONOMIZER
BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER B FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942 | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION
BOILER_B_FUEL_CONSUMPTION | BOILER B FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS
BOILER_B_FUEL_GAIN_LOSS | BOILER B FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_B_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 |  | eval_error: name 'BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_B_FUEL_GAS_CORRECTED_TPH | BOILER B FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW/1000) | 0 | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS
BOILER_B_FUEL_GAS_ENERGY_INPUT | BOILER B FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_FG_FLOW_RATE*1000*BOILER_B_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS
BOILER_B_H2O_FORMED | BOILER B H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2_H2O_COMBUSTION+BOILER_B_CH4_H2O_COMBUSTION+BOILER_B_ETHANE_H2O_COMBUSTION+BOILER_B_ETHYLENE_H2O_COMBUSTION+BOILER_B_PROPANE_H2O_COMBUSTION+BOILER_B_IC4_H2O_COMBUSTION+BOILER_B_NC4_H2O_COMBUSTION+BOILER_B_IC5_H2O_COMBUSTION+BOILER_B_NC5_H2O_COMBUSTION | 1.8586 | Missing inputs (not in hierarchy): BOILER_B_CH4_H2O_COMBUSTION; BOILER_B_ETHANE_H2O_COMBUSTION; BOILER_B_ETHYLENE_H2O_COMBUSTION; BOILER_B_H2_H2O_COMBUSTION; BOILER_B_IC4_H2O_COMBUSTION; BOILER_B_IC5_H2O_COMBUSTION (+3 more) | BOILER_B_CH4_H2O_COMBUSTION; BOILER_B_ETHANE_H2O_COMBUSTION; BOILER_B_ETHYLENE_H2O_COMBUSTION; BOILER_B_H2_H2O_COMBUSTION; BOILER_B_IC4_H2O_COMBUSTION; BOILER_B_IC5_H2O_COMBUSTION; BOILER_B_NC4_H2O_COMBUSTION; BOILER_B_NC5_H2O_COMBUSTION; BOILER_B_PROPANE_H2O_COMBUSTION
BOILER_B_H2_CO2_COMBUSTION | BOILER B H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*0 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_H2_H2O_COMBUSTION | BOILER B H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*8.937 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_H2_N2_COMBUSTION | BOILER B H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*26.407 | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER B HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_B_STACK_TEMPERATURE-15.6)))) | 0 | Missing inputs (not in hierarchy): BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_STATUS | BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER B HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,9*(BOILER_B_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_B_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_B_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_STATUS | BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER B HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_B_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0 | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_STATUS; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER B HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,0*10^-6*28*5654*BOILER_B_BOILER_LOAD) | 0 | Missing inputs (not in hierarchy): BOILER_B_STATUS | BOILER_B_STATUS
BOILER_B_HP_STEAM_ENTHALPY | BOILER B HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_B)+2.66244961166282*DESUPERHEATER_B_OUTLET_TEMPERATURE)*0.239+2) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_B | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_B
BOILER_B_IC4_CO2_COMBUSTION | BOILER B IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*3.029 | 0.009658 | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_IC4_H2O_COMBUSTION | BOILER B IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*1.55 | 0.005859 | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_IC4_N2_COMBUSTION | BOILER B IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*11.908 | 0.037969 | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_IC5_CO2_COMBUSTION | BOILER B IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*3.05 | 0.004107 | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_IC5_H2O_COMBUSTION | BOILER B IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*1.498 | 0.002017 | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_IC5_N2_COMBUSTION | BOILER B IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*11.805 | 0.015897 | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_LHV | BOILER B LHV | LBM_preprocessing_inferred_tags_main | Kcal/Kg | (BOILER_B_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_B_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_B_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_B_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_B_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_B_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_B_FG_N | 9984.6019 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_NC4_MASS_FRACTION (+3 more) | BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_NC4_MASS_FRACTION; BOILER_B_FG_NC5_MASS_FRACTION; BOILER_B_FG_NITROGEN_MASS_FRACTION; BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_LHV_DESIGN | BOILER B LHV DESIGN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_B_FG_DENSITY)/1000 | 39.6755 | Missing inputs (not in hierarchy): BOILER_B_FG_DENSITY | BOILER_B_FG_DENSITY
BOILER_B_LMTD_ECONOMIZER | BOILER B LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_B_STATUS==0,0,((673-ECONOMIZER_B_OUTLET_TEMPERATURE)-(BOILER_B_STACK_TEMPERATURE-ECONOMIZER_B_INLET_TEMPERATURE))/ln((673-ECONOMIZER_B_OUTLET_TEMPERATURE)/(-ECONOMIZER_B_INLET_TEMPERATURE+BOILER_B_STACK_TEMPERATURE))) |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE | BOILER_B_STATUS; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE
BOILER_B_MIXED_LHV_PER_KG | BOILER B MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019 | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV
BOILER_B_N2_FORMED | BOILER B N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2_N2_COMBUSTION+BOILER_B_CH4_N2_COMBUSTION+BOILER_B_ETHANE_N2_COMBUSTION+BOILER_B_ETHYLENE_N2_COMBUSTION+BOILER_B_PROPANE_N2_COMBUSTION+BOILER_B_IC4_N2_COMBUSTION+BOILER_B_NC4_N2_COMBUSTION+BOILER_B_IC5_N2_COMBUSTION+BOILER_B_NC5_N2_COMBUSTION | 11.0766 | Missing inputs (not in hierarchy): BOILER_B_CH4_N2_COMBUSTION; BOILER_B_ETHANE_N2_COMBUSTION; BOILER_B_ETHYLENE_N2_COMBUSTION; BOILER_B_H2_N2_COMBUSTION; BOILER_B_IC4_N2_COMBUSTION; BOILER_B_IC5_N2_COMBUSTION (+3 more) | BOILER_B_CH4_N2_COMBUSTION; BOILER_B_ETHANE_N2_COMBUSTION; BOILER_B_ETHYLENE_N2_COMBUSTION; BOILER_B_H2_N2_COMBUSTION; BOILER_B_IC4_N2_COMBUSTION; BOILER_B_IC5_N2_COMBUSTION; BOILER_B_NC4_N2_COMBUSTION; BOILER_B_NC5_N2_COMBUSTION; BOILER_B_PROPANE_N2_COMBUSTION
BOILER_B_NC4_CO2_COMBUSTION | BOILER B NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*3.029 | 0.01145 | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_NC4_H2O_COMBUSTION | BOILER B NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*1.55 | 0.004942 | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_NC4_N2_COMBUSTION | BOILER B NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*11.908 | 0.045014 | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_NC5_CO2_COMBUSTION | BOILER B NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*3.05 | 0.000124 | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_NC5_H2O_COMBUSTION | BOILER B NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05 | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_NC5_N2_COMBUSTION | BOILER B NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*11.805 | 0.000482 | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER B PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS
BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER B PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_B_ENERGY_GAINED; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS | BOILER_B_ENERGY_GAINED; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS
BOILER_B_PROPANE_CO2_COMBUSTION | BOILER B PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608 | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_PROPANE_H2O_COMBUSTION | BOILER B PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976 | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_PROPANE_N2_COMBUSTION | BOILER B PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327 | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_RADIATION_DUTY | BOILER B RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_ENERGY_GAINED-BOILER_B_CONVECTION_DUTY) | 0 | Missing inputs (not in hierarchy): BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS
BOILER_B_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER B RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_B_STATUS==0,0,BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) |  | Missing inputs (not in hierarchy): BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_B_STATUS | BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_B_STATUS
BOILER_B_RADIATION_LOSSES | BOILER B RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_MIXED_LHV_PER_KG*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOAD^2-0.0899*BOILER_B_BOILER_LOAD+3.2426)/100) | 0 | Missing inputs (not in hierarchy): BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS
BOILER_B_RADIATION_SECTION_EFFICIENCY | BOILER B RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS
BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER B SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_B_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_B_AIR_FUEL_MASS_RATIO | -50.7932 | Missing inputs (not in hierarchy): BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_COMBUSTION_AIR_TEMPERATURE | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_COMBUSTION_AIR_TEMPERATURE
BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER B SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0 | Missing inputs (not in hierarchy): BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_B_MAIN_FUEL_GAS_TEMPERATURE
BOILER_B_SH_DUTY | BOILER B SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_B_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_B_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | 0 | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE | BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE
BOILER_B_SH_PERFORMANCE | BOILER B SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,(BOILER_B_SH_SPECIFIC_DUTY)/0.110075721*100) | 0 | Missing inputs (not in hierarchy): BOILER_B_SH_SPECIFIC_DUTY; BOILER_B_STATUS | BOILER_B_SH_SPECIFIC_DUTY; BOILER_B_STATUS
BOILER_B_SH_SPECIFIC_DUTY | BOILER B SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_B_STATUS==0,0,BOILER_B_SH_DUTY/DESUPERHEATER_B_OUTLET_STEAM_FLOW*1000) | 0 | Missing inputs (not in hierarchy): BOILER_B_SH_DUTY; BOILER_B_STATUS | BOILER_B_SH_DUTY; BOILER_B_STATUS
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER B SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)) | 0 | Missing inputs (not in hierarchy): BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER B SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)*4.184) | 0 | Missing inputs (not in hierarchy): BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS
BOILER_B_STACK_LOSS | BOILER B STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_FLOW/(1000*1000)) | 0 | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_STACK_LOSS_CORRECTED | BOILER B STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_CORRECTED_TPH/1000) | 0 | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_STATUS | BOILER B STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_B_BOILER_LOAD>25&&DESUPERHEATER_B_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_B>40,1,0) | 0 | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS_B | HP_STEAM_PRESSURE_FROM_DS_B
BOILER_B_STEAM_DRUM_TEMP | BOILER B STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_B_STATUS==0,0,4.02521999671835*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0 | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE | BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE
BOILER_B_STEAM_TO_FIRE_DUTY_RATIO | BOILER B STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW/(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG)*1000) | 0 | Missing inputs (not in hierarchy): BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS
BOILER_B_SUPERHEATED_STEAM_BFW_RATIO | BOILER B SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_B_STATUS==0,0,(DESUPERHEATER_B_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_B)/(BOILER_B_CORRECTED_BFW_FLOW*1000)) |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; CBD_BLOW_DOWN_B | BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; CBD_BLOW_DOWN_B
BOILER_B_THERMAL_EFFICIENCY | BOILER B THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY)/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_B_BFW_ENERGY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER B TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0 | Missing inputs (not in hierarchy): BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_B_STATUS | BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_B_STATUS
BOILER_B_TOTAL_FLUE_GAS_CORRECTED | BOILER B TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_CORRECTED_TPH*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS
BOILER_B_TOTAL_FLUE_GAS_GENERATED | BOILER B TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW/1000*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS
BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER B TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_CH4_MASS_PERCENTAGE+BOILER_B_FG_ETHANE_MASS_PERCENTAGE+BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_B_FG_PROPANE_MASS_PERCENTAGE+BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_B_FG_NITROGEN_MASS_PERCENTAGE+BOILER_B_FG_IC4_MASS_PERCENTAGE+BOILER_B_FG_NC4_MASS_PERCENTAGE+BOILER_B_FG_NC5_MASS_P | 100 | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_FG_IC5_MASS_PERCENTAGE; BOILER_B_FG_NC4_MASS_PERCENTAGE; BOILER_B_FG_NC5_MASS_PERCENTAGE; BOILER_B_FG_NITROGEN_MASS_PERCENTAGE; BOILER_B_FG_PROPANE_MASS_PERCENTAGE
BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER B TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_TOTAL_MOISTURE_WITH_AIR+BOILER_B_H2O_FORMED | 1.868 | Missing inputs (not in hierarchy): BOILER_B_H2O_FORMED; BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER_B_H2O_FORMED; BOILER_B_TOTAL_MOISTURE_WITH_AIR
BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER B TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0 | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER B TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_B_MIXED_LHV_PER_KG) | 0 | Missing inputs (not in hierarchy): BOILER_B_MIXED_LHV_PER_KG; BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG; BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_B_STATUS
BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER B TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_B_RADIATION_LOSSES) | 0 | Missing inputs (not in hierarchy): BOILER_B_RADIATION_LOSSES; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_RADIATION_LOSSES; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER B TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_AIR_MOISTURE | 0.009371 | Missing inputs (not in hierarchy): BOILER_B_AIR_FUEL_MASS_RATIO | BOILER_B_AIR_FUEL_MASS_RATIO
BOILER_B_TOTAL_STEAM_ENERGY | BOILER B TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_HP_STEAM_ENTHALPY/1000000) | 0 | Missing inputs (not in hierarchy): BOILER_B_HP_STEAM_ENTHALPY; BOILER_B_STATUS | BOILER_B_HP_STEAM_ENTHALPY; BOILER_B_STATUS
BOILER_B_UA_ECONOMIZER | BOILER B UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY/BOILER_B_LMTD_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_B_ECONOMIZER_DUTY; BOILER_B_LMTD_ECONOMIZER; BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY; BOILER_B_LMTD_ECONOMIZER; BOILER_B_STATUS
BOILER_C_ACTUAL_SP_ENERGY_DELTA | BOILER C ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) |  | eval_error: name 'BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER C AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_C_AIR_CP_REF_T+BOILER_C_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044 | Missing inputs (not in hierarchy): BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER_C_CP_AT_COMBUSTION_TEMPERATURE
BOILER_C_AIR_FUEL_MASS_RATIO | BOILER C AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_EXCESS_AIR+BOILER_C_CORRECTED_COMBUSTION_AIR | 14.5295 | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_EXCESS_AIR | BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_EXCESS_AIR
BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER C AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*17.265 | 13.7122 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER C AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058 | Missing inputs (not in hierarchy): BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*14.807 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER C AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*34.344 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER C AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*15.487 | 0.04938 | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER C AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*15.353 | 0.020674 | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER C AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*15.487 | 0.058544 | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER C AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*15.353 | 0.000626 | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER C AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431 | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER C AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_C_CO2_FORMED/44.01+BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.85*BOILER_C_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_C_FLUE_GAS_MW)/BOILER_C_FLUE_GAS_MW | 0.21039 | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_MW; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_MW; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED
BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER C AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_C_FG_MW)/2 | 0.43669 | Missing inputs (not in hierarchy): BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_C_FG_MW | BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_C_FG_MW
BOILER_C_BFW_ENERGY | BOILER C BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*BOILER_C_BFW_ENTHALPY/1000) | 0 | Missing inputs (not in hierarchy): BOILER_C_BFW_ENTHALPY; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS | BOILER_C_BFW_ENTHALPY; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS
BOILER_C_BFW_ENTHALPY | BOILER C BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_C_INLET_TEMPERATURE) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_C_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_C_INLET_TEMPERATURE
BOILER_C_BLOWDOWN_LOSS | BOILER C BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,((CBD_BLOW_DOWN_C/1000)*((BOILER_C_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_C | BFW_PRESSURE_TO_BOILER; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_C
BOILER_C_BOILER_INDIRECT_EFFICIENCY | BOILER C BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_C_CALCULATED_AIRFLOW_NM3H | BOILER C CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_C_STATUS==0,0,BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0 | Missing inputs (not in hierarchy): BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS | BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS
BOILER_C_CH4_CO2_COMBUSTION | BOILER C CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*2.744 | 2.1793 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_CH4_H2O_COMBUSTION | BOILER C CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*2.246 | 1.7838 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_CH4_N2_COMBUSTION | BOILER C CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*13.275 | 10.5432 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_CO2_EMISSIONS | BOILER C CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_CO2_FORMED*BOILER_C_FUEL_GAS_CORRECTED_TPH) | 0 | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS | BOILER_C_CO2_FORMED; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS
BOILER_C_CO2_FORMED | BOILER C CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_CH4_CO2_COMBUSTION+BOILER_C_ETHANE_CO2_COMBUSTION+BOILER_C_ETHYLENE_CO2_COMBUSTION+BOILER_C_PROPANE_CO2_COMBUSTION+BOILER_C_NC4_CO2_COMBUSTION+BOILER_C_IC4_CO2_COMBUSTION+BOILER_C_NC5_CO2_COMBUSTION+BOILER_C_IC5_CO2_COMBUSTION | 2.3084 | Missing inputs (not in hierarchy): BOILER_C_CH4_CO2_COMBUSTION; BOILER_C_ETHANE_CO2_COMBUSTION; BOILER_C_ETHYLENE_CO2_COMBUSTION; BOILER_C_IC4_CO2_COMBUSTION; BOILER_C_IC5_CO2_COMBUSTION; BOILER_C_NC4_CO2_COMBUSTION (+2 more) | BOILER_C_CH4_CO2_COMBUSTION; BOILER_C_ETHANE_CO2_COMBUSTION; BOILER_C_ETHYLENE_CO2_COMBUSTION; BOILER_C_IC4_CO2_COMBUSTION; BOILER_C_IC5_CO2_COMBUSTION; BOILER_C_NC4_CO2_COMBUSTION; BOILER_C_NC5_CO2_COMBUSTION; BOILER_C_PROPANE_CO2_COMBUSTION
BOILER_C_CONVECTION_DUTY | BOILER C CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY+BOILER_C_SH_DUTY+BOILER_C_STACK_LOSS_CORRECTED) | 0 | Missing inputs (not in hierarchy): BOILER_C_ECONOMIZER_DUTY; BOILER_C_SH_DUTY; BOILER_C_STACK_LOSS_CORRECTED; BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY; BOILER_C_SH_DUTY; BOILER_C_STACK_LOSS_CORRECTED; BOILER_C_STATUS
BOILER_C_CONVECTION_SECTION_EFFICIENCY | BOILER C CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_C_CONVECTION_DUTY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS
BOILER_C_CORRECTED_BFW_FLOW | BOILER C CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_C_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-DESUPERHEATER_C_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_C))/1000) | 0 | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_C; BFW_FLOW_TO_ECONOMIZER_C; BOILER_C_STATUS; CBD_BLOW_DOWN_C | BFW_FLOW_TO_DESUPERHEATER_C; BFW_FLOW_TO_ECONOMIZER_C; BOILER_C_STATUS; CBD_BLOW_DOWN_C
BOILER_C_CORRECTED_COMBUSTION_AIR | BOILER C CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_C_AIR_MOISTURE) | 14.4151 | Missing inputs (not in hierarchy): BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_C_CORRECTED_COMBUTION_H2O_FORMED | BOILER C CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2O_FORMED+(BOILER_C_CORRECTED_COMBUSTION_AIR-BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679 | Missing inputs (not in hierarchy): BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_H2O_FORMED | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_H2O_FORMED
BOILER_C_CORRECTED_FUEL_FLOW | BOILER C CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW-((BOILER_C_FUEL_GAS_ENERGY_INPUT-(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY+BOILER_C_BLOWDOWN_LOSS+BOILER_C_STACK_LOSS+BOILER_C_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_C_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOA | 0 | Missing inputs (not in hierarchy): BOILER_C_BFW_ENERGY; BOILER_C_BLOWDOWN_LOSS; BOILER_C_FUEL_GAS_ENERGY_INPUT; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STACK_LOSS (+2 more) | BOILER_C_BFW_ENERGY; BOILER_C_BLOWDOWN_LOSS; BOILER_C_FUEL_GAS_ENERGY_INPUT; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STACK_LOSS; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER C CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS
BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER C CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9663 | Missing inputs (not in hierarchy): BOILER_C_COMBUSTION_AIR_TEMPERATURE | BOILER_C_COMBUSTION_AIR_TEMPERATURE
BOILER_C_CP_CH4_FUEL_TEMP | BOILER C CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3611 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_ETHANE_FUEL_TEMP | BOILER C CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0719 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_ETHYLENE_FUEL_TEMP | BOILER C CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6636 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_H2_FUEL_TEMP | BOILER C CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8451 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_IC4_FUEL_TEMP | BOILER C CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.104 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_IC5_FUEL_TEMP | BOILER C CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8774 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_NC4_FUEL_TEMP | BOILER C CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9243 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_NC5_FUEL_TEMP | BOILER C CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1613 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_PROPANE_FUEL_TEMP | BOILER C CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0441 | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER C CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_C_CP_H2_FUEL_TEMP+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_C_CP_CH4_FUEL_TEMP+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_C_CP_ETHYLENE_FUEL_TEMP+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7284 | Missing inputs (not in hierarchy): BOILER_C_CP_CH4_FUEL_TEMP; BOILER_C_CP_ETHANE_FUEL_TEMP; BOILER_C_CP_ETHYLENE_FUEL_TEMP; BOILER_C_CP_H2_FUEL_TEMP; BOILER_C_CP_IC4_FUEL_TEMP; BOILER_C_CP_IC5_FUEL_TEMP (+13 more) | BOILER_C_CP_CH4_FUEL_TEMP; BOILER_C_CP_ETHANE_FUEL_TEMP; BOILER_C_CP_ETHYLENE_FUEL_TEMP; BOILER_C_CP_H2_FUEL_TEMP; BOILER_C_CP_IC4_FUEL_TEMP; BOILER_C_CP_IC5_FUEL_TEMP; BOILER_C_CP_NC4_FUEL_TEMP; BOILER_C_CP_NC5_FUEL_TEMP; BOILER_C_CP_PROPANE_FUEL_TEMP; BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_ETHYLENE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_MW; BOILER_C_FG_NC4_MASS_FRACTION; BOILER_C_FG_NC5_MASS_FRACTION; BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER C CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_C_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_ETHYLENE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION (+4 more) | BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_ETHYLENE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_MW; BOILER_C_FG_NC4_MASS_FRACTION; BOILER_C_FG_NC5_MASS_FRACTION; BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_C_EXCESS_AIR*(1-BOILER_C_AIR_MOISTURE)+BOILER_C_N2_FORMED+BOILER_C_CO2_FORMED | 13.4993 | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_N2_FORMED
BOILER_C_ECONOMIZER_DUTY | BOILER C ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_C_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_C_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE
BOILER_C_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER C EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_BLOWDOWN_LOSS/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_C_BLOWDOWN_LOSS; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS | BOILER_C_BLOWDOWN_LOSS; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS
BOILER_C_ENERGY_GAINED | BOILER C ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY) | 0 | Missing inputs (not in hierarchy): BOILER_C_BFW_ENERGY; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_ETHANE_CO2_COMBUSTION | BOILER C ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHANE_H2O_COMBUSTION | BOILER C ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHANE_N2_COMBUSTION | BOILER C ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHYLENE_CO2_COMBUSTION | BOILER C ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*3.138 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_ETHYLENE_H2O_COMBUSTION | BOILER C ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*1.285 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_ETHYLENE_N2_COMBUSTION | BOILER C ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*11.385 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_EXCESS_AIR | BOILER C EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_C_FLUE_GAS_OXGYGEN)*((BOILER_C_N2_FORMED/28.01)+(BOILER_C_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_C_CO2_FORMED/44.01))/(20.95-BOILER_C_FLUE_GAS_OXGYGEN)) | 0.11442 | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_CORRECTED_COMBUTION_H2O_FORMED; BOILER_C_FLUE_GAS_OXGYGEN; BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED; BOILER_C_CORRECTED_COMBUTION_H2O_FORMED; BOILER_C_FLUE_GAS_OXGYGEN; BOILER_C_N2_FORMED
BOILER_C_FG_CH4_MASS_FRACTION | BOILER C FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_CH4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.79422 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_CH4_MASS_PERCENTAGE | BOILER C FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_C_FG_MW | 79.4217 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION
BOILER_C_FG_DENSITY | BOILER C FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_C_FG_MW/22.414 | 0.7893 | Missing inputs (not in hierarchy): BOILER_C_FG_MW | BOILER_C_FG_MW
BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER C FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_C_FG_ETHANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.026684 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_ETHANE_MASS_PERCENTAGE | BOILER C FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_C_FG_MW | 2.6684 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION
BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER C FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE | BOILER C FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_C_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION
BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER C FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE | BOILER C FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_C_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION
BOILER_C_FG_IC4_MASS_FRACTION | BOILER C FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_IC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.003188 | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_IC4_MASS_PERCENTAGE | BOILER C FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | 0.31885 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION
BOILER_C_FG_IC5_MASS_FRACTION | BOILER C FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_IC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.001347 | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_IC5_MASS_PERCENTAGE | BOILER C FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | 0.13466 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION
BOILER_C_FG_MW | BOILER C FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_C_FG_IC4_CONCENTRATIO | 17.6914 | Missing inputs (not in hierarchy): NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_C_FG_N2_CONCENTRATION; NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION
BOILER_C_FG_NC4_MASS_FRACTION | BOILER C FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.00378 | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NC4_MASS_PERCENTAGE | BOILER C FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | 0.37802 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION
BOILER_C_FG_NC5_MASS_FRACTION | BOILER C FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05 | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NC5_MASS_PERCENTAGE | BOILER C FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | 0.004081 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION
BOILER_C_FG_NITROGEN_MASS_FRACTION | BOILER C FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.16219 | Missing inputs (not in hierarchy): BOILER_C_FG_NITROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NITROGEN_MASS_PERCENTAGE | BOILER C FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_C_FG_MW | 16.219 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_N2_CONCENTRATION
BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER C FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_PROPANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.008553 | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_PROPANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_PROPANE_MASS_PERCENTAGE | BOILER C FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_C_FG_MW | 0.85531 | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION
BOILER_C_FLUE_GAS_MW | BOILER C FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_C_CO2_FORMED/44.01+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.96) | 27.6617 | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | 15.3673 | Missing inputs (not in hierarchy): BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_FOULING_INDEX | BOILER C FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_C_STATUS==0,0,1/BOILER_C_UA_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_UA_ECONOMIZER | BOILER_C_STATUS; BOILER_C_UA_ECONOMIZER
BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER C FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942 | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION
BOILER_C_FUEL_CONSUMPTION | BOILER C FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS
BOILER_C_FUEL_GAIN_LOSS | BOILER C FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_C_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 |  | eval_error: name 'BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_C_FUEL_GAS_CORRECTED_TPH | BOILER C FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW/1000) | 0 | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS
BOILER_C_FUEL_GAS_ENERGY_INPUT | BOILER C FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_FG_FLOW_RATE*1000*BOILER_C_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS
BOILER_C_H2O_FORMED | BOILER C H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2_H2O_COMBUSTION+BOILER_C_CH4_H2O_COMBUSTION+BOILER_C_ETHANE_H2O_COMBUSTION+BOILER_C_ETHYLENE_H2O_COMBUSTION+BOILER_C_PROPANE_H2O_COMBUSTION+BOILER_C_IC4_H2O_COMBUSTION+BOILER_C_NC4_H2O_COMBUSTION+BOILER_C_IC5_H2O_COMBUSTION+BOILER_C_NC5_H2O_COMBUSTION | 1.8586 | Missing inputs (not in hierarchy): BOILER_C_CH4_H2O_COMBUSTION; BOILER_C_ETHANE_H2O_COMBUSTION; BOILER_C_ETHYLENE_H2O_COMBUSTION; BOILER_C_H2_H2O_COMBUSTION; BOILER_C_IC4_H2O_COMBUSTION; BOILER_C_IC5_H2O_COMBUSTION (+3 more) | BOILER_C_CH4_H2O_COMBUSTION; BOILER_C_ETHANE_H2O_COMBUSTION; BOILER_C_ETHYLENE_H2O_COMBUSTION; BOILER_C_H2_H2O_COMBUSTION; BOILER_C_IC4_H2O_COMBUSTION; BOILER_C_IC5_H2O_COMBUSTION; BOILER_C_NC4_H2O_COMBUSTION; BOILER_C_NC5_H2O_COMBUSTION; BOILER_C_PROPANE_H2O_COMBUSTION
BOILER_C_H2_CO2_COMBUSTION | BOILER C H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*0 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_H2_H2O_COMBUSTION | BOILER C H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*8.937 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_H2_N2_COMBUSTION | BOILER C H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*26.407 | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER C HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_C_STACK_TEMPERATURE-15.6)))) | 0 | Missing inputs (not in hierarchy): BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS | BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER C HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,9*(BOILER_C_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_C_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_C_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0 | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_STATUS | BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER C HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_C_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0 | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER C HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,0*10^-6*28*5654*BOILER_C_BOILER_LOAD) | 0 | Missing inputs (not in hierarchy): BOILER_C_STATUS | BOILER_C_STATUS
BOILER_C_HP_STEAM_ENTHALPY | BOILER C HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_C)+2.66244961166282*DESUPERHEATER_C_OUTLET_TEMPERATURE)*0.239+2) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_C | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_C
BOILER_C_IC4_CO2_COMBUSTION | BOILER C IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*3.029 | 0.009658 | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_IC4_H2O_COMBUSTION | BOILER C IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*1.55 | 0.005859 | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_IC4_N2_COMBUSTION | BOILER C IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*11.908 | 0.037969 | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_IC5_CO2_COMBUSTION | BOILER C IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*3.05 | 0.004107 | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_IC5_H2O_COMBUSTION | BOILER C IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*1.498 | 0.002017 | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_IC5_N2_COMBUSTION | BOILER C IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*11.805 | 0.015897 | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_LHV | BOILER C LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_C_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_C_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_C_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_C_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_C_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_C_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_C_FG_N | 9984.6019 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_NC4_MASS_FRACTION (+3 more) | BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_NC4_MASS_FRACTION; BOILER_C_FG_NC5_MASS_FRACTION; BOILER_C_FG_NITROGEN_MASS_FRACTION; BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_LHV_DESIGEN | BOILER C LHV DESIGEN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_C_FG_DENSITY)/1000 | 39.6755 | Missing inputs (not in hierarchy): BOILER_C_FG_DENSITY | BOILER_C_FG_DENSITY
BOILER_C_LMTD_ECONOMIZER | BOILER C LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_C_STATUS==0,0,((673-ECONOMIZER_C_OUTLET_TEMPERATURE)-(BOILER_C_STACK_TEMPERATURE-ECONOMIZER_C_INLET_TEMPERATURE))/ln((673-ECONOMIZER_C_OUTLET_TEMPERATURE)/(-ECONOMIZER_C_INLET_TEMPERATURE+BOILER_C_STACK_TEMPERATURE))) |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE | BOILER_C_STATUS; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE
BOILER_C_MIXED_LHV_PER_KG | BOILER C MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019 | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV
BOILER_C_N2_FORMED | BOILER C N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2_N2_COMBUSTION+BOILER_C_CH4_N2_COMBUSTION+BOILER_C_ETHANE_N2_COMBUSTION+BOILER_C_ETHYLENE_N2_COMBUSTION+BOILER_C_PROPANE_N2_COMBUSTION+BOILER_C_IC4_N2_COMBUSTION+BOILER_C_NC4_N2_COMBUSTION+BOILER_C_IC5_N2_COMBUSTION+BOILER_C_NC5_N2_COMBUSTION | 11.0766 | Missing inputs (not in hierarchy): BOILER_C_CH4_N2_COMBUSTION; BOILER_C_ETHANE_N2_COMBUSTION; BOILER_C_ETHYLENE_N2_COMBUSTION; BOILER_C_H2_N2_COMBUSTION; BOILER_C_IC4_N2_COMBUSTION; BOILER_C_IC5_N2_COMBUSTION (+3 more) | BOILER_C_CH4_N2_COMBUSTION; BOILER_C_ETHANE_N2_COMBUSTION; BOILER_C_ETHYLENE_N2_COMBUSTION; BOILER_C_H2_N2_COMBUSTION; BOILER_C_IC4_N2_COMBUSTION; BOILER_C_IC5_N2_COMBUSTION; BOILER_C_NC4_N2_COMBUSTION; BOILER_C_NC5_N2_COMBUSTION; BOILER_C_PROPANE_N2_COMBUSTION
BOILER_C_NC4_CO2_COMBUSTION | BOILER C NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*3.029 | 0.01145 | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_NC4_H2O_COMBUSTION | BOILER C NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*1.55 | 0.004942 | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_NC4_N2_COMBUSTION | BOILER C NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*11.908 | 0.045014 | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_NC5_CO2_COMBUSTION | BOILER C NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*3.05 | 0.000124 | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_NC5_H2O_COMBUSTION | BOILER C NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05 | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_NC5_N2_COMBUSTION | BOILER C NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*11.805 | 0.000482 | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER C PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS
BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER C PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_C_ENERGY_GAINED; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS | BOILER_C_ENERGY_GAINED; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS
BOILER_C_PROPANE_CO2_COMBUSTION | BOILER C PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608 | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_PROPANE_H2O_COMBUSTION | BOILER C PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976 | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_PROPANE_N2_COMBUSTION | BOILER C PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327 | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_RADIATION_DUTY | BOILER C RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_ENERGY_GAINED-BOILER_C_CONVECTION_DUTY) | 0 | Missing inputs (not in hierarchy): BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS
BOILER_C_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER C RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_C_STATUS==0,0,BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) |  | Missing inputs (not in hierarchy): BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_C_STATUS | BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_C_STATUS
BOILER_C_RADIATION_LOSSES | BOILER C RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_MIXED_LHV_PER_KG*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOAD^2-0.0899*BOILER_C_BOILER_LOAD+3.2426)/100) | 0 | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS
BOILER_C_RADIATION_SECTION_EFFICIENCY | BOILER C RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS
BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER C SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_C_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_C_AIR_FUEL_MASS_RATIO | -50.7916 | Missing inputs (not in hierarchy): BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_COMBUSTION_AIR_TEMPERATURE | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_COMBUSTION_AIR_TEMPERATURE
BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER C SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0 | Missing inputs (not in hierarchy): BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_C_MAIN_FUEL_GAS_TEMPERATURE
BOILER_C_SH_DUTY | BOILER C SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_C_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_C_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | 0 | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE | BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE
BOILER_C_SH_PERFORMANCE | BOILER C SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,(BOILER_C_SH_SPECIFIC_DUTY)/0.110075721*100) | 0 | Missing inputs (not in hierarchy): BOILER_C_SH_SPECIFIC_DUTY; BOILER_C_STATUS | BOILER_C_SH_SPECIFIC_DUTY; BOILER_C_STATUS
BOILER_C_SH_SPECIFIC_DUTY | BOILER C SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_C_STATUS==0,0,BOILER_C_SH_DUTY/DESUPERHEATER_C_OUTLET_STEAM_FLOW*1000) | 0 | Missing inputs (not in hierarchy): BOILER_C_SH_DUTY; BOILER_C_STATUS | BOILER_C_SH_DUTY; BOILER_C_STATUS
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER C SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)) | 0 | Missing inputs (not in hierarchy): BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER C SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)*4.184) | 0 | Missing inputs (not in hierarchy): BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS
BOILER_C_STACK_LOSS | BOILER C STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_FLOW/(1000*1000)) | 0 | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_STACK_LOSS_CORRECTED | BOILER C STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_CORRECTED_TPH/1000) | 0 | Missing inputs (not in hierarchy): BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_STATUS | BOILER C STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_C_BOILER_LOAD>25&&DESUPERHEATER_C_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_C>40,1,0) | 0 | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS_C | HP_STEAM_PRESSURE_FROM_DS_C
BOILER_C_STEAM_DRUM_TEMP | BOILER C STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_C_STATUS==0,0,4.02521999671835*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0 | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE | BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE
BOILER_C_STEAM_TO_FIRE_DUTY_RATIO | BOILER C STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW/(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG)*1000) | 0 | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS
BOILER_C_SUPERHEATED_STEAM_BFW_RATIO | BOILER C SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_C_STATUS==0,0,(DESUPERHEATER_C_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_C)/(BOILER_C_CORRECTED_BFW_FLOW*1000)) |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; CBD_BLOW_DOWN_C | BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; CBD_BLOW_DOWN_C
BOILER_C_THERMAL_EFFICIENCY | BOILER C THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY)/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_C_BFW_ENERGY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER C TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0 | Missing inputs (not in hierarchy): BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_C_STATUS | BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_C_STATUS
BOILER_C_TOTAL_FLUE_GAS_CORRECTED | BOILER C TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_CORRECTED_TPH*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS
BOILER_C_TOTAL_FLUE_GAS_GENERATED | BOILER C TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW/1000*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS
BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER C TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_CH4_MASS_PERCENTAGE+BOILER_C_FG_ETHANE_MASS_PERCENTAGE+BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_C_FG_PROPANE_MASS_PERCENTAGE+BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_C_FG_NITROGEN_MASS_PERCENTAGE+BOILER_C_FG_IC4_MASS_PERCENTAGE+BOILER_C_FG_NC4_MASS_PERCENTAGE+BOILER_C_FG_NC5_MASS_P | 100 | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_FG_IC5_MASS_PERCENTAGE; BOILER_C_FG_NC4_MASS_PERCENTAGE; BOILER_C_FG_NC5_MASS_PERCENTAGE; BOILER_C_FG_NITROGEN_MASS_PERCENTAGE; BOILER_C_FG_PROPANE_MASS_PERCENTAGE
BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER C TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_TOTAL_MOISTURE_WITH_AIR+BOILER_C_H2O_FORMED | 1.868 | Missing inputs (not in hierarchy): BOILER_C_H2O_FORMED; BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER_C_H2O_FORMED; BOILER_C_TOTAL_MOISTURE_WITH_AIR
BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER C TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0 | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER C TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_C_MIXED_LHV_PER_KG) | 0 | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_C_STATUS
BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER C TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_C_RADIATION_LOSSES) | 0 | Missing inputs (not in hierarchy): BOILER_C_RADIATION_LOSSES; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_RADIATION_LOSSES; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER C TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_AIR_MOISTURE | 0.009372 | Missing inputs (not in hierarchy): BOILER_C_AIR_FUEL_MASS_RATIO | BOILER_C_AIR_FUEL_MASS_RATIO
BOILER_C_TOTAL_STEAM_ENERGY | BOILER C TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_HP_STEAM_ENTHALPY/1000000) | 0 | Missing inputs (not in hierarchy): BOILER_C_HP_STEAM_ENTHALPY; BOILER_C_STATUS | BOILER_C_HP_STEAM_ENTHALPY; BOILER_C_STATUS
BOILER_C_UA_ECONOMIZER | BOILER C UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY/BOILER_C_LMTD_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_C_ECONOMIZER_DUTY; BOILER_C_LMTD_ECONOMIZER; BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY; BOILER_C_LMTD_ECONOMIZER; BOILER_C_STATUS
BOILER_D_ACTUAL_SP_ENERGY_DELTA | BOILER D ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) |  | eval_error: name 'BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER D AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_D_AIR_CP_REF_T+BOILER_D_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044 | Missing inputs (not in hierarchy): BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER_D_CP_AT_COMBUSTION_TEMPERATURE
BOILER_D_AIR_FUEL_MASS_RATIO | BOILER D AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_EXCESS_AIR+BOILER_D_CORRECTED_COMBUSTION_AIR | 14.5272 | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_EXCESS_AIR | BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_EXCESS_AIR
BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER D AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*17.265 | 13.7122 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER D AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058 | Missing inputs (not in hierarchy): BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*14.807 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER D AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*34.344 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER D AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*15.487 | 0.04938 | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER D AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*15.353 | 0.020674 | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER D AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*15.487 | 0.058544 | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER D AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*15.353 | 0.000626 | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER D AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431 | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER D AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_D_CO2_FORMED/44.01+BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.85*BOILER_D_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_D_FLUE_GAS_MW)/BOILER_D_FLUE_GAS_MW | 0.21038 | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_MW; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_MW; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED
BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER D AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_D_FG_MW)/2 | 0.43669 | Missing inputs (not in hierarchy): BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_D_FG_MW | BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_D_FG_MW
BOILER_D_BFW_ENERGY | BOILER D BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*BOILER_D_BFW_ENTHALPY/1000) | 0 | Missing inputs (not in hierarchy): BOILER_D_BFW_ENTHALPY; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS | BOILER_D_BFW_ENTHALPY; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS
BOILER_D_BFW_ENTHALPY | BOILER D BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_D_INLET_TEMPERATURE) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_D_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_D_INLET_TEMPERATURE
BOILER_D_BLOWDOWN_LOSS | BOILER D BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,((CBD_BLOW_DOWN_D/1000)*((BOILER_D_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_D | BFW_PRESSURE_TO_BOILER; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_D
BOILER_D_BOILER_INDIRECT_EFFICIENCY | BOILER D BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_D_CALCULATED_AIRFLOW_NM3H | BOILER D CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_D_STATUS==0,0,BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0 | Missing inputs (not in hierarchy): BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS | BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS
BOILER_D_CH4_CO2_COMBUSTION | BOILER D CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*2.744 | 2.1793 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_CH4_H2O_COMBUSTION | BOILER D CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*2.246 | 1.7838 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_CH4_N2_COMBUSTION | BOILER D CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*13.275 | 10.5432 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_CO2_EMISSIONS | BOILER D CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_CO2_FORMED*BOILER_D_FUEL_GAS_CORRECTED_TPH) | 0 | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS | BOILER_D_CO2_FORMED; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS
BOILER_D_CO2_FORMED | BOILER D CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_CH4_CO2_COMBUSTION+BOILER_D_ETHANE_CO2_COMBUSTION+BOILER_D_ETHYLENE_CO2_COMBUSTION+BOILER_D_PROPANE_CO2_COMBUSTION+BOILER_D_NC4_CO2_COMBUSTION+BOILER_D_IC4_CO2_COMBUSTION+BOILER_D_NC5_CO2_COMBUSTION+BOILER_D_IC5_CO2_COMBUSTION | 2.3084 | Missing inputs (not in hierarchy): BOILER_D_CH4_CO2_COMBUSTION; BOILER_D_ETHANE_CO2_COMBUSTION; BOILER_D_ETHYLENE_CO2_COMBUSTION; BOILER_D_IC4_CO2_COMBUSTION; BOILER_D_IC5_CO2_COMBUSTION; BOILER_D_NC4_CO2_COMBUSTION (+2 more) | BOILER_D_CH4_CO2_COMBUSTION; BOILER_D_ETHANE_CO2_COMBUSTION; BOILER_D_ETHYLENE_CO2_COMBUSTION; BOILER_D_IC4_CO2_COMBUSTION; BOILER_D_IC5_CO2_COMBUSTION; BOILER_D_NC4_CO2_COMBUSTION; BOILER_D_NC5_CO2_COMBUSTION; BOILER_D_PROPANE_CO2_COMBUSTION
BOILER_D_CONVECTION_DUTY | BOILER D CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY+BOILER_D_SH_DUTY+BOILER_D_STACK_LOSS_CORRECTED) | 0 | Missing inputs (not in hierarchy): BOILER_D_ECONOMIZER_DUTY; BOILER_D_SH_DUTY; BOILER_D_STACK_LOSS_CORRECTED; BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY; BOILER_D_SH_DUTY; BOILER_D_STACK_LOSS_CORRECTED; BOILER_D_STATUS
BOILER_D_CONVECTION_SECTION_EFFICIENCY | BOILER D CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_D_CONVECTION_DUTY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS
BOILER_D_CORRECTED_BFW_FLOW | BOILER D CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_D_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-DESUPERHEATER_D_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_D))/1000) | 0 | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_D; BFW_FLOW_TO_ECONOMIZER_D; BOILER_D_STATUS; CBD_BLOW_DOWN_D | BFW_FLOW_TO_DESUPERHEATER_D; BFW_FLOW_TO_ECONOMIZER_D; BOILER_D_STATUS; CBD_BLOW_DOWN_D
BOILER_D_CORRECTED_COMBUSTION_AIR | BOILER D CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_D_AIR_MOISTURE) | 14.4151 | Missing inputs (not in hierarchy): BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_D_CORRECTED_COMBUTION_H2O_FORMED | BOILER D CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2O_FORMED+(BOILER_D_CORRECTED_COMBUSTION_AIR-BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679 | Missing inputs (not in hierarchy): BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_H2O_FORMED | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_H2O_FORMED
BOILER_D_CORRECTED_FUEL_FLOW | BOILER D CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW-((BOILER_D_FUEL_GAS_ENERGY_INPUT-(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY+BOILER_D_BLOWDOWN_LOSS+BOILER_D_STACK_LOSS+BOILER_D_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_D_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOA | 0 | Missing inputs (not in hierarchy): BOILER_D_BFW_ENERGY; BOILER_D_BLOWDOWN_LOSS; BOILER_D_FUEL_GAS_ENERGY_INPUT; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STACK_LOSS (+2 more) | BOILER_D_BFW_ENERGY; BOILER_D_BLOWDOWN_LOSS; BOILER_D_FUEL_GAS_ENERGY_INPUT; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STACK_LOSS; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER D CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS
BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER D CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9662 | Missing inputs (not in hierarchy): BOILER_D_COMBUSTION_AIR_TEMPERATURE | BOILER_D_COMBUSTION_AIR_TEMPERATURE
BOILER_D_CP_CH4_FUEL_TEMP | BOILER D CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3611 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_ETHANE_FUEL_TEMP | BOILER D CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.072 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_ETHYLENE_FUEL_TEMP | BOILER D CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6636 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_H2_FUEL_TEMP | BOILER D CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8451 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_IC4_FUEL_TEMP | BOILER D CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1042 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_IC5_FUEL_TEMP | BOILER D CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8775 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_NC4_FUEL_TEMP | BOILER D CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9244 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_NC5_FUEL_TEMP | BOILER D CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1614 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_PROPANE_FUEL_TEMP | BOILER D CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0442 | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER D CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_D_CP_H2_FUEL_TEMP+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_D_CP_CH4_FUEL_TEMP+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_D_CP_ETHYLENE_FUEL_TEMP+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7284 | Missing inputs (not in hierarchy): BOILER_D_CP_CH4_FUEL_TEMP; BOILER_D_CP_ETHANE_FUEL_TEMP; BOILER_D_CP_ETHYLENE_FUEL_TEMP; BOILER_D_CP_H2_FUEL_TEMP; BOILER_D_CP_IC4_FUEL_TEMP; BOILER_D_CP_IC5_FUEL_TEMP (+13 more) | BOILER_D_CP_CH4_FUEL_TEMP; BOILER_D_CP_ETHANE_FUEL_TEMP; BOILER_D_CP_ETHYLENE_FUEL_TEMP; BOILER_D_CP_H2_FUEL_TEMP; BOILER_D_CP_IC4_FUEL_TEMP; BOILER_D_CP_IC5_FUEL_TEMP; BOILER_D_CP_NC4_FUEL_TEMP; BOILER_D_CP_NC5_FUEL_TEMP; BOILER_D_CP_PROPANE_FUEL_TEMP; BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_ETHYLENE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_MW; BOILER_D_FG_NC4_MASS_FRACTION; BOILER_D_FG_NC5_MASS_FRACTION; BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER D CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_D_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_ETHYLENE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION (+4 more) | BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_ETHYLENE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_MW; BOILER_D_FG_NC4_MASS_FRACTION; BOILER_D_FG_NC5_MASS_FRACTION; BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_D_EXCESS_AIR*(1-BOILER_D_AIR_MOISTURE)+BOILER_D_N2_FORMED+BOILER_D_CO2_FORMED | 13.497 | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_N2_FORMED
BOILER_D_ECONOMIZER_DUTY | BOILER D ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_D_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_D_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE
BOILER_D_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER D EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_BLOWDOWN_LOSS/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_D_BLOWDOWN_LOSS; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS | BOILER_D_BLOWDOWN_LOSS; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS
BOILER_D_ENERGY_GAINED | BOILER D ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY) | 0 | Missing inputs (not in hierarchy): BOILER_D_BFW_ENERGY; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_ETHANE_CO2_COMBUSTION | BOILER D ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHANE_H2O_COMBUSTION | BOILER D ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHANE_N2_COMBUSTION | BOILER D ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHYLENE_CO2_COMBUSTION | BOILER D ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*3.138 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_ETHYLENE_H2O_COMBUSTION | BOILER D ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*1.285 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_ETHYLENE_N2_COMBUSTION | BOILER D ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*11.385 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_EXCESS_AIR | BOILER D EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_D_FLUE_GAS_OXGYGEN)*((BOILER_D_N2_FORMED/28.01)+(BOILER_D_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_D_CO2_FORMED/44.01))/(20.95-BOILER_D_FLUE_GAS_OXGYGEN)) | 0.1121 | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_CORRECTED_COMBUTION_H2O_FORMED; BOILER_D_FLUE_GAS_OXGYGEN; BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED; BOILER_D_CORRECTED_COMBUTION_H2O_FORMED; BOILER_D_FLUE_GAS_OXGYGEN; BOILER_D_N2_FORMED
BOILER_D_FG_CH4_MASS_FRACTION | BOILER D FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_CH4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.79422 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_CH4_MASS_PERCENTAGE | BOILER D FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_D_FG_MW | 79.4217 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION
BOILER_D_FG_DENSITY | BOILER D FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_D_FG_MW/22.414 | 0.7893 | Missing inputs (not in hierarchy): BOILER_D_FG_MW | BOILER_D_FG_MW
BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER D FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_D_FG_ETHANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.026684 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_ETHANE_MASS_PERCENTAGE | BOILER D FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_D_FG_MW | 2.6684 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION
BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER D FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE | BOILER D FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_D_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION
BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER D FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE | BOILER D FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_D_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION
BOILER_D_FG_IC4_MASS_FRACTION | BOILER D FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_IC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.003188 | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_IC4_MASS_PERCENTAGE | BOILER D FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | 0.31885 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION
BOILER_D_FG_IC5_MASS_FRACTION | BOILER D FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_IC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.001347 | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_IC5_MASS_PERCENTAGE | BOILER D FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | 0.13466 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION
BOILER_D_FG_MW | BOILER D FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_D_FG_IC4_CONCENTRATIO | 17.6914 | Missing inputs (not in hierarchy): NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_D_FG_N2_CONCENTRATION; NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION
BOILER_D_FG_NC4_MASS_FRACTION | BOILER D FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.00378 | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NC4_MASS_PERCENTAGE | BOILER D FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | 0.37802 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION
BOILER_D_FG_NC5_MASS_FRACTION | BOILER D FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05 | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NC5_MASS_PERCENTAGE | BOILER D FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | 0.004081 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION
BOILER_D_FG_NITROGEN_MASS_FRACTION | BOILER D FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.16219 | Missing inputs (not in hierarchy): BOILER_D_FG_NITROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NITROGEN_MASS_PERCENTAGE | BOILER D FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_D_FG_MW | 16.219 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_N2_CONCENTRATION
BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER D FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_PROPANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.008553 | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_PROPANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_PROPANE_MASS_PERCENTAGE | BOILER D FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_D_FG_MW | 0.85531 | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION
BOILER_D_FLUE_GAS_MW | BOILER D FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_D_CO2_FORMED/44.01+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.96) | 27.6615 | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | 15.365 | Missing inputs (not in hierarchy): BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_FOULING_INDEX | BOILER D FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_D_STATUS==0,0,1/BOILER_D_UA_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_UA_ECONOMIZER | BOILER_D_STATUS; BOILER_D_UA_ECONOMIZER
BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER D FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942 | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION
BOILER_D_FUEL_CONSUMPTION | BOILER D FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS
BOILER_D_FUEL_GAIN_LOSS | BOILER D FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_D_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 |  | eval_error: name 'BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_D_FUEL_GAS_CORRECTED_TPH | BOILER D FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW/1000) | 0 | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS
BOILER_D_FUEL_GAS_ENERGY_INPUT | BOILER D FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_FG_FLOW_RATE*1000*BOILER_D_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS
BOILER_D_H2O_FORMED | BOILER D H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2_H2O_COMBUSTION+BOILER_D_CH4_H2O_COMBUSTION+BOILER_D_ETHANE_H2O_COMBUSTION+BOILER_D_ETHYLENE_H2O_COMBUSTION+BOILER_D_PROPANE_H2O_COMBUSTION+BOILER_D_IC4_H2O_COMBUSTION+BOILER_D_NC4_H2O_COMBUSTION+BOILER_D_IC5_H2O_COMBUSTION+BOILER_D_NC5_H2O_COMBUSTION | 1.8586 | Missing inputs (not in hierarchy): BOILER_D_CH4_H2O_COMBUSTION; BOILER_D_ETHANE_H2O_COMBUSTION; BOILER_D_ETHYLENE_H2O_COMBUSTION; BOILER_D_H2_H2O_COMBUSTION; BOILER_D_IC4_H2O_COMBUSTION; BOILER_D_IC5_H2O_COMBUSTION (+3 more) | BOILER_D_CH4_H2O_COMBUSTION; BOILER_D_ETHANE_H2O_COMBUSTION; BOILER_D_ETHYLENE_H2O_COMBUSTION; BOILER_D_H2_H2O_COMBUSTION; BOILER_D_IC4_H2O_COMBUSTION; BOILER_D_IC5_H2O_COMBUSTION; BOILER_D_NC4_H2O_COMBUSTION; BOILER_D_NC5_H2O_COMBUSTION; BOILER_D_PROPANE_H2O_COMBUSTION
BOILER_D_H2_CO2_COMBUSTION | BOILER D H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*0 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_H2_H2O_COMBUSTION | BOILER D H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*8.937 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_H2_N2_COMBUSTION | BOILER D H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*26.407 | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER D HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_D_STACK_TEMPERATURE-15.6)))) | 0 | Missing inputs (not in hierarchy): BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS | BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER D HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,9*(BOILER_D_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_D_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_D_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0 | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_STATUS | BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER D HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_D_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0 | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER D HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,0*10^-6*28*5654*BOILER_D_BOILER_LOAD) | 0 | Missing inputs (not in hierarchy): BOILER_D_STATUS | BOILER_D_STATUS
BOILER_D_HP_STEAM_ENTHALPY | BOILER D HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_D)+2.66244961166282*DESUPERHEATER_D_OUTLET_TEMPERATURE)*0.239+2) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_D | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_D
BOILER_D_IC4_CO2_COMBUSTION | BOILER D IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*3.029 | 0.009658 | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_IC4_H2O_COMBUSTION | BOILER D IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*1.55 | 0.005859 | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_IC4_N2_COMBUSTION | BOILER D IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*11.908 | 0.037969 | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_IC5_CO2_COMBUSTION | BOILER D IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*3.05 | 0.004107 | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_IC5_H2O_COMBUSTION | BOILER D IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*1.498 | 0.002017 | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_IC5_N2_COMBUSTION | BOILER D IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*11.805 | 0.015897 | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_LHV | BOILER D LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_D_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_D_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_D_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_D_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_D_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_D_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_D_FG_N | 9984.6019 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_NC4_MASS_FRACTION (+3 more) | BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_NC4_MASS_FRACTION; BOILER_D_FG_NC5_MASS_FRACTION; BOILER_D_FG_NITROGEN_MASS_FRACTION; BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_LHV_DESIGEN | BOILER D LHV DESIGEN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_D_FG_DENSITY)/1000 | 39.6755 | Missing inputs (not in hierarchy): BOILER_D_FG_DENSITY | BOILER_D_FG_DENSITY
BOILER_D_LMTD_ECONOMIZER | BOILER D LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_D_STATUS==0,0,((673-ECONOMIZER_D_OUTLET_TEMPERATURE)-(BOILER_D_STACK_TEMPERATURE-ECONOMIZER_D_INLET_TEMPERATURE))/ln((673-ECONOMIZER_D_OUTLET_TEMPERATURE)/(-ECONOMIZER_D_INLET_TEMPERATURE+BOILER_D_STACK_TEMPERATURE))) |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE | BOILER_D_STATUS; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE
BOILER_D_MIXED_LHV_PER_KG | BOILER D MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019 | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV
BOILER_D_N2_FORMED | BOILER D N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2_N2_COMBUSTION+BOILER_D_CH4_N2_COMBUSTION+BOILER_D_ETHANE_N2_COMBUSTION+BOILER_D_ETHYLENE_N2_COMBUSTION+BOILER_D_PROPANE_N2_COMBUSTION+BOILER_D_IC4_N2_COMBUSTION+BOILER_D_NC4_N2_COMBUSTION+BOILER_D_IC5_N2_COMBUSTION+BOILER_D_NC5_N2_COMBUSTION | 11.0766 | Missing inputs (not in hierarchy): BOILER_D_CH4_N2_COMBUSTION; BOILER_D_ETHANE_N2_COMBUSTION; BOILER_D_ETHYLENE_N2_COMBUSTION; BOILER_D_H2_N2_COMBUSTION; BOILER_D_IC4_N2_COMBUSTION; BOILER_D_IC5_N2_COMBUSTION (+3 more) | BOILER_D_CH4_N2_COMBUSTION; BOILER_D_ETHANE_N2_COMBUSTION; BOILER_D_ETHYLENE_N2_COMBUSTION; BOILER_D_H2_N2_COMBUSTION; BOILER_D_IC4_N2_COMBUSTION; BOILER_D_IC5_N2_COMBUSTION; BOILER_D_NC4_N2_COMBUSTION; BOILER_D_NC5_N2_COMBUSTION; BOILER_D_PROPANE_N2_COMBUSTION
BOILER_D_NC4_CO2_COMBUSTION | BOILER D NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*3.029 | 0.01145 | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_NC4_H2O_COMBUSTION | BOILER D NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*1.55 | 0.004942 | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_NC4_N2_COMBUSTION | BOILER D NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*11.908 | 0.045014 | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_NC5_CO2_COMBUSTION | BOILER D NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*3.05 | 0.000124 | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_NC5_H2O_COMBUSTION | BOILER D NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05 | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_NC5_N2_COMBUSTION | BOILER D NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*11.805 | 0.000482 | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER D PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS
BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER D PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_D_ENERGY_GAINED; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS | BOILER_D_ENERGY_GAINED; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS
BOILER_D_PROPANE_CO2_COMBUSTION | BOILER D PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608 | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_PROPANE_H2O_COMBUSTION | BOILER D PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976 | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_PROPANE_N2_COMBUSTION | BOILER D PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327 | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_RADIATION_DUTY | BOILER D RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_ENERGY_GAINED-BOILER_D_CONVECTION_DUTY) | 0 | Missing inputs (not in hierarchy): BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS
BOILER_D_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER D RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_D_STATUS==0,0,BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) |  | Missing inputs (not in hierarchy): BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_D_STATUS | BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_D_STATUS
BOILER_D_RADIATION_LOSSES | BOILER D RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_MIXED_LHV_PER_KG*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOAD^2-0.0899*BOILER_D_BOILER_LOAD+3.2426)/100) | 0 | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS
BOILER_D_RADIATION_SECTION_EFFICIENCY | BOILER D RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS
BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER D SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_D_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_D_AIR_FUEL_MASS_RATIO | -51.4889 | Missing inputs (not in hierarchy): BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_COMBUSTION_AIR_TEMPERATURE | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_COMBUSTION_AIR_TEMPERATURE
BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER D SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0 | Missing inputs (not in hierarchy): BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_D_MAIN_FUEL_GAS_TEMPERATURE
BOILER_D_SH_DUTY | BOILER D SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_D_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_D_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | 0 | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE | BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE
BOILER_D_SH_PERFORMANCE | BOILER D SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,(BOILER_D_SH_SPECIFIC_DUTY)/0.110075721*100) | 0 | Missing inputs (not in hierarchy): BOILER_D_SH_SPECIFIC_DUTY; BOILER_D_STATUS | BOILER_D_SH_SPECIFIC_DUTY; BOILER_D_STATUS
BOILER_D_SH_SPECIFIC_DUTY | BOILER D SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_D_STATUS==0,0,BOILER_D_SH_DUTY/DESUPERHEATER_D_OUTLET_STEAM_FLOW*1000) | 0 | Missing inputs (not in hierarchy): BOILER_D_SH_DUTY; BOILER_D_STATUS | BOILER_D_SH_DUTY; BOILER_D_STATUS
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER D SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)) | 0 | Missing inputs (not in hierarchy): BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER D SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)*4.184) | 0 | Missing inputs (not in hierarchy): BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS
BOILER_D_STACK_LOSS | BOILER D STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_FLOW/(1000*1000)) | 0 | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_STACK_LOSS_CORRECTED | BOILER D STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_CORRECTED_TPH/1000) | 0 | Missing inputs (not in hierarchy): BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_STATUS | BOILER D STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_D_BOILER_LOAD>25&&DESUPERHEATER_D_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_D>40,1,0) | 0 | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS_D | HP_STEAM_PRESSURE_FROM_DS_D
BOILER_D_STEAM_DRUM_TEMP | BOILER D STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_D_STATUS==0,0,4.02521999671835*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0 | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE | BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE
BOILER_D_STEAM_TO_FIRE_DUTY_RATIO | BOILER D STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW/(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG)*1000) | 0 | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS
BOILER_D_SUPERHEATED_STEAM_BFW_RATIO | BOILER D SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_D_STATUS==0,0,(DESUPERHEATER_D_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_D)/(BOILER_D_CORRECTED_BFW_FLOW*1000)) |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; CBD_BLOW_DOWN_D | BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; CBD_BLOW_DOWN_D
BOILER_D_THERMAL_EFFICIENCY | BOILER D THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY)/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_D_BFW_ENERGY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER D TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0 | Missing inputs (not in hierarchy): BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_D_STATUS | BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_D_STATUS
BOILER_D_TOTAL_FLUE_GAS_CORRECTED | BOILER D TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_CORRECTED_TPH*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS
BOILER_D_TOTAL_FLUE_GAS_GENERATED | BOILER D TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW/1000*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS
BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER D TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_CH4_MASS_PERCENTAGE+BOILER_D_FG_ETHANE_MASS_PERCENTAGE+BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_D_FG_PROPANE_MASS_PERCENTAGE+BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_D_FG_NITROGEN_MASS_PERCENTAGE+BOILER_D_FG_IC4_MASS_PERCENTAGE+BOILER_D_FG_NC4_MASS_PERCENTAGE+BOILER_D_FG_NC5_MASS_P | 100 | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_FG_IC5_MASS_PERCENTAGE; BOILER_D_FG_NC4_MASS_PERCENTAGE; BOILER_D_FG_NC5_MASS_PERCENTAGE; BOILER_D_FG_NITROGEN_MASS_PERCENTAGE; BOILER_D_FG_PROPANE_MASS_PERCENTAGE
BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER D TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_TOTAL_MOISTURE_WITH_AIR+BOILER_D_H2O_FORMED | 1.868 | Missing inputs (not in hierarchy): BOILER_D_H2O_FORMED; BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER_D_H2O_FORMED; BOILER_D_TOTAL_MOISTURE_WITH_AIR
BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER D TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0 | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER D TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_D_MIXED_LHV_PER_KG) | 0 | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_D_STATUS
BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER D TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_D_RADIATION_LOSSES) | 0 | Missing inputs (not in hierarchy): BOILER_D_RADIATION_LOSSES; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_RADIATION_LOSSES; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER D TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_AIR_MOISTURE | 0.009371 | Missing inputs (not in hierarchy): BOILER_D_AIR_FUEL_MASS_RATIO | BOILER_D_AIR_FUEL_MASS_RATIO
BOILER_D_TOTAL_STEAM_ENERGY | BOILER D TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_HP_STEAM_ENTHALPY/1000000) | 0 | Missing inputs (not in hierarchy): BOILER_D_HP_STEAM_ENTHALPY; BOILER_D_STATUS | BOILER_D_HP_STEAM_ENTHALPY; BOILER_D_STATUS
BOILER_D_UA_ECONOMIZER | BOILER D UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY/BOILER_D_LMTD_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_D_ECONOMIZER_DUTY; BOILER_D_LMTD_ECONOMIZER; BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY; BOILER_D_LMTD_ECONOMIZER; BOILER_D_STATUS
BOILER_E_ACTUAL_SP_ENERGY_DELTA | BOILER E ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) |  | eval_error: name 'BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER E AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_E_AIR_CP_REF_T+BOILER_E_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044 | Missing inputs (not in hierarchy): BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER_E_CP_AT_COMBUSTION_TEMPERATURE
BOILER_E_AIR_FUEL_MASS_RATIO | BOILER E AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_EXCESS_AIR+BOILER_E_CORRECTED_COMBUSTION_AIR | 14.5458 | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_EXCESS_AIR | BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_EXCESS_AIR
BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER E AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*17.265 | 13.7122 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER E AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058 | Missing inputs (not in hierarchy): BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011 | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*14.807 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER E AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*34.344 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER E AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*15.487 | 0.04938 | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER E AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*15.353 | 0.020674 | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER E AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*15.487 | 0.058544 | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER E AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*15.353 | 0.000626 | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER E AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431 | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER E AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_E_CO2_FORMED/44.01+BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.85*BOILER_E_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_E_FLUE_GAS_MW)/BOILER_E_FLUE_GAS_MW | 0.21045 | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_MW; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_MW; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED
BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER E AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_E_FG_MW)/2 | 0.43677 | Missing inputs (not in hierarchy): BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_E_FG_MW | BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_E_FG_MW
BOILER_E_BFW_ENERGY | BOILER E BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*BOILER_E_BFW_ENTHALPY/1000) | 0 | Missing inputs (not in hierarchy): BOILER_E_BFW_ENTHALPY; BOILER_E_CORRECTED_BFW_FLOW | BOILER_E_BFW_ENTHALPY; BOILER_E_CORRECTED_BFW_FLOW
BOILER_E_BFW_ENTHALPY | BOILER E BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_E_INLET_TEMPERATURE) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_E_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_E_INLET_TEMPERATURE
BOILER_E_BLOWDOWN_LOSS | BOILER E BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,((CBD_BLOW_DOWN_E/1000)*((BOILER_E_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_E_STEAM_DRUM_TEMP*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_E_STEAM_DRUM_TEMP*4.22416911685416-3.01717714574329)*0.2390006))/1000) | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; CBD_BLOW_DOWN_E | BFW_PRESSURE_TO_BOILER; CBD_BLOW_DOWN_E
BOILER_E_BOILER_INDIRECT_EFFICIENCY | BOILER E BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) |  | Missing inputs (not in hierarchy): BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_E_CALCULATED_AIRFLOW_NM3H | BOILER E CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_E_STATUS==0,0,BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0 | Missing inputs (not in hierarchy): BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_CORRECTED_FUEL_FLOW
BOILER_E_CH4_CO2_COMBUSTION | BOILER E CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*2.744 | 2.1793 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_CH4_H2O_COMBUSTION | BOILER E CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*2.246 | 1.7838 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_CH4_N2_COMBUSTION | BOILER E CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*13.275 | 10.5432 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_CO2_EMISSIONS | BOILER E CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_CO2_FORMED*BOILER_E_FUEL_GAS_CORRECTED_TPH) | 0 | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_CO2_FORMED; BOILER_E_FUEL_GAS_CORRECTED_TPH
BOILER_E_CO2_FORMED | BOILER E CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_CH4_CO2_COMBUSTION+BOILER_E_ETHANE_CO2_COMBUSTION+BOILER_E_ETHYLENE_CO2_COMBUSTION+BOILER_E_PROPANE_CO2_COMBUSTION+BOILER_E_NC4_CO2_COMBUSTION+BOILER_E_IC4_CO2_COMBUSTION+BOILER_E_NC5_CO2_COMBUSTION+BOILER_E_IC5_CO2_COMBUSTION | 2.3084 | Missing inputs (not in hierarchy): BOILER_E_CH4_CO2_COMBUSTION; BOILER_E_ETHANE_CO2_COMBUSTION; BOILER_E_ETHYLENE_CO2_COMBUSTION; BOILER_E_IC4_CO2_COMBUSTION; BOILER_E_IC5_CO2_COMBUSTION; BOILER_E_NC4_CO2_COMBUSTION (+2 more) | BOILER_E_CH4_CO2_COMBUSTION; BOILER_E_ETHANE_CO2_COMBUSTION; BOILER_E_ETHYLENE_CO2_COMBUSTION; BOILER_E_IC4_CO2_COMBUSTION; BOILER_E_IC5_CO2_COMBUSTION; BOILER_E_NC4_CO2_COMBUSTION; BOILER_E_NC5_CO2_COMBUSTION; BOILER_E_PROPANE_CO2_COMBUSTION
BOILER_E_CONVECTION_DUTY | BOILER E CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY+BOILER_E_SH_DUTY+BOILER_E_STACK_LOSS_CORRECTED) | 0 | Missing inputs (not in hierarchy): BOILER_E_ECONOMIZER_DUTY; BOILER_E_STACK_LOSS_CORRECTED | BOILER_E_ECONOMIZER_DUTY; BOILER_E_STACK_LOSS_CORRECTED
BOILER_E_CONVECTION_SECTION_EFFICIENCY | BOILER E CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_E_CONVECTION_DUTY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_CONVECTION_DUTY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
BOILER_E_CORRECTED_BFW_FLOW | BOILER E CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_E_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-DESUPERHEATER_E_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_E))/1000) | 0 | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_E; BFW_FLOW_TO_ECONOMIZER_E; CBD_BLOW_DOWN_E | BFW_FLOW_TO_DESUPERHEATER_E; BFW_FLOW_TO_ECONOMIZER_E; CBD_BLOW_DOWN_E
BOILER_E_CORRECTED_COMBUSTION_AIR | BOILER E CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_E_AIR_MOISTURE) | 14.4151 | Missing inputs (not in hierarchy): BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_E_CORRECTED_COMBUTION_H2O_FORMED | BOILER E CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2O_FORMED+(BOILER_E_CORRECTED_COMBUSTION_AIR-BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679 | Missing inputs (not in hierarchy): BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_H2O_FORMED | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_H2O_FORMED
BOILER_E_CORRECTED_FUEL_FLOW | BOILER E CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295-((BOILER_E_FUEL_GAS_ENERGY_INPUT-(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY+BOILER_E_BLOWDOWN_LOSS+BOILER_E_STACK_LOSS+BOILER_E_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_E_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOIL | 0 | Missing inputs (not in hierarchy): BOILER_E_BFW_ENERGY; BOILER_E_BLOWDOWN_LOSS; BOILER_E_FUEL_GAS_ENERGY_INPUT; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_E_MIXED_LHV_PER_KG; BOILER_E_STACK_LOSS (+1 more) | BOILER_E_BFW_ENERGY; BOILER_E_BLOWDOWN_LOSS; BOILER_E_FUEL_GAS_ENERGY_INPUT; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_E_MIXED_LHV_PER_KG; BOILER_E_STACK_LOSS; BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER E CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG
BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER E CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)-9.647459*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2+16.63537*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^3+(0.000117/((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_COMBUSTION_AIR_TEM | 6.9665 | Missing inputs (not in hierarchy): BOILER_E_COMBUSTION_AIR_TEMP | BOILER_E_COMBUSTION_AIR_TEMP
BOILER_E_CP_CH4_FUEL_TEMP | BOILER E CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3641 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_ETHANE_FUEL_TEMP | BOILER E CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0902 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_ETHYLENE_FUEL_TEMP | BOILER E CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6778 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_H2_FUEL_TEMP | BOILER E CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8465 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_IC4_FUEL_TEMP | BOILER E CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1642 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_IC5_FUEL_TEMP | BOILER E CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.9245 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_NC4_FUEL_TEMP | BOILER E CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9597 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_NC5_FUEL_TEMP | BOILER E CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.2004 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_PROPANE_FUEL_TEMP | BOILER E CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0717 | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER E CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_E_CP_H2_FUEL_TEMP+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_E_CP_CH4_FUEL_TEMP+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_E_CP_ETHYLENE_FUEL_TEMP+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7312 | Missing inputs (not in hierarchy): BOILER_E_CP_CH4_FUEL_TEMP; BOILER_E_CP_ETHANE_FUEL_TEMP; BOILER_E_CP_ETHYLENE_FUEL_TEMP; BOILER_E_CP_H2_FUEL_TEMP; BOILER_E_CP_IC4_FUEL_TEMP; BOILER_E_CP_IC5_FUEL_TEMP (+13 more) | BOILER_E_CP_CH4_FUEL_TEMP; BOILER_E_CP_ETHANE_FUEL_TEMP; BOILER_E_CP_ETHYLENE_FUEL_TEMP; BOILER_E_CP_H2_FUEL_TEMP; BOILER_E_CP_IC4_FUEL_TEMP; BOILER_E_CP_IC5_FUEL_TEMP; BOILER_E_CP_NC4_FUEL_TEMP; BOILER_E_CP_NC5_FUEL_TEMP; BOILER_E_CP_PROPANE_FUEL_TEMP; BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_ETHYLENE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_MW; BOILER_E_FG_NC4_MASS_FRACTION; BOILER_E_FG_NC5_MASS_FRACTION; BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER E CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_E_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_ETHYLENE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION (+4 more) | BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_ETHYLENE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_MW; BOILER_E_FG_NC4_MASS_FRACTION; BOILER_E_FG_NC5_MASS_FRACTION; BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_E_EXCESS_AIR*(1-BOILER_E_AIR_MOISTURE)+BOILER_E_N2_FORMED+BOILER_E_CO2_FORMED | 13.5156 | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_N2_FORMED
BOILER_E_ECONOMIZER_DUTY | BOILER E ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_E_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_E_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0 | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_E_CORRECTED_BFW_FLOW; ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_E_CORRECTED_BFW_FLOW; ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE
BOILER_E_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER E EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_BLOWDOWN_LOSS/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_E_BLOWDOWN_LOSS; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_BLOWDOWN_LOSS; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
BOILER_E_ENERGY_GAINED | BOILER E ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY) | 0 | Missing inputs (not in hierarchy): BOILER_E_BFW_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_ETHANE_CO2_COMBUSTION | BOILER E ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHANE_H2O_COMBUSTION | BOILER E ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHANE_N2_COMBUSTION | BOILER E ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHYLENE_CO2_COMBUSTION | BOILER E ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*3.138 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_ETHYLENE_H2O_COMBUSTION | BOILER E ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*1.285 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_ETHYLENE_N2_COMBUSTION | BOILER E ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*11.385 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_EXCESS_AIR | BOILER E EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_E_FLUE_GAS_OXGYGEN_NEW)*((BOILER_E_N2_FORMED/28.01)+(BOILER_E_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_E_CO2_FORMED/44.01))/(20.95-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | 0.13068 | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_CORRECTED_COMBUTION_H2O_FORMED; BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED; BOILER_E_CORRECTED_COMBUTION_H2O_FORMED; BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_N2_FORMED
BOILER_E_FG_CH4_MASS_FRACTION | BOILER E FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_CH4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.79422 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_CH4_MASS_PERCENTAGE | BOILER E FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_E_FG_MW | 79.4217 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION
BOILER_E_FG_DENSITY | BOILER E FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_E_FG_MW/22.414 | 0.7893 | Missing inputs (not in hierarchy): BOILER_E_FG_MW | BOILER_E_FG_MW
BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER E FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_E_FG_ETHANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.026684 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_ETHANE_MASS_PERCENTAGE | BOILER E FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_E_FG_MW | 2.6684 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION
BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER E FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE | BOILER E FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_E_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION
BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER E FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE | BOILER E FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_E_FG_MW | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION
BOILER_E_FG_IC4_MASS_FRACTION | BOILER E FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_IC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.003188 | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_IC4_MASS_PERCENTAGE | BOILER E FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | 0.31885 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION
BOILER_E_FG_IC5_MASS_FRACTION | BOILER E FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_IC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.001347 | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_IC5_MASS_PERCENTAGE | BOILER E FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | 0.13466 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION
BOILER_E_FG_MW | BOILER E FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_E_FG_IC4_CONCENTRATIO | 17.6914 | Missing inputs (not in hierarchy): NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_E_FG_N2_CONCENTRATION; NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION
BOILER_E_FG_NC4_MASS_FRACTION | BOILER E FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.00378 | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NC4_MASS_PERCENTAGE | BOILER E FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | 0.37802 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION
BOILER_E_FG_NC5_MASS_FRACTION | BOILER E FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05 | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NC5_MASS_PERCENTAGE | BOILER E FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | 0.004081 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION
BOILER_E_FG_NITROGEN_MASS_FRACTION | BOILER E FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.16219 | Missing inputs (not in hierarchy): BOILER_E_FG_NITROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NITROGEN_MASS_PERCENTAGE | BOILER E FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_E_FG_MW | 16.219 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_N2_CONCENTRATION
BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER E FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_PROPANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.008553 | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_PROPANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_PROPANE_MASS_PERCENTAGE | BOILER E FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_E_FG_MW | 0.85531 | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION
BOILER_E_FLUE_GAS_MW | BOILER E FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_E_CO2_FORMED/44.01+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.96) | 27.663 | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | 15.3836 | Missing inputs (not in hierarchy): BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_FOULING_INDEX | BOILER E FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_E_STATUS==0,0,1/BOILER_E_UA_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_E_UA_ECONOMIZER | BOILER_E_UA_ECONOMIZER
BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER E FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942 | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION
BOILER_E_FUEL_CONSUMPTION | BOILER E FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG
BOILER_E_FUEL_GAIN_LOSS | BOILER E FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_E_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 |  | eval_error: name 'BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER E FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW/1000) | 0 | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_CORRECTED_FUEL_FLOW
BOILER_E_FUEL_GAS_ENERGY_INPUT | BOILER E FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_FG_FLOW_RATE*1000*BOILER_E_MIXED_LHV_PER_KG/10^6) | 0 | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
BOILER_E_H2O_FORMED | BOILER E H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2_H2O_COMBUSTION+BOILER_E_CH4_H2O_COMBUSTION+BOILER_E_ETHANE_H2O_COMBUSTION+BOILER_E_ETHYLENE_H2O_COMBUSTION+BOILER_E_PROPANE_H2O_COMBUSTION+BOILER_E_IC4_H2O_COMBUSTION+BOILER_E_NC4_H2O_COMBUSTION+BOILER_E_IC5_H2O_COMBUSTION+BOILER_E_NC5_H2O_COMBUSTION | 1.8586 | Missing inputs (not in hierarchy): BOILER_E_CH4_H2O_COMBUSTION; BOILER_E_ETHANE_H2O_COMBUSTION; BOILER_E_ETHYLENE_H2O_COMBUSTION; BOILER_E_H2_H2O_COMBUSTION; BOILER_E_IC4_H2O_COMBUSTION; BOILER_E_IC5_H2O_COMBUSTION (+3 more) | BOILER_E_CH4_H2O_COMBUSTION; BOILER_E_ETHANE_H2O_COMBUSTION; BOILER_E_ETHYLENE_H2O_COMBUSTION; BOILER_E_H2_H2O_COMBUSTION; BOILER_E_IC4_H2O_COMBUSTION; BOILER_E_IC5_H2O_COMBUSTION; BOILER_E_NC4_H2O_COMBUSTION; BOILER_E_NC5_H2O_COMBUSTION; BOILER_E_PROPANE_H2O_COMBUSTION
BOILER_E_H2_CO2_COMBUSTION | BOILER E H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*0 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_H2_H2O_COMBUSTION | BOILER E H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*8.937 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_H2_N2_COMBUSTION | BOILER E H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*26.407 | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER E HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_E_STACK_TEMPERATURE-15.6)))) | 0 | Missing inputs (not in hierarchy): BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO
BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER E HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,9*(BOILER_E_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_E_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_E_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0 | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER E HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_E_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0 | Missing inputs (not in hierarchy): BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_HP_STEAM_ENTHALPY | BOILER E HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_E)+2.66244961166282*DESUPERHEATER_E_OUTLET_TEMPERATURE)*0.239+2) | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS | BOILER_A_STATUS
BOILER_E_IC4_CO2_COMBUSTION | BOILER E IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*3.029 | 0.009658 | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_IC4_H2O_COMBUSTION | BOILER E IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*1.55 | 0.005859 | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_IC4_N2_COMBUSTION | BOILER E IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*11.908 | 0.037969 | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_IC5_CO2_COMBUSTION | BOILER E IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*3.05 | 0.004107 | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_IC5_H2O_COMBUSTION | BOILER E IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*1.498 | 0.002017 | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_IC5_N2_COMBUSTION | BOILER E IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*11.805 | 0.015897 | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_LHV | BOILER E LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_E_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_E_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_E_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_E_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_E_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_E_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_E_FG_N | 9984.6019 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_NC4_MASS_FRACTION (+3 more) | BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_NC4_MASS_FRACTION; BOILER_E_FG_NC5_MASS_FRACTION; BOILER_E_FG_NITROGEN_MASS_FRACTION; BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_LHV_DESIGN | BOILER E LHV DESIGN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_E_FG_DENSITY)/1000 | 39.6755 | Missing inputs (not in hierarchy): BOILER_E_FG_DENSITY | BOILER_E_FG_DENSITY
BOILER_E_LMTD_ECONOMIZER | BOILER E LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_E_STATUS==0,0,((673-ECONOMIZER_E_OUTLET_TEMPERATURE)-(BOILER_E_STACK_TEMPERATURE-ECONOMIZER_E_INLET_TEMPERATURE))/ln((673-ECONOMIZER_E_OUTLET_TEMPERATURE)/(-ECONOMIZER_E_INLET_TEMPERATURE+BOILER_E_STACK_TEMPERATURE))) |  | Missing inputs (not in hierarchy): ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE | ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE
BOILER_E_MIXED_LHV_PER_KG | BOILER E MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | Kcal/kg | (BOILER_LHV) | 9984.6019 | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV
BOILER_E_N2_FORMED | BOILER E N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2_N2_COMBUSTION+BOILER_E_CH4_N2_COMBUSTION+BOILER_E_ETHANE_N2_COMBUSTION+BOILER_E_ETHYLENE_N2_COMBUSTION+BOILER_E_PROPANE_N2_COMBUSTION+BOILER_E_IC4_N2_COMBUSTION+BOILER_E_NC4_N2_COMBUSTION+BOILER_E_IC5_N2_COMBUSTION+BOILER_E_NC5_N2_COMBUSTION | 11.0766 | Missing inputs (not in hierarchy): BOILER_E_CH4_N2_COMBUSTION; BOILER_E_ETHANE_N2_COMBUSTION; BOILER_E_ETHYLENE_N2_COMBUSTION; BOILER_E_H2_N2_COMBUSTION; BOILER_E_IC4_N2_COMBUSTION; BOILER_E_IC5_N2_COMBUSTION (+3 more) | BOILER_E_CH4_N2_COMBUSTION; BOILER_E_ETHANE_N2_COMBUSTION; BOILER_E_ETHYLENE_N2_COMBUSTION; BOILER_E_H2_N2_COMBUSTION; BOILER_E_IC4_N2_COMBUSTION; BOILER_E_IC5_N2_COMBUSTION; BOILER_E_NC4_N2_COMBUSTION; BOILER_E_NC5_N2_COMBUSTION; BOILER_E_PROPANE_N2_COMBUSTION
BOILER_E_NC4_CO2_COMBUSTION | BOILER E NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*3.029 | 0.01145 | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_NC4_H2O_COMBUSTION | BOILER E NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*1.55 | 0.004942 | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_NC4_N2_COMBUSTION | BOILER E NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*11.908 | 0.045014 | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_NC5_CO2_COMBUSTION | BOILER E NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*3.05 | 0.000124 | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_NC5_H2O_COMBUSTION | BOILER E NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05 | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_NC5_N2_COMBUSTION | BOILER E NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*11.805 | 0.000482 | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER E PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED
BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER E PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_ENERGY_GAINED*100) |  | Missing inputs (not in hierarchy): BOILER_E_ENERGY_GAINED; BOILER_E_RADIATION_DUTY | BOILER_E_ENERGY_GAINED; BOILER_E_RADIATION_DUTY
BOILER_E_PROPANE_CO2_COMBUSTION | BOILER E PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608 | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_PROPANE_H2O_COMBUSTION | BOILER E PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976 | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_PROPANE_N2_COMBUSTION | BOILER E PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327 | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_RADIATION_DUTY | BOILER E RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_ENERGY_GAINED-BOILER_E_CONVECTION_DUTY) | 0 | Missing inputs (not in hierarchy): BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED
BOILER_E_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER E RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_E_STATUS==0,0,BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) |  | Missing inputs (not in hierarchy): BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION
BOILER_E_RADIATION_LOSSES | BOILER E RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_MIXED_LHV_PER_KG*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOILER_LOAD^2-0.0899*BOILER_E_BOILER_LOAD+3.2426)/100) | 0 | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
BOILER_E_RADIATION_SECTION_EFFICIENCY | BOILER E RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_RADIATION_DUTY | BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_RADIATION_DUTY
BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER E SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_E_COMBUSTION_AIR_TEMP-15.6)*BOILER_E_AIR_FUEL_MASS_RATIO | -48.2191 | Missing inputs (not in hierarchy): BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_COMBUSTION_AIR_TEMP | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_COMBUSTION_AIR_TEMP
BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER E SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0 | Missing inputs (not in hierarchy): BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_E_MAIN_FUEL_GAS_TEMPERATURE
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER E SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)) | 0 | Missing inputs (not in hierarchy): BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER E SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)*4.184) | 0 | Missing inputs (not in hierarchy): BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION
BOILER_E_STACK_LOSS | BOILER E STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_FLOW/1.295/(1000*1000)) | 0 | Missing inputs (not in hierarchy): BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_STACK_LOSS_CORRECTED | BOILER E STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_CORRECTED_TPH/1000) | 0 | Missing inputs (not in hierarchy): BOILER_E_FUEL_GAS_CORRECTED_TPH; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_FUEL_GAS_CORRECTED_TPH; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_STEAM_TO_FIRE_DUTY_RATIO | BOILER E STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | KG/ KCAL | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW/(BOILER_E_FG_FLOW_RATE*BOILER_E_MIXED_LHV_PER_KG)*1000) | 0 | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER E SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_E_STATUS==0,0,(DESUPERHEATER_E_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_E)/(BOILER_E_CORRECTED_BFW_FLOW*1000)) |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_BFW_FLOW; CBD_BLOW_DOWN_E | BOILER_E_CORRECTED_BFW_FLOW; CBD_BLOW_DOWN_E
BOILER_E_THERMAL_EFFICIENCY | BOILER E THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY)/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) |  | Missing inputs (not in hierarchy): BOILER_E_BFW_ENERGY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER E TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0 | Missing inputs (not in hierarchy): BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3
BOILER_E_TOTAL_FLUE_GAS_CORRECTED | BOILER E TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_CORRECTED_TPH*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_FUEL_GAS_CORRECTED_TPH
BOILER_E_TOTAL_FLUE_GAS_GENERATED | BOILER E TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295/1000*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0 | Missing inputs (not in hierarchy): BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO
BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER E TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_CH4_MASS_PERCENTAGE+BOILER_E_FG_ETHANE_MASS_PERCENTAGE+BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_E_FG_PROPANE_MASS_PERCENTAGE+BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_E_FG_NITROGEN_MASS_PERCENTAGE+BOILER_E_FG_IC4_MASS_PERCENTAGE+BOILER_E_FG_NC4_MASS_PERCENTAGE+BOILER_E_FG_NC5_MASS_P | 100 | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_FG_IC5_MASS_PERCENTAGE; BOILER_E_FG_NC4_MASS_PERCENTAGE; BOILER_E_FG_NC5_MASS_PERCENTAGE; BOILER_E_FG_NITROGEN_MASS_PERCENTAGE; BOILER_E_FG_PROPANE_MASS_PERCENTAGE
BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER E TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_TOTAL_MOISTURE_WITH_AIR+BOILER_E_H2O_FORMED | 1.868 | Missing inputs (not in hierarchy): BOILER_E_H2O_FORMED; BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER_E_H2O_FORMED; BOILER_E_TOTAL_MOISTURE_WITH_AIR
BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER E TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0 | Missing inputs (not in hierarchy): BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER E TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_E_MIXED_LHV_PER_KG) | 0 | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG; BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER_E_MIXED_LHV_PER_KG; BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL
BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER E TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_E_RADIATION_LOSSES) | 0 | Missing inputs (not in hierarchy): BOILER_E_RADIATION_LOSSES; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_RADIATION_LOSSES; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER E TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_AIR_MOISTURE | 0.009383 | Missing inputs (not in hierarchy): BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_E_AIR_FUEL_MASS_RATIO
BOILER_E_TOTAL_STEAM_ENERGY | BOILER E TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_HP_STEAM_ENTHALPY/1000000) | 0 | Missing inputs (not in hierarchy): BOILER_E_HP_STEAM_ENTHALPY | BOILER_E_HP_STEAM_ENTHALPY
BOILER_E_UA_ECONOMIZER | BOILER E UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY/BOILER_E_LMTD_ECONOMIZER) |  | Missing inputs (not in hierarchy): BOILER_E_ECONOMIZER_DUTY; BOILER_E_LMTD_ECONOMIZER | BOILER_E_ECONOMIZER_DUTY; BOILER_E_LMTD_ECONOMIZER
BOILER_FG_CH4_CONCENTRATION | BOILER FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CH4_CONCENTRATION_ARRAZI,87.548) | 87.548 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_CO2_CONCENTRATION | BOILER FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CO2_CONCENTRATION_ARRAZI,0) | 0 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_ETHANE_CONCENTRATION | BOILER FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_ETHANE_CONCENTRATION_ARRAZI,1.569) | 1.569 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_HYDROGEN_CONCENTRATION | BOILER FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,0,0) | 0 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_IC4_CONCENTRATION | BOILER FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC4_CONCENTRATION_ARRAZI,.097) | 0.097 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_IC5_CONCENTRATION | BOILER FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC5_CONCENTRATION_ARRAZI,.033) | 0.033 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_N2_CONCENTRATION | BOILER FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_N2_CONCENTRATION_ARRAZI,10.236) | 10.236 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_NC4_CONCENTRATION | BOILER FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC4_CONCENTRATION_ARRAZI,.115) | 0.115 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_NC5_CONCENTRATION | BOILER FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC5_CONCENTRATION_ARRAZI,.001) | 0.001 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_PROPANE_CONCENTRATION | BOILER FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_PROPANE_CONCENTRATION_ARRAZI,.343) | 0.343 | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_LHV | BOILER LHV | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | Kcal/Kg | (BOILER_A_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_A_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_A_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_A_FG_ETHYLENE_MASS_FRACTION*LHV_C2H4_ETHYLENE+BOILER_A_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_A_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPAN | 9984.6019 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION (+4 more) | BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION; BOILER_A_FG_NC4_MASS_FRACTION; BOILER_A_FG_NC5_MASS_FRACTION; BOILER_A_FG_NITROGEN_MASS_FRACTION; BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_OVERALL_EFFICIENCY | BOILER OVERALL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | (BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_BOILER_INDIRECT_EFFICIENCY*BOILER_A_STATUS+BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_BOILER_INDIRECT_EFFICIENCY*BOILER_B_STATUS+BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_BOILER_INDIRECT_EFFICIENCY*BOILER_C_STATUS+BOILER_D_TOTAL_STEAM_ENERGY*BOILER_D_BOILER_INDIRECT_EFFICI |  | Missing inputs (not in hierarchy): BOILER_A_BOILER_INDIRECT_EFFICIENCY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_BOILER_INDIRECT_EFFICIENCY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY (+9 more) | BOILER_A_BOILER_INDIRECT_EFFICIENCY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_BOILER_INDIRECT_EFFICIENCY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_BOILER_INDIRECT_EFFICIENCY; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_BOILER_INDIRECT_EFFICIENCY; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_BOILER_INDIRECT_EFFICIENCY; BOILER_E_TOTAL_STEAM_ENERGY; TOTAL_STEAM_ENERGY
Boiler_E_Nox_Emission | Boiler E Nox Emission | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | ng/J | if(BOILER_E_STATUS==0,0,BOILER_E_NOX*46/24.45*1000000*2.07/10000000*20.9/(20.9-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | 0 | Missing inputs (not in hierarchy): BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_NOX | BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_NOX
Boiler_E_Nox_Emission_Actual_Value | Boiler E Nox Emission Actual Value | 362_DM_ | nan |  |  | No formula and no PI value available
Boiler_E_Nox_Emission_Forecast | Boiler E Nox Emission Forecast | 362_DM_ | ng/J |  |  | No formula and no PI value available
Boiler_E_Nox_Emission_Max_Forecast | Boiler E Nox Emission Max Forecast | 362_DM_ | ng/J |  |  | No formula and no PI value available
Boiler_E_Nox_Emission_Timestamp_Max_Forecast | Boiler E Nox Emission Timestamp Max Forecast | 362_DM_ | nan |  |  | No formula and no PI value available
CAPACITY_UTILIZATION_1 | CAPACITY UTILIZATION 1 | LBM_preprocessing_inferred_tags_main | % | [TOTAL_STEAM_PRODUCTION]/750000*100 |  | Missing inputs (not in hierarchy): TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
COMBUSTION_AIR_TEMP | COMBUSTION AIR TEMP | LBM_preprocessing_inferred_tags_main | DEG C | ((BOILER_A_COMBUSTION_AIR_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_COMBUSTION_AIR_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_COMBUSTION_AIR_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_COMBUSTION_AIR_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_COMBUSTION_AIR_TEMP*BOILER_E_STATUS))/BOILERS_ONLINE |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_COMBUSTION_AIR_TEMPERATURE; BOILER_A_STATUS; BOILER_B_COMBUSTION_AIR_TEMPERATURE; BOILER_B_STATUS; BOILER_C_COMBUSTION_AIR_TEMPERATURE (+4 more) | BOILERS_ONLINE; BOILER_A_COMBUSTION_AIR_TEMPERATURE; BOILER_A_STATUS; BOILER_B_COMBUSTION_AIR_TEMPERATURE; BOILER_B_STATUS; BOILER_C_COMBUSTION_AIR_TEMPERATURE; BOILER_C_STATUS; BOILER_D_COMBUSTION_AIR_TEMPERATURE; BOILER_D_STATUS; BOILER_E_COMBUSTION_AIR_TEMP
Capacity_Utilization | CAPACITY UTILIZATION | LBM_ | % |  |  | No formula and no PI value available
ENERGY_NUMBER | ENERGY NUMBER | TRG_compute_inferred_pre_pta | MMBTU/ HR | ((BOILER_A_FG_FLOW_RATE_actual*BOILER_A_MIXED_LHV_PER_KG_actual*1000)*BOILER_A_STATUS_actual+(BOILER_B_FG_FLOW_RATE_actual*BOILER_B_MIXED_LHV_PER_KG_actual*1000)*BOILER_B_STATUS_actual+(BOILER_C_FG_FLOW_RATE_actual*BOILER_C_MIXED_LHV_PER_KG_actual*1000)*BOILER_C_STATUS_actual+(BOILER_D_FG_FLOW_RATE_ |  | eval_error: name 'BOILER_A_FG_FLOW_RATE_actual' is not defined
ENVIRONMENT_NUMBER | ENVIRONMENT NUMBER | TRG_compute_inferred_pre_pta | MT/ HR | ([ENERGY_NUMBER_actual]/0.0468/1000)*2.75 |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
EQUIVALENT_FUEL | EQUIVALENT FUEL | TRG_compute_inferred_pre_pta | MT/ HR | [OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual]/0.0468/1000 |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
EQUIVALENT_FUEL_DAY | EQUIVALENT FUEL DAY | TRG_compute_inferred_pre_pta | MT/ DAY | [EQUIVALENT_FUEL_actual]*24 |  | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
EXCESS_O2 | EXCESS O2 | LBM_preprocessing_inferred_tags_main | % | ((BOILER_A_FLUE_GAS_OXGYGEN*BOILER_A_STATUS)+(BOILER_B_FLUE_GAS_OXGYGEN*BOILER_B_STATUS)+(BOILER_C_FLUE_GAS_OXGYGEN*BOILER_C_STATUS)+(BOILER_D_FLUE_GAS_OXGYGEN*BOILER_D_STATUS)+(BOILER_E_FLUE_GAS_OXGYGEN_NEW*BOILER_E_STATUS))/BOILERS_ONLINE |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_STATUS; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_STATUS; BOILER_C_FLUE_GAS_OXGYGEN (+4 more) | BOILERS_ONLINE; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_STATUS; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_STATUS; BOILER_C_FLUE_GAS_OXGYGEN; BOILER_C_STATUS; BOILER_D_FLUE_GAS_OXGYGEN; BOILER_D_STATUS; BOILER_E_FLUE_GAS_OXGYGEN_NEW
FIRE_DUTY | FIRE DUTY | LBM_preprocessing_inferred_tags_main | MMBTU/ DAY | ((BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG*1000)*BOILER_A_STATUS+(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG*1000)*BOILER_B_STATUS+(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG*1000)*BOILER_C_STATUS+(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG*1000)*BOILER_D_STATUS+(BOILER_E_FG_FL | 0 | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS; BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS; BOILER_C_MIXED_LHV_PER_KG (+4 more) | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS; BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS; BOILER_E_MIXED_LHV_PER_KG
FLAG_BFW_QUALITY | FLAG BFW QUALITY | LBM_preprocessing_inferred_tags_main | % | if([BFW_OXYGEN]>7ll[BFW_SILICA]>20ll[BFW_SODIUM]>20[BFW_PH]>9.6ll[BFW_PH]<9.2ll[BFW_CONDUCTIVITY]>10,0,1) |  | Missing inputs (not in hierarchy): BFW_CONDUCTIVITY; BFW_OXYGEN; BFW_PH; BFW_SILICA; BFW_SODIUM | BFW_CONDUCTIVITY; BFW_OXYGEN; BFW_PH; BFW_SILICA; BFW_SODIUM
FLAG_BFW_QUALITY_PTA | FLAG BFW QUALITY PTA | TRG_compute_pta | % |  |  | No formula and no PI value available
FLAG_QUALITY_RATE | FLAG QUALITY RATE | LBM_preprocessing_inferred_tags_main | % | if(([STEAM_TEMP]>390&&[STEAM_PRESS]>40),1,0) |  | Missing inputs (not in hierarchy): STEAM_PRESS; STEAM_TEMP | STEAM_PRESS; STEAM_TEMP
FLAG_QUALITY_RATE_PTA | FLAG QUALITY RATE PTA | TRG_compute_pta | % |  |  | No formula and no PI value available
NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | NORMALIZED BOILER A FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | 87.5988 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_A_FG_CO2_CONCENTRATION | NORMALIZED BOILER A FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER A FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 1.5699 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER A FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL)*100 | 0 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER_A_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER A FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION
NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | NORMALIZED BOILER A FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.097056 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | NORMALIZED BOILER A FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.033019 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | NORMALIZED BOILER A FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | 10.2419 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | NORMALIZED BOILER A FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.11507 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | NORMALIZED BOILER A FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.001001 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER A FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.3432 | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | NORMALIZED BOILER B FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | 87.5988 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_B_FG_CO2_CONCENTRATION | NORMALIZED BOILER B FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER B FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 1.5699 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER B FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL)*100 | 0 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER_B_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER B FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION
NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | NORMALIZED BOILER B FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.097056 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | NORMALIZED BOILER B FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.033019 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | NORMALIZED BOILER B FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | 10.2419 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | NORMALIZED BOILER B FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.11507 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | NORMALIZED BOILER B FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.001001 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER B FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.3432 | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | NORMALIZED BOILER C FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | 87.5988 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_C_FG_CO2_CONCENTRATION | NORMALIZED BOILER C FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER C FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 1.5699 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER C FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL)*100 | 0 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER_C_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER C FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION
NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | NORMALIZED BOILER C FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.097056 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | NORMALIZED BOILER C FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.033019 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | NORMALIZED BOILER C FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | 10.2419 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | NORMALIZED BOILER C FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.11507 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | NORMALIZED BOILER C FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.001001 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER C FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.3432 | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | NORMALIZED BOILER D FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | 87.5988 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_D_FG_CO2_CONCENTRATION | NORMALIZED BOILER D FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER D FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 1.5699 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER D FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL)*100 | 0 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER_D_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER D FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION
NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | NORMALIZED BOILER D FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.097056 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | NORMALIZED BOILER D FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.033019 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | NORMALIZED BOILER D FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | 10.2419 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | NORMALIZED BOILER D FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.11507 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | NORMALIZED BOILER D FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.001001 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER D FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.3432 | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | NORMALIZED BOILER E FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | 87.5988 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_E_FG_CO2_CONCENTRATION | NORMALIZED BOILER E FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER E FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 1.5699 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER E FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL)*100 | 0 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER_E_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER E FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION
NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | NORMALIZED BOILER E FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.097056 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | NORMALIZED BOILER E FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.033019 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | NORMALIZED BOILER E FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | 10.2419 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | NORMALIZED BOILER E FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.11507 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | NORMALIZED BOILER E FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.001001 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER E FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.3432 | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION
NUMBER_OF_BOILERS_ONLINE | Number of boilers running | LBM_preprocessing_inferred_tags_main | nan | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS]) |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
NUMBER_OF_BOILERS_OPTIMUM | Optimum number of boilers that can be run considering steam margin. | LBM_preprocessing_inferred_tags_main | nan | if([STEAM_MARGIN_NUMBER]>2.0,([NUMBER_OF_BOILERS_ONLINE]-1),[NUMBER_OF_BOILERS_ONLINE]) |  | Missing inputs (not in hierarchy): NUMBER_OF_BOILERS_ONLINE; STEAM_MARGIN_NUMBER | NUMBER_OF_BOILERS_ONLINE; STEAM_MARGIN_NUMBER
OVERALL_ENERGY_CONSUMPTION_DAY | OVERALL ENERGY CONSUMPTION DAY | TRG_compute_inferred_pre_pta | GJ/ DAY | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24 |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_DELTA | OVERALL ENERGY CONSUMPTION DAY DELTA | TRG_compute_inferred_pre_pta | GJ/ DAY | abs(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24)*TOTAL_STEAM_PRODUCTION_MT_DAY_actual |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_benchmark | OVERALL ENERGY CONSUMPTION DAY BENCHMARK | TRG_compute_inferred_pre_pta | GJ/ DAY | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24 |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark' is not defined
OVERALL_SUPERHEATED_STEAM_BFW_RATIO | OVERALL SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | [-] | (BOILER_A_SUPERHEATED_STEAM_BFW_RATIO+BOILER_B_SUPERHEATED_STEAM_BFW_RATIO+BOILER_C_SUPERHEATED_STEAM_BFW_RATIO+BOILER_D_SUPERHEATED_STEAM_BFW_RATIO+BOILER_E_SUPERHEATED_STEAM_BFW_RATIO)/5 |  | Missing inputs (not in hierarchy): BOILER_A_SUPERHEATED_STEAM_BFW_RATIO; BOILER_B_SUPERHEATED_STEAM_BFW_RATIO; BOILER_C_SUPERHEATED_STEAM_BFW_RATIO; BOILER_D_SUPERHEATED_STEAM_BFW_RATIO; BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER_A_SUPERHEATED_STEAM_BFW_RATIO; BOILER_B_SUPERHEATED_STEAM_BFW_RATIO; BOILER_C_SUPERHEATED_STEAM_BFW_RATIO; BOILER_D_SUPERHEATED_STEAM_BFW_RATIO; BOILER_E_SUPERHEATED_STEAM_BFW_RATIO
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION | OVER ALL SPECIFIC ENERGY CONSUMPTION | LBM_preprocessing_inferred_tags_main | GJ/T | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_I |  | Missing inputs (not in hierarchy): BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY (+8 more) | BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_E_TOTAL_STEAM_ENERGY
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA | OVER ALL SPECIFIC ENERGY CONSUMPTION DELTA | TRG_compute_inferred_pre_pta | nan | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark<0,0,(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark)) |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
QUALITY_RATE | QUALITY RATE | TRG_compute_inferred_post_pta | % | FLAG_QUALITY_RATE_PTA_actual*100/24 |  | eval_error: name 'FLAG_QUALITY_RATE_PTA_actual' is not defined
SPECIFIC_ENERGY_AVG | SPECIFIC ENERGY AVG | LBM_preprocessing_inferred_tags_main | KG/ KCAL | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_D_STATUS+BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_E_STATUS)/BOI |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ (+4 more) | BOILERS_ONLINE; BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_C_STATUS; BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_D_STATUS; BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ
STACK_TEMP | STACK TEMP | LBM_preprocessing_inferred_tags_main | DEG C | ((BOILER_A_STACK_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_STACK_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_STACK_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_STACK_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_STACK_TEMPERATURE*BOILER_E_STATUS))/BOILERS_ONLINE |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
STEAM_MARGIN_NUMBER | Available steam margin divided by 150 | LBM_preprocessing_inferred_tags_main | nan | [STEAM_MARGIN_TPH]/150 |  | Missing inputs (not in hierarchy): STEAM_MARGIN_TPH | STEAM_MARGIN_TPH
STEAM_MARGIN_TPH | Steam margin available in running boilers in TPH | LBM_preprocessing_inferred_tags_main | TPH | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS])*150-[TOTAL_STEAM_PRODUCTION] |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; TOTAL_STEAM_PRODUCTION | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; TOTAL_STEAM_PRODUCTION
STEAM_PRESS | STEAM PRESS | LBM_preprocessing_inferred_tags_main | BARG | ((HP_STEAM_PRESSURE_FROM_DS*BOILER_A_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_B*BOILER_B_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_C*BOILER_C_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_D*BOILER_D_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_E*BOILER_E_STATUS))/BOILERS_ONLINE |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; HP_STEAM_PRESSURE_FROM_DS (+3 more) | BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; HP_STEAM_PRESSURE_FROM_DS; HP_STEAM_PRESSURE_FROM_DS_B; HP_STEAM_PRESSURE_FROM_DS_C; HP_STEAM_PRESSURE_FROM_DS_D
STEAM_TEMP | STEAM TEMP | LBM_preprocessing_inferred_tags_main | DEG C | (DESUPERHEATER_OUTLET_TEMPERATURE*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_TEMPERATURE*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_TEMPERATURE*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_TEMPERATURE*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_TEMPERATURE*BOILER_E_STATUS)/BOILERS_ONLINE |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
TOTAL_BLOWDOWN_LOSS | TOTAL BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_BLOWDOWN_LOSS+BOILER_B_BLOWDOWN_LOSS+BOILER_C_BLOWDOWN_LOSS+BOILER_D_BLOWDOWN_LOSS+BOILER_E_BLOWDOWN_LOSS | 0 | Missing inputs (not in hierarchy): BOILER_A_BLOWDOWN_LOSS; BOILER_B_BLOWDOWN_LOSS; BOILER_C_BLOWDOWN_LOSS; BOILER_D_BLOWDOWN_LOSS; BOILER_E_BLOWDOWN_LOSS | BOILER_A_BLOWDOWN_LOSS; BOILER_B_BLOWDOWN_LOSS; BOILER_C_BLOWDOWN_LOSS; BOILER_D_BLOWDOWN_LOSS; BOILER_E_BLOWDOWN_LOSS
TOTAL_CO2_EMISSIONS | TOTAL CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | BOILER_A_CO2_EMISSIONS+BOILER_B_CO2_EMISSIONS+BOILER_C_CO2_EMISSIONS+BOILER_D_CO2_EMISSIONS+BOILER_E_CO2_EMISSIONS | 0 | Missing inputs (not in hierarchy): BOILER_A_CO2_EMISSIONS; BOILER_B_CO2_EMISSIONS; BOILER_C_CO2_EMISSIONS; BOILER_D_CO2_EMISSIONS; BOILER_E_CO2_EMISSIONS | BOILER_A_CO2_EMISSIONS; BOILER_B_CO2_EMISSIONS; BOILER_C_CO2_EMISSIONS; BOILER_D_CO2_EMISSIONS; BOILER_E_CO2_EMISSIONS
TOTAL_CO2_GAP | TOTAL CO2 GAP | TRG_compute_inferred_pre_pta | MMBTU/ DAY | [EQUIVALENT_FUEL_actual]*2.75*24 |  | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
TOTAL_ENERGY_GAP | TOTAL ENERGY GAP | TRG_compute_inferred_pre_pta | MT/ DAY | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
TOTAL_FUEL_COMPOSTION_MASS | TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_A_FG_CH4_MASS_PERCENTAGE+BOILER_A_FG_ETHANE_MASS_PERCENTAGE+BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_A_FG_PROPANE_MASS_PERCENTAGE+BOILER_A_FG_NC4_MASS_PERCENTAGE+BOILER_A_FG_IC4_MASS_PERCENTAGE+BOILER_A_FG_NC5_MASS_PERCENTAGE+BOILER_A_FG_IC5_MASS_PERCEN | 100 | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_PERCENTAGE; BOILER_A_FG_ETHANE_MASS_PERCENTAGE; BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_A_FG_IC4_MASS_PERCENTAGE; BOILER_A_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_A_FG_CH4_MASS_PERCENTAGE; BOILER_A_FG_ETHANE_MASS_PERCENTAGE; BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_A_FG_IC4_MASS_PERCENTAGE; BOILER_A_FG_IC5_MASS_PERCENTAGE; BOILER_A_FG_NC4_MASS_PERCENTAGE; BOILER_A_FG_NC5_MASS_PERCENTAGE; BOILER_A_FG_NITROGEN_MASS_PERCENTAGE; BOILER_A_FG_PROPANE_MASS_PERCENTAGE
TOTAL_FUEL_CONSUMPTION_GCAL_H | TOTAL FUEL CONSUMPTION GCAL H | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | 0 | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
TOTAL_FUEL_FLOW | TOTAL FUEL FLOW | LBM_preprocessing_inferred_tags_main | Ton/h | (BOILER_A_FUEL_GAS_FLOW+BOILER_B_FUEL_GAS_FLOW+BOILER_C_FUEL_GAS_FLOW+BOILER_D_FUEL_GAS_FLOW+BOILER_E_FUEL_GAS_FLOW/1.295)/1000 | 0.88188 | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_FLOW | BOILER_B_FUEL_GAS_FLOW
TOTAL_FUEL_GAIN_LOSS | TOTAL FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | BOILER_A_FUEL_GAIN_LOSS_actual+BOILER_B_FUEL_GAIN_LOSS_actual+BOILER_C_FUEL_GAIN_LOSS_actual+BOILER_D_FUEL_GAIN_LOSS_actual+BOILER_E_FUEL_GAIN_LOSS_actual |  | eval_error: name 'BOILER_A_FUEL_GAIN_LOSS_actual' is not defined
TOTAL_FUEL_TO_AIR_RATIO | TOTAL FUEL TO AIR RATIO | LBM_preprocessing_inferred_tags_main | Kg/ Kg Fuel | BOILER_A_AIR_FUEL_MASS_RATIO+BOILER_B_AIR_FUEL_MASS_RATIO+BOILER_C_AIR_FUEL_MASS_RATIO+BOILER_D_AIR_FUEL_MASS_RATIO+BOILER_E_AIR_FUEL_MASS_RATIO | 72.66 | Missing inputs (not in hierarchy): BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_E_AIR_FUEL_MASS_RATIO
TOTAL_STACK_LOSS_GCAL_H | TOTAL STACK LOSS GCAL/H | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_STACK_LOSS_CORRECTED+BOILER_B_STACK_LOSS_CORRECTED+BOILER_C_STACK_LOSS_CORRECTED+BOILER_D_STACK_LOSS_CORRECTED+BOILER_E_STACK_LOSS_CORRECTED | 0 | Missing inputs (not in hierarchy): BOILER_A_STACK_LOSS_CORRECTED; BOILER_B_STACK_LOSS_CORRECTED; BOILER_C_STACK_LOSS_CORRECTED; BOILER_D_STACK_LOSS_CORRECTED; BOILER_E_STACK_LOSS_CORRECTED | BOILER_A_STACK_LOSS_CORRECTED; BOILER_B_STACK_LOSS_CORRECTED; BOILER_C_STACK_LOSS_CORRECTED; BOILER_D_STACK_LOSS_CORRECTED; BOILER_E_STACK_LOSS_CORRECTED
TOTAL_STEAM_ENERGY | TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_TOTAL_STEAM_ENERGY+BOILER_B_TOTAL_STEAM_ENERGY+BOILER_C_TOTAL_STEAM_ENERGY+BOILER_D_TOTAL_STEAM_ENERGY+BOILER_E_TOTAL_STEAM_ENERGY | 0 | Missing inputs (not in hierarchy): BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY | BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY
TOTAL_STEAM_PRODUCTION | TOTAL STEAM PRODUCTION | LBM_preprocessing_inferred_tags_main | T/h | (DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_STATUS)/1000 | 0 | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
TOTAL_STEAM_PRODUCTION_MT_DAY | TOTAL STEAM PRODUCTION IN MT PER DAY | LBM_preprocessing_inferred_tags_main | MT/ DAY | [TOTAL_STEAM_PRODUCTION]*24 |  | Missing inputs (not in hierarchy): TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
Timestamp | Timestamp | fixed,LBM_,362_DM_ | nan |  |  | No formula and no PI value available
index_energy | INDEX ENERGY | TRG_compute_inferred_pre_pta | % | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
index_environment | INDEX ENVIRONMENT | TRG_compute_inferred_pre_pta | % | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
index_process | INDEX PROCESS | TRG_compute_inferred_pre_pta | % | (TOTAL_STEAM_PRODUCTION_actual/(TOTAL_STEAM_PRODUCTION_actual+opportunity_production_actual/24))*100*0+100 |  | eval_error: name 'TOTAL_STEAM_PRODUCTION_actual' is not defined
opportunity_energy | OPPORTUNITY ENERGY | TRG_compute_inferred_pre_pta | MMBTU/ DAY | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
opportunity_environment | OPPORTUNITY ENVIRONMENT | TRG_compute_inferred_pre_pta | MT/ DAY | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[EQUIVALENT_FUEL_actual]*2.75*24) |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
opportunity_production | OPPORTUNITY PRODUCTION | TRG_compute_inferred_pre_pta | MT/ DAY | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual])*24/([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark])*0 |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
plant_status | plant status | LBM_preprocessing_inferred_tags_main | nan | if(BOILERS_ONLINE==0,0,1) | 0 | Missing inputs (not in hierarchy): BOILERS_ONLINE | BOILERS_ONLINE

## Computed_Full_PEEO
tag_name | description | category | uom | formula | value
ARRAZI_PLANT_LOAD_1 | ARRAZI PLANT LOAD 1 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | if(ARRAZI_PLANT_LOAD==MISSING_NUMERIC,0,ARRAZI_PLANT_LOAD) | 0
ARRAZI_PLANT_STATUS | ARRAZI PLANT STATUS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_LOAD_1<70,0,1) | 0
BOILERS_ONLINE | BOILERS ONLINE | LBM_preprocessing_inferred_tags_main | - | BOILER_A_STATUS+BOILER_B_STATUS+BOILER_C_STATUS+BOILER_D_STATUS+BOILER_E_STATUS | 0
BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER A AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_A_AIR_CP_REF_T+BOILER_A_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044
BOILER_A_AIR_CP_REF_T | BOILER A AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_A_AIR_FUEL_MASS_RATIO | BOILER A AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_EXCESS_AIR+BOILER_A_CORRECTED_COMBUSTION_AIR | 14.5295
BOILER_A_AIR_MOISTURE | BOILER A AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_A_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_A_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER A AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*17.265 | 13.7122
BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER A AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058
BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011
BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*14.807 | 0
BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER A AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*34.344 | 0
BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER A AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*15.487 | 0.04938
BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER A AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*15.353 | 0.020674
BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER A AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*15.487 | 0.058544
BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER A AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*15.353 | 0.000626
BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER A AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431
BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER A AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_A_CO2_FORMED/44.01+BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.85*BOILER_A_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_A_FLUE_GAS_MW)/BOILER_A_FLUE_GAS_MW | 0.21039
BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER A AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_A_FG_MW)/2 | 0.4367
BOILER_A_BFW_ENERGY | BOILER A BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*BOILER_A_BFW_ENTHALPY/1000) | 0
BOILER_A_BFW_ENTHALPY | BOILER A BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_A_INLET_TEMPERATURE) | 0
BOILER_A_BLOWDOWN_LOSS | BOILER A BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,((BOILER_A_CBD_BD/1000)*((STEAM_DRUM_A_PRESSURE*2.11087739028321+SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | 0
BOILER_A_BOILER_LOAD | BOILER A BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_OUTLET_STEAM_FLOW/150000*100 | 1.7975
BOILER_A_CALCULATED_AIRFLOW_NM3H | BOILER A CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_A_STATUS==0,0,BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0
BOILER_A_CH4_CO2_COMBUSTION | BOILER A CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*2.744 | 2.1793
BOILER_A_CH4_H2O_COMBUSTION | BOILER A CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*2.246 | 1.7838
BOILER_A_CH4_N2_COMBUSTION | BOILER A CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*13.275 | 10.5432
BOILER_A_CO2_EMISSIONS | BOILER A CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_CO2_FORMED*BOILER_A_FUEL_GAS_CORRECTED_TPH) | 0
BOILER_A_CO2_FORMED | BOILER A CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_CH4_CO2_COMBUSTION+BOILER_A_ETHANE_CO2_COMBUSTION+BOILER_A_ETHYLENE_CO2_COMBUSTION+BOILER_A_PROPANE_CO2_COMBUSTION+BOILER_A_NC4_CO2_COMBUSTION+BOILER_A_IC4_CO2_COMBUSTION+BOILER_A_NC5_CO2_COMBUSTION+BOILER_A_IC5_CO2_COMBUSTION | 2.3084
BOILER_A_CONVECTION_DUTY | BOILER A CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY+BOILER_A_SH_DUTY+BOILER_A_STACK_LOSS_CORRECTED) | 0
BOILER_A_CORRECTED_BFW_FLOW | BOILER A CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_A_STATUS==0,0,(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-DESUPERHEATER_OUTLET_STEAM_FLOW-BOILER_A_CBD_BD))/1000) | 0
BOILER_A_CORRECTED_COMBUSTION_AIR | BOILER A CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_A_AIR_MOISTURE) | 14.4151
BOILER_A_CORRECTED_COMBUTION_H2O_FORMED | BOILER A CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2O_FORMED+(BOILER_A_CORRECTED_COMBUSTION_AIR-BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679
BOILER_A_CORRECTED_FUEL_FLOW | BOILER A CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW-((BOILER_A_FUEL_GAS_ENERGY_INPUT-(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY+BOILER_A_BLOWDOWN_LOSS+BOILER_A_STACK_LOSS+BOILER_A_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_A_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOA | 0
BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER A CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | 0
BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER A CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9663
BOILER_A_CP_CH4_FUEL_TEMP | BOILER A CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3614
BOILER_A_CP_ETHANE_FUEL_TEMP | BOILER A CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0739
BOILER_A_CP_ETHYLENE_FUEL_TEMP | BOILER A CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6651
BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER A CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6499
BOILER_A_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER A CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER A CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_A_CP_H2_FUEL_TEMP | BOILER A CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8453
BOILER_A_CP_IC4_FUEL_TEMP | BOILER A CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1103
BOILER_A_CP_IC5_FUEL_TEMP | BOILER A CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8823
BOILER_A_CP_NC4_FUEL_TEMP | BOILER A CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.928
BOILER_A_CP_NC5_FUEL_TEMP | BOILER A CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1654
BOILER_A_CP_OF_AIR_AT_STACK_TEMP | BOILER A CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_A_STACK_TEMPERATURE+273.15)/ | 6.9676
BOILER_A_CP_OF_H2O_AT_STACK_TEMP | BOILER A CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_A_CP_PROPANE_FUEL_TEMP | BOILER A CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.047
BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER A CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_A_CP_H2_FUEL_TEMP+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_A_CP_CH4_FUEL_TEMP+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_A_CP_ETHYLENE_FUEL_TEMP+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7287
BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER A CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_A_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229
BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_A_EXCESS_AIR*(1-BOILER_A_AIR_MOISTURE)+BOILER_A_N2_FORMED+BOILER_A_CO2_FORMED | 13.4993
BOILER_A_ECONOMIZER_DUTY | BOILER A ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*((STEAM_DRUM_A_PRESSURE*0.0336523715096497+ECONIMIZER_A_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_A_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0
BOILER_A_ENERGY_GAINED | BOILER A ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY) | 0
BOILER_A_ETHANE_CO2_COMBUSTION | BOILER A ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103
BOILER_A_ETHANE_H2O_COMBUSTION | BOILER A ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977
BOILER_A_ETHANE_N2_COMBUSTION | BOILER A ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072
BOILER_A_ETHYLENE_CO2_COMBUSTION | BOILER A ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*3.138 | 0
BOILER_A_ETHYLENE_H2O_COMBUSTION | BOILER A ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*1.285 | 0
BOILER_A_ETHYLENE_N2_COMBUSTION | BOILER A ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*11.385 | 0
BOILER_A_EXCESS_AIR | BOILER A EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_A_FLUE_GAS_OXGYGEN)*((BOILER_A_N2_FORMED/28.01)+(BOILER_A_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_A_CO2_FORMED/44.01))/(20.95-BOILER_A_FLUE_GAS_OXGYGEN)) | 0.11442
BOILER_A_FG_CH4_MASS_FRACTION | BOILER A FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_CH4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_A_FG_CH4_MASS_PERCENTAGE | BOILER A FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_A_FG_MW | 79.4217
BOILER_A_FG_DENSITY | BOILER A FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_A_FG_MW/22.414 | 0.7893
BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER A FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | BOILER_A_FG_ETHANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_A_FG_ETHANE_MASS_PERCENTAGE | BOILER A FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_A_FG_MW | 2.6684
BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER A FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE | BOILER A FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_A_FG_MW | 0
BOILER_A_FG_FLOW_RATE | BOILER A FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_A_FUEL_GAS_FLOW/1000 | 0.17548
BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER A FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE | BOILER A FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_A_FG_MW | 0
BOILER_A_FG_IC4_MASS_FRACTION | BOILER A FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_IC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_A_FG_IC4_MASS_PERCENTAGE | BOILER A FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | 0.31885
BOILER_A_FG_IC5_MASS_FRACTION | BOILER A FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_IC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_A_FG_IC5_MASS_PERCENTAGE | BOILER A FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | 0.13466
BOILER_A_FG_MW | BOILER A FG MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | G/MOL | (NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW+NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_A_FG_PROPANE_CONCEN | 17.6914
BOILER_A_FG_NC4_MASS_FRACTION | BOILER A FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_A_FG_NC4_MASS_PERCENTAGE | BOILER A FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | 0.37802
BOILER_A_FG_NC5_MASS_FRACTION | BOILER A FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_A_FG_NC5_MASS_PERCENTAGE | BOILER A FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | 0.004081
BOILER_A_FG_NITROGEN_MASS_FRACTION | BOILER A FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | BOILER A FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_A_FG_MW | 16.219
BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER A FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_PROPANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_A_FG_PROPANE_MASS_PERCENTAGE | BOILER A FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_A_FG_MW | 0.85531
BOILER_A_FLUE_GAS_MW | BOILER A FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_A_CO2_FORMED/44.01+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.96) | 27.6617
BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | 15.3673
BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER A FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | (BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942
BOILER_A_FUEL_CONSUMPTION | BOILER A FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | 0
BOILER_A_FUEL_GAS_CORRECTED_TPH | BOILER A FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW/1000) | 0
BOILER_A_FUEL_GAS_ENERGY_INPUT | BOILER A FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_FG_FLOW_RATE*1000*BOILER_A_MIXED_LHV_PER_KG/10^6) | 0
BOILER_A_H2O_FORMED | BOILER A H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2_H2O_COMBUSTION+BOILER_A_CH4_H2O_COMBUSTION+BOILER_A_ETHANE_H2O_COMBUSTION+BOILER_A_ETHYLENE_H2O_COMBUSTION+BOILER_A_PROPANE_H2O_COMBUSTION+BOILER_A_IC4_H2O_COMBUSTION+BOILER_A_NC4_H2O_COMBUSTION+BOILER_A_IC5_H2O_COMBUSTION+BOILER_A_NC5_H2O_COMBUSTION | 1.8586
BOILER_A_H2_CO2_COMBUSTION | BOILER A H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*0 | 0
BOILER_A_H2_H2O_COMBUSTION | BOILER A H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*8.937 | 0
BOILER_A_H2_N2_COMBUSTION | BOILER A H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*26.407 | 0
BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER A HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_A_STACK_TEMPERATURE-15.6)))) | 0
BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER A HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,9*(BOILER_A_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_A_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_A_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0
BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER A HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_A_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0
BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER A HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,0*10^-6*28*5654*BOILER_A_BOILER_LOAD) | 0
BOILER_A_HP_STEAM_ENTHALPY | BOILER A HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS)+2.66244961166282*DESUPERHEATER_OUTLET_TEMPERATURE)*0.239+2) | 0
BOILER_A_IC4_CO2_COMBUSTION | BOILER A IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*3.029 | 0.009658
BOILER_A_IC4_H2O_COMBUSTION | BOILER A IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*1.55 | 0.005859
BOILER_A_IC4_N2_COMBUSTION | BOILER A IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*11.908 | 0.037969
BOILER_A_IC5_CO2_COMBUSTION | BOILER A IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*3.05 | 0.004107
BOILER_A_IC5_H2O_COMBUSTION | BOILER A IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*1.498 | 0.002017
BOILER_A_IC5_N2_COMBUSTION | BOILER A IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*11.805 | 0.015897
BOILER_A_LHV_DESIGN | BOILER A LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (LHV_FG/BOILER_A_FG_DENSITY)/1000 | 39.6755
BOILER_A_MIXED_LHV_PER_KG | BOILER A MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019
BOILER_A_N2_FORMED | BOILER A N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2_N2_COMBUSTION+BOILER_A_CH4_N2_COMBUSTION+BOILER_A_ETHANE_N2_COMBUSTION+BOILER_A_ETHYLENE_N2_COMBUSTION+BOILER_A_PROPANE_N2_COMBUSTION+BOILER_A_IC4_N2_COMBUSTION+BOILER_A_NC4_N2_COMBUSTION+BOILER_A_IC5_N2_COMBUSTION+BOILER_A_NC5_N2_COMBUSTION | 11.0766
BOILER_A_NC4_CO2_COMBUSTION | BOILER A NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*3.029 | 0.01145
BOILER_A_NC4_H2O_COMBUSTION | BOILER A NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*1.55 | 0.004942
BOILER_A_NC4_N2_COMBUSTION | BOILER A NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*11.908 | 0.045014
BOILER_A_NC5_CO2_COMBUSTION | BOILER A NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*3.05 | 0.000124
BOILER_A_NC5_H2O_COMBUSTION | BOILER A NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05
BOILER_A_NC5_N2_COMBUSTION | BOILER A NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*11.805 | 0.000482
BOILER_A_PROPANE_CO2_COMBUSTION | BOILER A PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608
BOILER_A_PROPANE_H2O_COMBUSTION | BOILER A PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976
BOILER_A_PROPANE_N2_COMBUSTION | BOILER A PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327
BOILER_A_RADIATION_DUTY | BOILER A RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_ENERGY_GAINED-BOILER_A_CONVECTION_DUTY) | 0
BOILER_A_RADIATION_LOSSES | BOILER A RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_MIXED_LHV_PER_KG*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOAD^2-0.0899*BOILER_A_BOILER_LOAD+3.2426)/100) | 0
BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER A SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_A_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_A_AIR_FUEL_MASS_RATIO | -50.8545
BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER A SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0
BOILER_A_SH_DUTY | BOILER A SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*((STEAM_DRUM_A_PRESSURE*-2.64315212289699+DESUPERHEATER_TEMPERATURE*3.58096116723573+1939.73413132244)-(STEAM_DRUM_A_PRESSURE*-4.27591051303366+SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | 0
BOILER_A_SH_PERFORMANCE | BOILER A SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,(BOILER_A_SH_SPECIFIC_DUTY)/0.128049016*100) | 0
BOILER_A_SH_SPECIFIC_DUTY | BOILER A SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_A_STATUS==0,0,BOILER_A_SH_DUTY/DESUPERHEATER_OUTLET_STEAM_FLOW*1000) | 0
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER A SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)) | 0
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER A SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)*4.184) | 0
BOILER_A_STACK_LOSS | BOILER A STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_FLOW/(1000*1000)) | 0
BOILER_A_STACK_LOSS_CORRECTED | BOILER A STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_CORRECTED_TPH/1000) | 0
BOILER_A_STATUS | BOILER A STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_A_BOILER_LOAD>25&&DESUPERHEATER_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS>40,1,0) | 0
BOILER_A_STEAM_DRUM_TEMP | BOILER A STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_A_STATUS==0,0,4.02521999671835*log(STEAM_DRUM_A_PRESSURE*98.065)^3-4.64392873298701*log(STEAM_DRUM_A_PRESSURE*98.065)^2+11.2370106828649*log(STEAM_DRUM_A_PRESSURE*98.065)+83.4806425229703) | 0
BOILER_A_STEAM_TO_FIRE_DUTY_RATIO | BOILER A STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW/(BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG)*1000) | 0
BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER A TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0
BOILER_A_TOTAL_FLUE_GAS_CORRECTED | BOILER A TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_CORRECTED_TPH*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_A_TOTAL_FLUE_GAS_GENERATED | BOILER A TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW/1000*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER A TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_TOTAL_MOISTURE_WITH_AIR+BOILER_A_H2O_FORMED | 1.868
BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER A TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0
BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER A TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_A_MIXED_LHV_PER_KG) | 0
BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER A TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_A_RADIATION_LOSSES) | 0
BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER A TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_AIR_MOISTURE | 0.009372
BOILER_A_TOTAL_STEAM_ENERGY | BOILER A TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_HP_STEAM_ENTHALPY/1000000) | 0
BOILER_A_VAPOUR_PRESSURE_OF_H2O | BOILER A VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER B AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_B_AIR_CP_REF_T+BOILER_B_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044
BOILER_B_AIR_CP_REF_T | BOILER B AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_B_AIR_FUEL_MASS_RATIO | BOILER B AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_EXCESS_AIR+BOILER_B_CORRECTED_COMBUSTION_AIR | 14.528
BOILER_B_AIR_MOISTURE | BOILER B AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_B_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_B_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER B AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*17.265 | 13.7122
BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER B AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058
BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011
BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*14.807 | 0
BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER B AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*34.344 | 0
BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER B AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*15.487 | 0.04938
BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER B AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*15.353 | 0.020674
BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER B AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*15.487 | 0.058544
BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER B AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*15.353 | 0.000626
BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER B AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431
BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER B AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_B_CO2_FORMED/44.01+BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.85*BOILER_B_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_B_FLUE_GAS_MW)/BOILER_B_FLUE_GAS_MW | 0.21038
BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER B AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_B_FG_MW)/2 | 0.43669
BOILER_B_BFW_ENERGY | BOILER B BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*BOILER_B_BFW_ENTHALPY/1000) | 0
BOILER_B_BFW_ENTHALPY | BOILER B BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_B_INLET_TEMPERATURE) | 0
BOILER_B_BLOWDOWN_LOSS | BOILER B BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,((CBD_BLOW_DOWN_B/1000)*((BOILER_B_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | 0
BOILER_B_BOILER_LOAD | BOILER B BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_B_OUTLET_STEAM_FLOW/150000*100 | 1.8401
BOILER_B_CALCULATED_AIRFLOW_NM3H | BOILER B CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_B_STATUS==0,0,BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0
BOILER_B_CH4_CO2_COMBUSTION | BOILER B CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*2.744 | 2.1793
BOILER_B_CH4_H2O_COMBUSTION | BOILER B CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*2.246 | 1.7838
BOILER_B_CH4_N2_COMBUSTION | BOILER B CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*13.275 | 10.5432
BOILER_B_CO2_EMISSIONS | BOILER B CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_CO2_FORMED*BOILER_B_FUEL_GAS_CORRECTED_TPH) | 0
BOILER_B_CO2_FORMED | BOILER B CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_CH4_CO2_COMBUSTION+BOILER_B_ETHANE_CO2_COMBUSTION+BOILER_B_ETHYLENE_CO2_COMBUSTION+BOILER_B_PROPANE_CO2_COMBUSTION+BOILER_B_NC4_CO2_COMBUSTION+BOILER_B_IC4_CO2_COMBUSTION+BOILER_B_NC5_CO2_COMBUSTION+BOILER_B_IC5_CO2_COMBUSTION | 2.3084
BOILER_B_CONVECTION_DUTY | BOILER B CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY+BOILER_B_SH_DUTY+BOILER_B_STACK_LOSS_CORRECTED) | 0
BOILER_B_CORRECTED_BFW_FLOW | BOILER B CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_B_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-DESUPERHEATER_B_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_B))/1000) | 0
BOILER_B_CORRECTED_COMBUSTION_AIR | BOILER B CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_B_AIR_MOISTURE) | 14.4151
BOILER_B_CORRECTED_COMBUTION_H2O_FORMED | BOILER B CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2O_FORMED+(BOILER_B_CORRECTED_COMBUSTION_AIR-BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679
BOILER_B_CORRECTED_FUEL_FLOW | BOILER B CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW-((BOILER_B_FUEL_GAS_ENERGY_INPUT-(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY+BOILER_B_BLOWDOWN_LOSS+BOILER_B_STACK_LOSS+BOILER_B_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_B_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOA | 0
BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER B CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | 0
BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER B CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9663
BOILER_B_CP_CH4_FUEL_TEMP | BOILER B CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3613
BOILER_B_CP_ETHANE_FUEL_TEMP | BOILER B CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0729
BOILER_B_CP_ETHYLENE_FUEL_TEMP | BOILER B CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6644
BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER B CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6497
BOILER_B_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER B CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER B CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_B_CP_H2_FUEL_TEMP | BOILER B CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8452
BOILER_B_CP_IC4_FUEL_TEMP | BOILER B CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1072
BOILER_B_CP_IC5_FUEL_TEMP | BOILER B CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8799
BOILER_B_CP_NC4_FUEL_TEMP | BOILER B CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9262
BOILER_B_CP_NC5_FUEL_TEMP | BOILER B CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1634
BOILER_B_CP_OF_AIR_AT_STACK_TEMP | BOILER B CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_B_STACK_TEMPERATURE+273.15)/ | 6.9675
BOILER_B_CP_OF_H2O_AT_STACK_TEMP | BOILER B CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_B_CP_PROPANE_FUEL_TEMP | BOILER B CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0456
BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER B CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_B_CP_H2_FUEL_TEMP+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_B_CP_CH4_FUEL_TEMP+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_B_CP_ETHYLENE_FUEL_TEMP+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7286
BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER B CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_B_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229
BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_B_EXCESS_AIR*(1-BOILER_B_AIR_MOISTURE)+BOILER_B_N2_FORMED+BOILER_B_CO2_FORMED | 13.4978
BOILER_B_ECONOMIZER_DUTY | BOILER B ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_B_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_B_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0
BOILER_B_ENERGY_GAINED | BOILER B ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY) | 0
BOILER_B_ETHANE_CO2_COMBUSTION | BOILER B ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103
BOILER_B_ETHANE_H2O_COMBUSTION | BOILER B ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977
BOILER_B_ETHANE_N2_COMBUSTION | BOILER B ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072
BOILER_B_ETHYLENE_CO2_COMBUSTION | BOILER B ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*3.138 | 0
BOILER_B_ETHYLENE_H2O_COMBUSTION | BOILER B ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*1.285 | 0
BOILER_B_ETHYLENE_N2_COMBUSTION | BOILER B ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*11.385 | 0
BOILER_B_EXCESS_AIR | BOILER B EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_B_FLUE_GAS_OXGYGEN)*((BOILER_B_N2_FORMED/28.01)+(BOILER_B_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_B_CO2_FORMED/44.01))/(20.95-BOILER_B_FLUE_GAS_OXGYGEN)) | 0.11288
BOILER_B_FG_CH4_MASS_FRACTION | BOILER B FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_CH4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_B_FG_CH4_MASS_PERCENTAGE | BOILER B FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_B_FG_MW | 79.4217
BOILER_B_FG_DENSITY | BOILER B FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_B_FG_MW/22.414 | 0.7893
BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER B FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_B_FG_ETHANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_B_FG_ETHANE_MASS_PERCENTAGE | BOILER B FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_B_FG_MW | 2.6684
BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER B FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE | BOILER B FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_B_FG_MW | 0
BOILER_B_FG_FLOW_RATE | BOILER B FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_B_FUEL_GAS_FLOW/1000 | 0.17548
BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER B FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE | BOILER B FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_B_FG_MW | 0
BOILER_B_FG_IC4_MASS_FRACTION | BOILER B FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_IC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_B_FG_IC4_MASS_PERCENTAGE | BOILER B FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | 0.31885
BOILER_B_FG_IC5_MASS_FRACTION | BOILER B FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_IC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_B_FG_IC5_MASS_PERCENTAGE | BOILER B FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | 0.13466
BOILER_B_FG_MW | BOILER B FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_B_FG_IC4_CONCENTRATIO | 17.6914
BOILER_B_FG_NC4_MASS_FRACTION | BOILER B FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_B_FG_NC4_MASS_PERCENTAGE | BOILER B FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | 0.37802
BOILER_B_FG_NC5_MASS_FRACTION | BOILER B FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_B_FG_NC5_MASS_PERCENTAGE | BOILER B FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | 0.004081
BOILER_B_FG_NITROGEN_MASS_FRACTION | BOILER B FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_B_FG_NITROGEN_MASS_PERCENTAGE | BOILER B FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_B_FG_MW | 16.219
BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER B FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_PROPANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_B_FG_PROPANE_MASS_PERCENTAGE | BOILER B FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_B_FG_MW | 0.85531
BOILER_B_FLUE_GAS_MW | BOILER B FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_B_CO2_FORMED/44.01+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.96) | 27.6616
BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | 15.3658
BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER B FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942
BOILER_B_FUEL_CONSUMPTION | BOILER B FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | 0
BOILER_B_FUEL_GAS_CORRECTED_TPH | BOILER B FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW/1000) | 0
BOILER_B_FUEL_GAS_ENERGY_INPUT | BOILER B FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_FG_FLOW_RATE*1000*BOILER_B_MIXED_LHV_PER_KG/10^6) | 0
BOILER_B_H2O_FORMED | BOILER B H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2_H2O_COMBUSTION+BOILER_B_CH4_H2O_COMBUSTION+BOILER_B_ETHANE_H2O_COMBUSTION+BOILER_B_ETHYLENE_H2O_COMBUSTION+BOILER_B_PROPANE_H2O_COMBUSTION+BOILER_B_IC4_H2O_COMBUSTION+BOILER_B_NC4_H2O_COMBUSTION+BOILER_B_IC5_H2O_COMBUSTION+BOILER_B_NC5_H2O_COMBUSTION | 1.8586
BOILER_B_H2_CO2_COMBUSTION | BOILER B H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*0 | 0
BOILER_B_H2_H2O_COMBUSTION | BOILER B H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*8.937 | 0
BOILER_B_H2_N2_COMBUSTION | BOILER B H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*26.407 | 0
BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER B HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_B_STACK_TEMPERATURE-15.6)))) | 0
BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER B HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,9*(BOILER_B_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_B_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_B_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0
BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER B HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_B_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0
BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER B HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,0*10^-6*28*5654*BOILER_B_BOILER_LOAD) | 0
BOILER_B_HP_STEAM_ENTHALPY | BOILER B HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_B)+2.66244961166282*DESUPERHEATER_B_OUTLET_TEMPERATURE)*0.239+2) | 0
BOILER_B_IC4_CO2_COMBUSTION | BOILER B IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*3.029 | 0.009658
BOILER_B_IC4_H2O_COMBUSTION | BOILER B IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*1.55 | 0.005859
BOILER_B_IC4_N2_COMBUSTION | BOILER B IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*11.908 | 0.037969
BOILER_B_IC5_CO2_COMBUSTION | BOILER B IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*3.05 | 0.004107
BOILER_B_IC5_H2O_COMBUSTION | BOILER B IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*1.498 | 0.002017
BOILER_B_IC5_N2_COMBUSTION | BOILER B IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*11.805 | 0.015897
BOILER_B_LHV | BOILER B LHV | LBM_preprocessing_inferred_tags_main | Kcal/Kg | (BOILER_B_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_B_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_B_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_B_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_B_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_B_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_B_FG_N | 9984.6019
BOILER_B_LHV_DESIGN | BOILER B LHV DESIGN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_B_FG_DENSITY)/1000 | 39.6755
BOILER_B_MIXED_LHV_PER_KG | BOILER B MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019
BOILER_B_N2_FORMED | BOILER B N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2_N2_COMBUSTION+BOILER_B_CH4_N2_COMBUSTION+BOILER_B_ETHANE_N2_COMBUSTION+BOILER_B_ETHYLENE_N2_COMBUSTION+BOILER_B_PROPANE_N2_COMBUSTION+BOILER_B_IC4_N2_COMBUSTION+BOILER_B_NC4_N2_COMBUSTION+BOILER_B_IC5_N2_COMBUSTION+BOILER_B_NC5_N2_COMBUSTION | 11.0766
BOILER_B_NC4_CO2_COMBUSTION | BOILER B NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*3.029 | 0.01145
BOILER_B_NC4_H2O_COMBUSTION | BOILER B NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*1.55 | 0.004942
BOILER_B_NC4_N2_COMBUSTION | BOILER B NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*11.908 | 0.045014
BOILER_B_NC5_CO2_COMBUSTION | BOILER B NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*3.05 | 0.000124
BOILER_B_NC5_H2O_COMBUSTION | BOILER B NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05
BOILER_B_NC5_N2_COMBUSTION | BOILER B NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*11.805 | 0.000482
BOILER_B_PROPANE_CO2_COMBUSTION | BOILER B PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608
BOILER_B_PROPANE_H2O_COMBUSTION | BOILER B PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976
BOILER_B_PROPANE_N2_COMBUSTION | BOILER B PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327
BOILER_B_RADIATION_DUTY | BOILER B RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_ENERGY_GAINED-BOILER_B_CONVECTION_DUTY) | 0
BOILER_B_RADIATION_LOSSES | BOILER B RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_MIXED_LHV_PER_KG*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOAD^2-0.0899*BOILER_B_BOILER_LOAD+3.2426)/100) | 0
BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER B SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_B_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_B_AIR_FUEL_MASS_RATIO | -50.7932
BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER B SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0
BOILER_B_SH_DUTY | BOILER B SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_B_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_B_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | 0
BOILER_B_SH_PERFORMANCE | BOILER B SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,(BOILER_B_SH_SPECIFIC_DUTY)/0.110075721*100) | 0
BOILER_B_SH_SPECIFIC_DUTY | BOILER B SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_B_STATUS==0,0,BOILER_B_SH_DUTY/DESUPERHEATER_B_OUTLET_STEAM_FLOW*1000) | 0
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER B SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)) | 0
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER B SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)*4.184) | 0
BOILER_B_STACK_LOSS | BOILER B STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_FLOW/(1000*1000)) | 0
BOILER_B_STACK_LOSS_CORRECTED | BOILER B STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_CORRECTED_TPH/1000) | 0
BOILER_B_STATUS | BOILER B STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_B_BOILER_LOAD>25&&DESUPERHEATER_B_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_B>40,1,0) | 0
BOILER_B_STEAM_DRUM_TEMP | BOILER B STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_B_STATUS==0,0,4.02521999671835*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0
BOILER_B_STEAM_TO_FIRE_DUTY_RATIO | BOILER B STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW/(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG)*1000) | 0
BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER B TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0
BOILER_B_TOTAL_FLUE_GAS_CORRECTED | BOILER B TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_CORRECTED_TPH*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_B_TOTAL_FLUE_GAS_GENERATED | BOILER B TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW/1000*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER B TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_CH4_MASS_PERCENTAGE+BOILER_B_FG_ETHANE_MASS_PERCENTAGE+BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_B_FG_PROPANE_MASS_PERCENTAGE+BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_B_FG_NITROGEN_MASS_PERCENTAGE+BOILER_B_FG_IC4_MASS_PERCENTAGE+BOILER_B_FG_NC4_MASS_PERCENTAGE+BOILER_B_FG_NC5_MASS_P | 100
BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER B TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_TOTAL_MOISTURE_WITH_AIR+BOILER_B_H2O_FORMED | 1.868
BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER B TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0
BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER B TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_B_MIXED_LHV_PER_KG) | 0
BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER B TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_B_RADIATION_LOSSES) | 0
BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER B TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_AIR_MOISTURE | 0.009371
BOILER_B_TOTAL_STEAM_ENERGY | BOILER B TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_HP_STEAM_ENTHALPY/1000000) | 0
BOILER_B_VAPOUR_PRESSURE_OF_H2O | BOILER B VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER C AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_C_AIR_CP_REF_T+BOILER_C_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044
BOILER_C_AIR_CP_REF_T | BOILER C AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_C_AIR_FUEL_MASS_RATIO | BOILER C AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_EXCESS_AIR+BOILER_C_CORRECTED_COMBUSTION_AIR | 14.5295
BOILER_C_AIR_MOISTURE | BOILER C AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_C_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_C_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER C AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*17.265 | 13.7122
BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER C AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058
BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011
BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*14.807 | 0
BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER C AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*34.344 | 0
BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER C AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*15.487 | 0.04938
BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER C AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*15.353 | 0.020674
BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER C AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*15.487 | 0.058544
BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER C AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*15.353 | 0.000626
BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER C AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431
BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER C AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_C_CO2_FORMED/44.01+BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.85*BOILER_C_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_C_FLUE_GAS_MW)/BOILER_C_FLUE_GAS_MW | 0.21039
BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER C AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_C_FG_MW)/2 | 0.43669
BOILER_C_BFW_ENERGY | BOILER C BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*BOILER_C_BFW_ENTHALPY/1000) | 0
BOILER_C_BFW_ENTHALPY | BOILER C BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_C_INLET_TEMPERATURE) | 0
BOILER_C_BLOWDOWN_LOSS | BOILER C BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,((CBD_BLOW_DOWN_C/1000)*((BOILER_C_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | 0
BOILER_C_BOILER_LOAD | BOILER C BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_C_OUTLET_STEAM_FLOW/150000*100 | 1.7993
BOILER_C_CALCULATED_AIRFLOW_NM3H | BOILER C CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_C_STATUS==0,0,BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0
BOILER_C_CH4_CO2_COMBUSTION | BOILER C CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*2.744 | 2.1793
BOILER_C_CH4_H2O_COMBUSTION | BOILER C CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*2.246 | 1.7838
BOILER_C_CH4_N2_COMBUSTION | BOILER C CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*13.275 | 10.5432
BOILER_C_CO2_EMISSIONS | BOILER C CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_CO2_FORMED*BOILER_C_FUEL_GAS_CORRECTED_TPH) | 0
BOILER_C_CO2_FORMED | BOILER C CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_CH4_CO2_COMBUSTION+BOILER_C_ETHANE_CO2_COMBUSTION+BOILER_C_ETHYLENE_CO2_COMBUSTION+BOILER_C_PROPANE_CO2_COMBUSTION+BOILER_C_NC4_CO2_COMBUSTION+BOILER_C_IC4_CO2_COMBUSTION+BOILER_C_NC5_CO2_COMBUSTION+BOILER_C_IC5_CO2_COMBUSTION | 2.3084
BOILER_C_CONVECTION_DUTY | BOILER C CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY+BOILER_C_SH_DUTY+BOILER_C_STACK_LOSS_CORRECTED) | 0
BOILER_C_CORRECTED_BFW_FLOW | BOILER C CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_C_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-DESUPERHEATER_C_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_C))/1000) | 0
BOILER_C_CORRECTED_COMBUSTION_AIR | BOILER C CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_C_AIR_MOISTURE) | 14.4151
BOILER_C_CORRECTED_COMBUTION_H2O_FORMED | BOILER C CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2O_FORMED+(BOILER_C_CORRECTED_COMBUSTION_AIR-BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679
BOILER_C_CORRECTED_FUEL_FLOW | BOILER C CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW-((BOILER_C_FUEL_GAS_ENERGY_INPUT-(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY+BOILER_C_BLOWDOWN_LOSS+BOILER_C_STACK_LOSS+BOILER_C_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_C_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOA | 0
BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER C CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | 0
BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER C CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9663
BOILER_C_CP_CH4_FUEL_TEMP | BOILER C CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3611
BOILER_C_CP_ETHANE_FUEL_TEMP | BOILER C CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0719
BOILER_C_CP_ETHYLENE_FUEL_TEMP | BOILER C CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6636
BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER C CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6502
BOILER_C_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER C CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER C CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_C_CP_H2_FUEL_TEMP | BOILER C CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8451
BOILER_C_CP_IC4_FUEL_TEMP | BOILER C CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.104
BOILER_C_CP_IC5_FUEL_TEMP | BOILER C CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8774
BOILER_C_CP_NC4_FUEL_TEMP | BOILER C CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9243
BOILER_C_CP_NC5_FUEL_TEMP | BOILER C CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1613
BOILER_C_CP_OF_AIR_AT_STACK_TEMP | BOILER C CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_C_STACK_TEMPERATURE+273.15)/ | 6.9676
BOILER_C_CP_OF_H2O_AT_STACK_TEMP | BOILER C CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_C_CP_PROPANE_FUEL_TEMP | BOILER C CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0441
BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER C CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_C_CP_H2_FUEL_TEMP+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_C_CP_CH4_FUEL_TEMP+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_C_CP_ETHYLENE_FUEL_TEMP+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7284
BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER C CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_C_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229
BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_C_EXCESS_AIR*(1-BOILER_C_AIR_MOISTURE)+BOILER_C_N2_FORMED+BOILER_C_CO2_FORMED | 13.4993
BOILER_C_ECONOMIZER_DUTY | BOILER C ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_C_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_C_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0
BOILER_C_ENERGY_GAINED | BOILER C ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY) | 0
BOILER_C_ETHANE_CO2_COMBUSTION | BOILER C ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103
BOILER_C_ETHANE_H2O_COMBUSTION | BOILER C ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977
BOILER_C_ETHANE_N2_COMBUSTION | BOILER C ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072
BOILER_C_ETHYLENE_CO2_COMBUSTION | BOILER C ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*3.138 | 0
BOILER_C_ETHYLENE_H2O_COMBUSTION | BOILER C ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*1.285 | 0
BOILER_C_ETHYLENE_N2_COMBUSTION | BOILER C ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*11.385 | 0
BOILER_C_EXCESS_AIR | BOILER C EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_C_FLUE_GAS_OXGYGEN)*((BOILER_C_N2_FORMED/28.01)+(BOILER_C_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_C_CO2_FORMED/44.01))/(20.95-BOILER_C_FLUE_GAS_OXGYGEN)) | 0.11442
BOILER_C_FG_CH4_MASS_FRACTION | BOILER C FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_CH4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_C_FG_CH4_MASS_PERCENTAGE | BOILER C FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_C_FG_MW | 79.4217
BOILER_C_FG_DENSITY | BOILER C FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_C_FG_MW/22.414 | 0.7893
BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER C FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_C_FG_ETHANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_C_FG_ETHANE_MASS_PERCENTAGE | BOILER C FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_C_FG_MW | 2.6684
BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER C FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE | BOILER C FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_C_FG_MW | 0
BOILER_C_FG_FLOW_RATE | BOILER C FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_C_FUEL_GAS_FLOW/1000 | 0.1755
BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER C FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE | BOILER C FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_C_FG_MW | 0
BOILER_C_FG_IC4_MASS_FRACTION | BOILER C FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_IC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_C_FG_IC4_MASS_PERCENTAGE | BOILER C FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | 0.31885
BOILER_C_FG_IC5_MASS_FRACTION | BOILER C FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_IC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_C_FG_IC5_MASS_PERCENTAGE | BOILER C FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | 0.13466
BOILER_C_FG_MW | BOILER C FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_C_FG_IC4_CONCENTRATIO | 17.6914
BOILER_C_FG_NC4_MASS_FRACTION | BOILER C FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_C_FG_NC4_MASS_PERCENTAGE | BOILER C FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | 0.37802
BOILER_C_FG_NC5_MASS_FRACTION | BOILER C FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_C_FG_NC5_MASS_PERCENTAGE | BOILER C FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | 0.004081
BOILER_C_FG_NITROGEN_MASS_FRACTION | BOILER C FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_C_FG_NITROGEN_MASS_PERCENTAGE | BOILER C FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_C_FG_MW | 16.219
BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER C FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_PROPANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_C_FG_PROPANE_MASS_PERCENTAGE | BOILER C FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_C_FG_MW | 0.85531
BOILER_C_FLUE_GAS_MW | BOILER C FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_C_CO2_FORMED/44.01+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.96) | 27.6617
BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | 15.3673
BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER C FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942
BOILER_C_FUEL_CONSUMPTION | BOILER C FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | 0
BOILER_C_FUEL_GAS_CORRECTED_TPH | BOILER C FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW/1000) | 0
BOILER_C_FUEL_GAS_ENERGY_INPUT | BOILER C FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_FG_FLOW_RATE*1000*BOILER_C_MIXED_LHV_PER_KG/10^6) | 0
BOILER_C_H2O_FORMED | BOILER C H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2_H2O_COMBUSTION+BOILER_C_CH4_H2O_COMBUSTION+BOILER_C_ETHANE_H2O_COMBUSTION+BOILER_C_ETHYLENE_H2O_COMBUSTION+BOILER_C_PROPANE_H2O_COMBUSTION+BOILER_C_IC4_H2O_COMBUSTION+BOILER_C_NC4_H2O_COMBUSTION+BOILER_C_IC5_H2O_COMBUSTION+BOILER_C_NC5_H2O_COMBUSTION | 1.8586
BOILER_C_H2_CO2_COMBUSTION | BOILER C H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*0 | 0
BOILER_C_H2_H2O_COMBUSTION | BOILER C H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*8.937 | 0
BOILER_C_H2_N2_COMBUSTION | BOILER C H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*26.407 | 0
BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER C HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_C_STACK_TEMPERATURE-15.6)))) | 0
BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER C HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,9*(BOILER_C_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_C_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_C_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0
BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER C HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_C_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0
BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER C HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,0*10^-6*28*5654*BOILER_C_BOILER_LOAD) | 0
BOILER_C_HP_STEAM_ENTHALPY | BOILER C HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_C)+2.66244961166282*DESUPERHEATER_C_OUTLET_TEMPERATURE)*0.239+2) | 0
BOILER_C_IC4_CO2_COMBUSTION | BOILER C IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*3.029 | 0.009658
BOILER_C_IC4_H2O_COMBUSTION | BOILER C IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*1.55 | 0.005859
BOILER_C_IC4_N2_COMBUSTION | BOILER C IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*11.908 | 0.037969
BOILER_C_IC5_CO2_COMBUSTION | BOILER C IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*3.05 | 0.004107
BOILER_C_IC5_H2O_COMBUSTION | BOILER C IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*1.498 | 0.002017
BOILER_C_IC5_N2_COMBUSTION | BOILER C IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*11.805 | 0.015897
BOILER_C_LHV | BOILER C LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_C_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_C_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_C_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_C_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_C_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_C_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_C_FG_N | 9984.6019
BOILER_C_LHV_DESIGEN | BOILER C LHV DESIGEN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_C_FG_DENSITY)/1000 | 39.6755
BOILER_C_MIXED_LHV_PER_KG | BOILER C MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019
BOILER_C_N2_FORMED | BOILER C N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2_N2_COMBUSTION+BOILER_C_CH4_N2_COMBUSTION+BOILER_C_ETHANE_N2_COMBUSTION+BOILER_C_ETHYLENE_N2_COMBUSTION+BOILER_C_PROPANE_N2_COMBUSTION+BOILER_C_IC4_N2_COMBUSTION+BOILER_C_NC4_N2_COMBUSTION+BOILER_C_IC5_N2_COMBUSTION+BOILER_C_NC5_N2_COMBUSTION | 11.0766
BOILER_C_NC4_CO2_COMBUSTION | BOILER C NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*3.029 | 0.01145
BOILER_C_NC4_H2O_COMBUSTION | BOILER C NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*1.55 | 0.004942
BOILER_C_NC4_N2_COMBUSTION | BOILER C NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*11.908 | 0.045014
BOILER_C_NC5_CO2_COMBUSTION | BOILER C NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*3.05 | 0.000124
BOILER_C_NC5_H2O_COMBUSTION | BOILER C NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05
BOILER_C_NC5_N2_COMBUSTION | BOILER C NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*11.805 | 0.000482
BOILER_C_PROPANE_CO2_COMBUSTION | BOILER C PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608
BOILER_C_PROPANE_H2O_COMBUSTION | BOILER C PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976
BOILER_C_PROPANE_N2_COMBUSTION | BOILER C PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327
BOILER_C_RADIATION_DUTY | BOILER C RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_ENERGY_GAINED-BOILER_C_CONVECTION_DUTY) | 0
BOILER_C_RADIATION_LOSSES | BOILER C RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_MIXED_LHV_PER_KG*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOAD^2-0.0899*BOILER_C_BOILER_LOAD+3.2426)/100) | 0
BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER C SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_C_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_C_AIR_FUEL_MASS_RATIO | -50.7916
BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER C SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0
BOILER_C_SH_DUTY | BOILER C SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_C_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_C_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | 0
BOILER_C_SH_PERFORMANCE | BOILER C SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,(BOILER_C_SH_SPECIFIC_DUTY)/0.110075721*100) | 0
BOILER_C_SH_SPECIFIC_DUTY | BOILER C SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_C_STATUS==0,0,BOILER_C_SH_DUTY/DESUPERHEATER_C_OUTLET_STEAM_FLOW*1000) | 0
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER C SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)) | 0
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER C SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)*4.184) | 0
BOILER_C_STACK_LOSS | BOILER C STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_FLOW/(1000*1000)) | 0
BOILER_C_STACK_LOSS_CORRECTED | BOILER C STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_CORRECTED_TPH/1000) | 0
BOILER_C_STATUS | BOILER C STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_C_BOILER_LOAD>25&&DESUPERHEATER_C_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_C>40,1,0) | 0
BOILER_C_STEAM_DRUM_TEMP | BOILER C STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_C_STATUS==0,0,4.02521999671835*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0
BOILER_C_STEAM_TO_FIRE_DUTY_RATIO | BOILER C STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW/(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG)*1000) | 0
BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER C TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0
BOILER_C_TOTAL_FLUE_GAS_CORRECTED | BOILER C TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_CORRECTED_TPH*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_C_TOTAL_FLUE_GAS_GENERATED | BOILER C TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW/1000*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER C TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_CH4_MASS_PERCENTAGE+BOILER_C_FG_ETHANE_MASS_PERCENTAGE+BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_C_FG_PROPANE_MASS_PERCENTAGE+BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_C_FG_NITROGEN_MASS_PERCENTAGE+BOILER_C_FG_IC4_MASS_PERCENTAGE+BOILER_C_FG_NC4_MASS_PERCENTAGE+BOILER_C_FG_NC5_MASS_P | 100
BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER C TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_TOTAL_MOISTURE_WITH_AIR+BOILER_C_H2O_FORMED | 1.868
BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER C TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0
BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER C TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_C_MIXED_LHV_PER_KG) | 0
BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER C TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_C_RADIATION_LOSSES) | 0
BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER C TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_AIR_MOISTURE | 0.009372
BOILER_C_TOTAL_STEAM_ENERGY | BOILER C TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_HP_STEAM_ENTHALPY/1000000) | 0
BOILER_C_VAPOUR_PRESSURE_OF_H2O | BOILER C VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER D AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_D_AIR_CP_REF_T+BOILER_D_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044
BOILER_D_AIR_CP_REF_T | BOILER D AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_D_AIR_FUEL_MASS_RATIO | BOILER D AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_EXCESS_AIR+BOILER_D_CORRECTED_COMBUSTION_AIR | 14.5272
BOILER_D_AIR_MOISTURE | BOILER D AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_D_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_D_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER D AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*17.265 | 13.7122
BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER D AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058
BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011
BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*14.807 | 0
BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER D AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*34.344 | 0
BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER D AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*15.487 | 0.04938
BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER D AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*15.353 | 0.020674
BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER D AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*15.487 | 0.058544
BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER D AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*15.353 | 0.000626
BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER D AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431
BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER D AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_D_CO2_FORMED/44.01+BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.85*BOILER_D_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_D_FLUE_GAS_MW)/BOILER_D_FLUE_GAS_MW | 0.21038
BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER D AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_D_FG_MW)/2 | 0.43669
BOILER_D_BFW_ENERGY | BOILER D BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*BOILER_D_BFW_ENTHALPY/1000) | 0
BOILER_D_BFW_ENTHALPY | BOILER D BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_D_INLET_TEMPERATURE) | 0
BOILER_D_BLOWDOWN_LOSS | BOILER D BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,((CBD_BLOW_DOWN_D/1000)*((BOILER_D_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | 0
BOILER_D_BOILER_LOAD | BOILER D BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_D_OUTLET_STEAM_FLOW/150000*100 | 1.8534
BOILER_D_CALCULATED_AIRFLOW_NM3H | BOILER D CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_D_STATUS==0,0,BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0
BOILER_D_CH4_CO2_COMBUSTION | BOILER D CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*2.744 | 2.1793
BOILER_D_CH4_H2O_COMBUSTION | BOILER D CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*2.246 | 1.7838
BOILER_D_CH4_N2_COMBUSTION | BOILER D CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*13.275 | 10.5432
BOILER_D_CO2_EMISSIONS | BOILER D CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_CO2_FORMED*BOILER_D_FUEL_GAS_CORRECTED_TPH) | 0
BOILER_D_CO2_FORMED | BOILER D CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_CH4_CO2_COMBUSTION+BOILER_D_ETHANE_CO2_COMBUSTION+BOILER_D_ETHYLENE_CO2_COMBUSTION+BOILER_D_PROPANE_CO2_COMBUSTION+BOILER_D_NC4_CO2_COMBUSTION+BOILER_D_IC4_CO2_COMBUSTION+BOILER_D_NC5_CO2_COMBUSTION+BOILER_D_IC5_CO2_COMBUSTION | 2.3084
BOILER_D_CONVECTION_DUTY | BOILER D CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY+BOILER_D_SH_DUTY+BOILER_D_STACK_LOSS_CORRECTED) | 0
BOILER_D_CORRECTED_BFW_FLOW | BOILER D CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_D_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-DESUPERHEATER_D_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_D))/1000) | 0
BOILER_D_CORRECTED_COMBUSTION_AIR | BOILER D CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_D_AIR_MOISTURE) | 14.4151
BOILER_D_CORRECTED_COMBUTION_H2O_FORMED | BOILER D CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2O_FORMED+(BOILER_D_CORRECTED_COMBUSTION_AIR-BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679
BOILER_D_CORRECTED_FUEL_FLOW | BOILER D CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW-((BOILER_D_FUEL_GAS_ENERGY_INPUT-(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY+BOILER_D_BLOWDOWN_LOSS+BOILER_D_STACK_LOSS+BOILER_D_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_D_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOA | 0
BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER D CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | 0
BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER D CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | 6.9662
BOILER_D_CP_CH4_FUEL_TEMP | BOILER D CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3611
BOILER_D_CP_ETHANE_FUEL_TEMP | BOILER D CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.072
BOILER_D_CP_ETHYLENE_FUEL_TEMP | BOILER D CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6636
BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER D CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6481
BOILER_D_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER D CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2) | 8.3661
BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER D CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_D_CP_H2_FUEL_TEMP | BOILER D CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8451
BOILER_D_CP_IC4_FUEL_TEMP | BOILER D CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1042
BOILER_D_CP_IC5_FUEL_TEMP | BOILER D CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.8775
BOILER_D_CP_NC4_FUEL_TEMP | BOILER D CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9244
BOILER_D_CP_NC5_FUEL_TEMP | BOILER D CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.1614
BOILER_D_CP_OF_AIR_AT_STACK_TEMP | BOILER D CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_D_STACK_TEMPERATURE+273.15)/ | 6.9675
BOILER_D_CP_OF_H2O_AT_STACK_TEMP | BOILER D CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_D_CP_PROPANE_FUEL_TEMP | BOILER D CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0442
BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER D CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_D_CP_H2_FUEL_TEMP+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_D_CP_CH4_FUEL_TEMP+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_D_CP_ETHYLENE_FUEL_TEMP+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7284
BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER D CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_D_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229
BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_D_EXCESS_AIR*(1-BOILER_D_AIR_MOISTURE)+BOILER_D_N2_FORMED+BOILER_D_CO2_FORMED | 13.497
BOILER_D_ECONOMIZER_DUTY | BOILER D ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_D_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_D_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0
BOILER_D_ENERGY_GAINED | BOILER D ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY) | 0
BOILER_D_ETHANE_CO2_COMBUSTION | BOILER D ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103
BOILER_D_ETHANE_H2O_COMBUSTION | BOILER D ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977
BOILER_D_ETHANE_N2_COMBUSTION | BOILER D ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072
BOILER_D_ETHYLENE_CO2_COMBUSTION | BOILER D ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*3.138 | 0
BOILER_D_ETHYLENE_H2O_COMBUSTION | BOILER D ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*1.285 | 0
BOILER_D_ETHYLENE_N2_COMBUSTION | BOILER D ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*11.385 | 0
BOILER_D_EXCESS_AIR | BOILER D EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_D_FLUE_GAS_OXGYGEN)*((BOILER_D_N2_FORMED/28.01)+(BOILER_D_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_D_CO2_FORMED/44.01))/(20.95-BOILER_D_FLUE_GAS_OXGYGEN)) | 0.1121
BOILER_D_FG_CH4_MASS_FRACTION | BOILER D FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_CH4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_D_FG_CH4_MASS_PERCENTAGE | BOILER D FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_D_FG_MW | 79.4217
BOILER_D_FG_DENSITY | BOILER D FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_D_FG_MW/22.414 | 0.7893
BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER D FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_D_FG_ETHANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_D_FG_ETHANE_MASS_PERCENTAGE | BOILER D FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_D_FG_MW | 2.6684
BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER D FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE | BOILER D FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_D_FG_MW | 0
BOILER_D_FG_FLOW_RATE | BOILER D FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_D_FUEL_GAS_FLOW/1000 | 0.17549
BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER D FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE | BOILER D FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_D_FG_MW | 0
BOILER_D_FG_IC4_MASS_FRACTION | BOILER D FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_IC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_D_FG_IC4_MASS_PERCENTAGE | BOILER D FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | 0.31885
BOILER_D_FG_IC5_MASS_FRACTION | BOILER D FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_IC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_D_FG_IC5_MASS_PERCENTAGE | BOILER D FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | 0.13466
BOILER_D_FG_MW | BOILER D FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_D_FG_IC4_CONCENTRATIO | 17.6914
BOILER_D_FG_NC4_MASS_FRACTION | BOILER D FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_D_FG_NC4_MASS_PERCENTAGE | BOILER D FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | 0.37802
BOILER_D_FG_NC5_MASS_FRACTION | BOILER D FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_D_FG_NC5_MASS_PERCENTAGE | BOILER D FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | 0.004081
BOILER_D_FG_NITROGEN_MASS_FRACTION | BOILER D FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_D_FG_NITROGEN_MASS_PERCENTAGE | BOILER D FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_D_FG_MW | 16.219
BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER D FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_PROPANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_D_FG_PROPANE_MASS_PERCENTAGE | BOILER D FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_D_FG_MW | 0.85531
BOILER_D_FLUE_GAS_MW | BOILER D FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_D_CO2_FORMED/44.01+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.96) | 27.6615
BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | 15.365
BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER D FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942
BOILER_D_FUEL_CONSUMPTION | BOILER D FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | 0
BOILER_D_FUEL_GAS_CORRECTED_TPH | BOILER D FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW/1000) | 0
BOILER_D_FUEL_GAS_ENERGY_INPUT | BOILER D FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_FG_FLOW_RATE*1000*BOILER_D_MIXED_LHV_PER_KG/10^6) | 0
BOILER_D_H2O_FORMED | BOILER D H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2_H2O_COMBUSTION+BOILER_D_CH4_H2O_COMBUSTION+BOILER_D_ETHANE_H2O_COMBUSTION+BOILER_D_ETHYLENE_H2O_COMBUSTION+BOILER_D_PROPANE_H2O_COMBUSTION+BOILER_D_IC4_H2O_COMBUSTION+BOILER_D_NC4_H2O_COMBUSTION+BOILER_D_IC5_H2O_COMBUSTION+BOILER_D_NC5_H2O_COMBUSTION | 1.8586
BOILER_D_H2_CO2_COMBUSTION | BOILER D H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*0 | 0
BOILER_D_H2_H2O_COMBUSTION | BOILER D H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*8.937 | 0
BOILER_D_H2_N2_COMBUSTION | BOILER D H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*26.407 | 0
BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER D HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_D_STACK_TEMPERATURE-15.6)))) | 0
BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER D HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,9*(BOILER_D_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_D_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_D_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0
BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER D HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_D_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0
BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER D HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,0*10^-6*28*5654*BOILER_D_BOILER_LOAD) | 0
BOILER_D_HP_STEAM_ENTHALPY | BOILER D HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_D)+2.66244961166282*DESUPERHEATER_D_OUTLET_TEMPERATURE)*0.239+2) | 0
BOILER_D_IC4_CO2_COMBUSTION | BOILER D IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*3.029 | 0.009658
BOILER_D_IC4_H2O_COMBUSTION | BOILER D IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*1.55 | 0.005859
BOILER_D_IC4_N2_COMBUSTION | BOILER D IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*11.908 | 0.037969
BOILER_D_IC5_CO2_COMBUSTION | BOILER D IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*3.05 | 0.004107
BOILER_D_IC5_H2O_COMBUSTION | BOILER D IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*1.498 | 0.002017
BOILER_D_IC5_N2_COMBUSTION | BOILER D IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*11.805 | 0.015897
BOILER_D_LHV | BOILER D LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_D_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_D_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_D_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_D_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_D_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_D_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_D_FG_N | 9984.6019
BOILER_D_LHV_DESIGEN | BOILER D LHV DESIGEN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_D_FG_DENSITY)/1000 | 39.6755
BOILER_D_MIXED_LHV_PER_KG | BOILER D MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | 9984.6019
BOILER_D_N2_FORMED | BOILER D N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2_N2_COMBUSTION+BOILER_D_CH4_N2_COMBUSTION+BOILER_D_ETHANE_N2_COMBUSTION+BOILER_D_ETHYLENE_N2_COMBUSTION+BOILER_D_PROPANE_N2_COMBUSTION+BOILER_D_IC4_N2_COMBUSTION+BOILER_D_NC4_N2_COMBUSTION+BOILER_D_IC5_N2_COMBUSTION+BOILER_D_NC5_N2_COMBUSTION | 11.0766
BOILER_D_NC4_CO2_COMBUSTION | BOILER D NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*3.029 | 0.01145
BOILER_D_NC4_H2O_COMBUSTION | BOILER D NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*1.55 | 0.004942
BOILER_D_NC4_N2_COMBUSTION | BOILER D NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*11.908 | 0.045014
BOILER_D_NC5_CO2_COMBUSTION | BOILER D NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*3.05 | 0.000124
BOILER_D_NC5_H2O_COMBUSTION | BOILER D NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05
BOILER_D_NC5_N2_COMBUSTION | BOILER D NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*11.805 | 0.000482
BOILER_D_PROPANE_CO2_COMBUSTION | BOILER D PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608
BOILER_D_PROPANE_H2O_COMBUSTION | BOILER D PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976
BOILER_D_PROPANE_N2_COMBUSTION | BOILER D PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327
BOILER_D_RADIATION_DUTY | BOILER D RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_ENERGY_GAINED-BOILER_D_CONVECTION_DUTY) | 0
BOILER_D_RADIATION_LOSSES | BOILER D RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_MIXED_LHV_PER_KG*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOAD^2-0.0899*BOILER_D_BOILER_LOAD+3.2426)/100) | 0
BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER D SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_D_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_D_AIR_FUEL_MASS_RATIO | -51.4889
BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER D SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0
BOILER_D_SH_DUTY | BOILER D SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_D_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_D_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | 0
BOILER_D_SH_PERFORMANCE | BOILER D SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,(BOILER_D_SH_SPECIFIC_DUTY)/0.110075721*100) | 0
BOILER_D_SH_SPECIFIC_DUTY | BOILER D SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_D_STATUS==0,0,BOILER_D_SH_DUTY/DESUPERHEATER_D_OUTLET_STEAM_FLOW*1000) | 0
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER D SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)) | 0
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER D SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)*4.184) | 0
BOILER_D_STACK_LOSS | BOILER D STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_FLOW/(1000*1000)) | 0
BOILER_D_STACK_LOSS_CORRECTED | BOILER D STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_CORRECTED_TPH/1000) | 0
BOILER_D_STATUS | BOILER D STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_D_BOILER_LOAD>25&&DESUPERHEATER_D_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_D>40,1,0) | 0
BOILER_D_STEAM_DRUM_TEMP | BOILER D STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_D_STATUS==0,0,4.02521999671835*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0
BOILER_D_STEAM_TO_FIRE_DUTY_RATIO | BOILER D STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW/(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG)*1000) | 0
BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER D TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0
BOILER_D_TOTAL_FLUE_GAS_CORRECTED | BOILER D TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_CORRECTED_TPH*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_D_TOTAL_FLUE_GAS_GENERATED | BOILER D TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW/1000*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER D TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_CH4_MASS_PERCENTAGE+BOILER_D_FG_ETHANE_MASS_PERCENTAGE+BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_D_FG_PROPANE_MASS_PERCENTAGE+BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_D_FG_NITROGEN_MASS_PERCENTAGE+BOILER_D_FG_IC4_MASS_PERCENTAGE+BOILER_D_FG_NC4_MASS_PERCENTAGE+BOILER_D_FG_NC5_MASS_P | 100
BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER D TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_TOTAL_MOISTURE_WITH_AIR+BOILER_D_H2O_FORMED | 1.868
BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER D TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0
BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER D TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_D_MIXED_LHV_PER_KG) | 0
BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER D TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_D_RADIATION_LOSSES) | 0
BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER D TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_AIR_MOISTURE | 0.009371
BOILER_D_TOTAL_STEAM_ENERGY | BOILER D TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_HP_STEAM_ENTHALPY/1000000) | 0
BOILER_D_VAPOUR_PRESSURE_OF_H2O | BOILER D VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER E AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_E_AIR_CP_REF_T+BOILER_E_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | 0.24044
BOILER_E_AIR_CP_REF_T | BOILER E AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | 6.96
BOILER_E_AIR_FUEL_MASS_RATIO | BOILER E AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_EXCESS_AIR+BOILER_E_CORRECTED_COMBUSTION_AIR | 14.5458
BOILER_E_AIR_MOISTURE | BOILER E AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_E_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_E_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER E AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*17.265 | 13.7122
BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER E AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | 14.4058
BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | 0.43011
BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*14.807 | 0
BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER E AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*34.344 | 0
BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER E AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*15.487 | 0.04938
BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER E AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*15.353 | 0.020674
BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER E AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*15.487 | 0.058544
BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER E AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*15.353 | 0.000626
BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER E AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*15.703 | 0.13431
BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER E AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_E_CO2_FORMED/44.01+BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.85*BOILER_E_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_E_FLUE_GAS_MW)/BOILER_E_FLUE_GAS_MW | 0.21045
BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER E AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_E_FG_MW)/2 | 0.43677
BOILER_E_BFW_ENERGY | BOILER E BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*BOILER_E_BFW_ENTHALPY/1000) | 0
BOILER_E_BFW_ENTHALPY | BOILER E BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_E_INLET_TEMPERATURE) | 0
BOILER_E_BLOWDOWN_LOSS | BOILER E BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,((CBD_BLOW_DOWN_E/1000)*((BOILER_E_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_E_STEAM_DRUM_TEMP*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_E_STEAM_DRUM_TEMP*4.22416911685416-3.01717714574329)*0.2390006))/1000) | 0
BOILER_E_BOILER_LOAD | BOILER E BOILER LOAD | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | DESUPERHEATER_E_OUTLET_STEAM_FLOW/150000*100 | 1.8692
BOILER_E_CALCULATED_AIRFLOW_NM3H | BOILER E CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_E_STATUS==0,0,BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | 0
BOILER_E_CH4_CO2_COMBUSTION | BOILER E CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*2.744 | 2.1793
BOILER_E_CH4_H2O_COMBUSTION | BOILER E CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*2.246 | 1.7838
BOILER_E_CH4_N2_COMBUSTION | BOILER E CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*13.275 | 10.5432
BOILER_E_CO2_EMISSIONS | BOILER E CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_CO2_FORMED*BOILER_E_FUEL_GAS_CORRECTED_TPH) | 0
BOILER_E_CO2_FORMED | BOILER E CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_CH4_CO2_COMBUSTION+BOILER_E_ETHANE_CO2_COMBUSTION+BOILER_E_ETHYLENE_CO2_COMBUSTION+BOILER_E_PROPANE_CO2_COMBUSTION+BOILER_E_NC4_CO2_COMBUSTION+BOILER_E_IC4_CO2_COMBUSTION+BOILER_E_NC5_CO2_COMBUSTION+BOILER_E_IC5_CO2_COMBUSTION | 2.3084
BOILER_E_CONVECTION_DUTY | BOILER E CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY+BOILER_E_SH_DUTY+BOILER_E_STACK_LOSS_CORRECTED) | 0
BOILER_E_CORRECTED_BFW_FLOW | BOILER E CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_E_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-DESUPERHEATER_E_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_E))/1000) | 0
BOILER_E_CORRECTED_COMBUSTION_AIR | BOILER E CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_E_AIR_MOISTURE) | 14.4151
BOILER_E_CORRECTED_COMBUTION_H2O_FORMED | BOILER E CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2O_FORMED+(BOILER_E_CORRECTED_COMBUSTION_AIR-BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | 1.8679
BOILER_E_CORRECTED_FUEL_FLOW | BOILER E CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295-((BOILER_E_FUEL_GAS_ENERGY_INPUT-(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY+BOILER_E_BLOWDOWN_LOSS+BOILER_E_STACK_LOSS+BOILER_E_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_E_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOIL | 0
BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER E CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | 0
BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER E CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)-9.647459*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2+16.63537*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^3+(0.000117/((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_COMBUSTION_AIR_TEM | 6.9665
BOILER_E_CP_CH4_FUEL_TEMP | BOILER E CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.3641
BOILER_E_CP_ETHANE_FUEL_TEMP | BOILER E CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | 12.0902
BOILER_E_CP_ETHYLENE_FUEL_TEMP | BOILER E CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | 9.6778
BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER E CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6572
BOILER_E_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER E CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2) | 8.3667
BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER E CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9587
BOILER_E_CP_H2_FUEL_TEMP | BOILER E CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.8465
BOILER_E_CP_IC4_FUEL_TEMP | BOILER E CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 27.1642
BOILER_E_CP_IC5_FUEL_TEMP | BOILER E CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 25.9245
BOILER_E_CP_NC4_FUEL_TEMP | BOILER E CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | 22.9597
BOILER_E_CP_NC5_FUEL_TEMP | BOILER E CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | 26.2004
BOILER_E_CP_OF_AIR_AT_STACK_TEMP | BOILER E CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_STACK_TEMPERATURE+273.15)/ | 6.9677
BOILER_E_CP_OF_H2O_AT_STACK_TEMP | BOILER E CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.46443
BOILER_E_CP_PROPANE_FUEL_TEMP | BOILER E CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | 17.0717
BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER E CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_E_CP_H2_FUEL_TEMP+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_E_CP_CH4_FUEL_TEMP+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_E_CP_ETHYLENE_FUEL_TEMP+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | 7.7312
BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER E CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_E_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | 7.7229
BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_E_EXCESS_AIR*(1-BOILER_E_AIR_MOISTURE)+BOILER_E_N2_FORMED+BOILER_E_CO2_FORMED | 13.5156
BOILER_E_ECONOMIZER_DUTY | BOILER E ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_E_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_E_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | 0
BOILER_E_ENERGY_GAINED | BOILER E ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY) | 0
BOILER_E_ETHANE_CO2_COMBUSTION | BOILER E ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*2.927 | 0.078103
BOILER_E_ETHANE_H2O_COMBUSTION | BOILER E ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*1.798 | 0.047977
BOILER_E_ETHANE_N2_COMBUSTION | BOILER E ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*12.394 | 0.33072
BOILER_E_ETHYLENE_CO2_COMBUSTION | BOILER E ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*3.138 | 0
BOILER_E_ETHYLENE_H2O_COMBUSTION | BOILER E ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*1.285 | 0
BOILER_E_ETHYLENE_N2_COMBUSTION | BOILER E ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*11.385 | 0
BOILER_E_EXCESS_AIR | BOILER E EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_E_FLUE_GAS_OXGYGEN_NEW)*((BOILER_E_N2_FORMED/28.01)+(BOILER_E_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_E_CO2_FORMED/44.01))/(20.95-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | 0.13068
BOILER_E_FG_CH4_MASS_FRACTION | BOILER E FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_CH4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_E_FG_CH4_MASS_PERCENTAGE | BOILER E FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_E_FG_MW | 79.4217
BOILER_E_FG_DENSITY | BOILER E FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_E_FG_MW/22.414 | 0.7893
BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER E FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_E_FG_ETHANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_E_FG_ETHANE_MASS_PERCENTAGE | BOILER E FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_E_FG_MW | 2.6684
BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER E FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE | BOILER E FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_E_FG_MW | 0
BOILER_E_FG_FLOW_RATE | BOILER E FG FLOW RATE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | TPH | BOILER_E_FUEL_GAS_FLOW/1.295/1000 | 0.17993
BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER E FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE | BOILER E FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_E_FG_MW | 0
BOILER_E_FG_IC4_MASS_FRACTION | BOILER E FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_IC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_E_FG_IC4_MASS_PERCENTAGE | BOILER E FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | 0.31885
BOILER_E_FG_IC5_MASS_FRACTION | BOILER E FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_IC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_E_FG_IC5_MASS_PERCENTAGE | BOILER E FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | 0.13466
BOILER_E_FG_MW | BOILER E FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_E_FG_IC4_CONCENTRATIO | 17.6914
BOILER_E_FG_NC4_MASS_FRACTION | BOILER E FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_E_FG_NC4_MASS_PERCENTAGE | BOILER E FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | 0.37802
BOILER_E_FG_NC5_MASS_FRACTION | BOILER E FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_E_FG_NC5_MASS_PERCENTAGE | BOILER E FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | 0.004081
BOILER_E_FG_NITROGEN_MASS_FRACTION | BOILER E FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_E_FG_NITROGEN_MASS_PERCENTAGE | BOILER E FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_E_FG_MW | 16.219
BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER E FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_PROPANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_E_FG_PROPANE_MASS_PERCENTAGE | BOILER E FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_E_FG_MW | 0.85531
BOILER_E_FLUE_GAS_MW | BOILER E FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_E_CO2_FORMED/44.01+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.96) | 27.663
BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | 15.3836
BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER E FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | 99.942
BOILER_E_FUEL_CONSUMPTION | BOILER E FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | 0
BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER E FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW/1000) | 0
BOILER_E_FUEL_GAS_ENERGY_INPUT | BOILER E FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_FG_FLOW_RATE*1000*BOILER_E_MIXED_LHV_PER_KG/10^6) | 0
BOILER_E_H2O_FORMED | BOILER E H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2_H2O_COMBUSTION+BOILER_E_CH4_H2O_COMBUSTION+BOILER_E_ETHANE_H2O_COMBUSTION+BOILER_E_ETHYLENE_H2O_COMBUSTION+BOILER_E_PROPANE_H2O_COMBUSTION+BOILER_E_IC4_H2O_COMBUSTION+BOILER_E_NC4_H2O_COMBUSTION+BOILER_E_IC5_H2O_COMBUSTION+BOILER_E_NC5_H2O_COMBUSTION | 1.8586
BOILER_E_H2_CO2_COMBUSTION | BOILER E H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*0 | 0
BOILER_E_H2_H2O_COMBUSTION | BOILER E H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*8.937 | 0
BOILER_E_H2_N2_COMBUSTION | BOILER E H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*26.407 | 0
BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER E HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_E_STACK_TEMPERATURE-15.6)))) | 0
BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER E HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,9*(BOILER_E_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_E_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_E_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | 0
BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER E HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_E_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | 0
BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER E HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,0*10^-6*28*5654*BOILER_E_BOILER_LOAD) | 0
BOILER_E_HP_STEAM_ENTHALPY | BOILER E HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_E)+2.66244961166282*DESUPERHEATER_E_OUTLET_TEMPERATURE)*0.239+2) | 0
BOILER_E_IC4_CO2_COMBUSTION | BOILER E IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*3.029 | 0.009658
BOILER_E_IC4_H2O_COMBUSTION | BOILER E IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*1.55 | 0.005859
BOILER_E_IC4_N2_COMBUSTION | BOILER E IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*11.908 | 0.037969
BOILER_E_IC5_CO2_COMBUSTION | BOILER E IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*3.05 | 0.004107
BOILER_E_IC5_H2O_COMBUSTION | BOILER E IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*1.498 | 0.002017
BOILER_E_IC5_N2_COMBUSTION | BOILER E IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*11.805 | 0.015897
BOILER_E_LHV | BOILER E LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_E_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_E_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_E_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_E_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_E_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_E_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_E_FG_N | 9984.6019
BOILER_E_LHV_DESIGN | BOILER E LHV DESIGN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_E_FG_DENSITY)/1000 | 39.6755
BOILER_E_MIXED_LHV_PER_KG | BOILER E MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | Kcal/kg | (BOILER_LHV) | 9984.6019
BOILER_E_N2_FORMED | BOILER E N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2_N2_COMBUSTION+BOILER_E_CH4_N2_COMBUSTION+BOILER_E_ETHANE_N2_COMBUSTION+BOILER_E_ETHYLENE_N2_COMBUSTION+BOILER_E_PROPANE_N2_COMBUSTION+BOILER_E_IC4_N2_COMBUSTION+BOILER_E_NC4_N2_COMBUSTION+BOILER_E_IC5_N2_COMBUSTION+BOILER_E_NC5_N2_COMBUSTION | 11.0766
BOILER_E_NC4_CO2_COMBUSTION | BOILER E NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*3.029 | 0.01145
BOILER_E_NC4_H2O_COMBUSTION | BOILER E NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*1.55 | 0.004942
BOILER_E_NC4_N2_COMBUSTION | BOILER E NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*11.908 | 0.045014
BOILER_E_NC5_CO2_COMBUSTION | BOILER E NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*3.05 | 0.000124
BOILER_E_NC5_H2O_COMBUSTION | BOILER E NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*1.498 | 6.1e-05
BOILER_E_NC5_N2_COMBUSTION | BOILER E NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*11.805 | 0.000482
BOILER_E_PROPANE_CO2_COMBUSTION | BOILER E PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*2.994 | 0.025608
BOILER_E_PROPANE_H2O_COMBUSTION | BOILER E PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*1.634 | 0.013976
BOILER_E_PROPANE_N2_COMBUSTION | BOILER E PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*12.074 | 0.10327
BOILER_E_RADIATION_DUTY | BOILER E RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_ENERGY_GAINED-BOILER_E_CONVECTION_DUTY) | 0
BOILER_E_RADIATION_LOSSES | BOILER E RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_MIXED_LHV_PER_KG*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOILER_LOAD^2-0.0899*BOILER_E_BOILER_LOAD+3.2426)/100) | 0
BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER E SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_E_COMBUSTION_AIR_TEMP-15.6)*BOILER_E_AIR_FUEL_MASS_RATIO | -48.2191
BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER E SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | 0
BOILER_E_SH_DUTY | BOILER E SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_E_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_E_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_E_STEAM_DRUM_TEMP*3.45877718874616+2082.10231045632))*0.239006/10000 | 0
BOILER_E_SH_PERFORMANCE | BOILER E SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,(BOILER_E_SH_SPECIFIC_DUTY)/0.110075721*100) | 0
BOILER_E_SH_SPECIFIC_DUTY | BOILER E SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_E_STATUS==0,0,BOILER_E_SH_DUTY/DESUPERHEATER_E_OUTLET_STEAM_FLOW*1000) | 0
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER E SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)) | 0
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER E SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)*4.184) | 0
BOILER_E_STACK_LOSS | BOILER E STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_FLOW/1.295/(1000*1000)) | 0
BOILER_E_STACK_LOSS_CORRECTED | BOILER E STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_CORRECTED_TPH/1000) | 0
BOILER_E_STATUS | BOILER E STATUS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | if(BOILER_E_BOILER_LOAD>25&&DESUPERHEATER_E_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_E>40,1,0) | 0
BOILER_E_STEAM_DRUM_PRESSURE | BOILER E STEAM DRUM PRESSURE | LBM_preprocessing_inferred_tags_main | nan | if(HP_STEAM_PRESSURE_FROM_DS_E==MISSING_NUMERIC,0,HP_STEAM_PRESSURE_FROM_DS_E) | 1.884
BOILER_E_STEAM_DRUM_TEMP | BOILER E STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_E_STATUS==0,0,4.02521999671835*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0
BOILER_E_STEAM_TO_FIRE_DUTY_RATIO | BOILER E STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | KG/ KCAL | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW/(BOILER_E_FG_FLOW_RATE*BOILER_E_MIXED_LHV_PER_KG)*1000) | 0
BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER E TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | 0
BOILER_E_TOTAL_FLUE_GAS_CORRECTED | BOILER E TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_CORRECTED_TPH*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_E_TOTAL_FLUE_GAS_GENERATED | BOILER E TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295/1000*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | 0
BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER E TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_CH4_MASS_PERCENTAGE+BOILER_E_FG_ETHANE_MASS_PERCENTAGE+BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_E_FG_PROPANE_MASS_PERCENTAGE+BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_E_FG_NITROGEN_MASS_PERCENTAGE+BOILER_E_FG_IC4_MASS_PERCENTAGE+BOILER_E_FG_NC4_MASS_PERCENTAGE+BOILER_E_FG_NC5_MASS_P | 100
BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER E TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_TOTAL_MOISTURE_WITH_AIR+BOILER_E_H2O_FORMED | 1.868
BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER E TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | 0
BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER E TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_E_MIXED_LHV_PER_KG) | 0
BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER E TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_E_RADIATION_LOSSES) | 0
BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER E TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_AIR_MOISTURE | 0.009383
BOILER_E_TOTAL_STEAM_ENERGY | BOILER E TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_HP_STEAM_ENTHALPY/1000000) | 0
BOILER_E_VAPOUR_PRESSURE_OF_H2O | BOILER E VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_FG_CH4_CONCENTRATION | BOILER FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CH4_CONCENTRATION_ARRAZI,87.548) | 87.548
BOILER_FG_CO2_CONCENTRATION | BOILER FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CO2_CONCENTRATION_ARRAZI,0) | 0
BOILER_FG_ETHANE_CONCENTRATION | BOILER FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_ETHANE_CONCENTRATION_ARRAZI,1.569) | 1.569
BOILER_FG_ETHYLENE_CONCENTRATION | BOILER FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 0 | 0
BOILER_FG_HYDROGEN_CONCENTRATION | BOILER FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,0,0) | 0
BOILER_FG_IC4_CONCENTRATION | BOILER FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC4_CONCENTRATION_ARRAZI,.097) | 0.097
BOILER_FG_IC5_CONCENTRATION | BOILER FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC5_CONCENTRATION_ARRAZI,.033) | 0.033
BOILER_FG_N2_CONCENTRATION | BOILER FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_N2_CONCENTRATION_ARRAZI,10.236) | 10.236
BOILER_FG_NC4_CONCENTRATION | BOILER FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC4_CONCENTRATION_ARRAZI,.115) | 0.115
BOILER_FG_NC5_CONCENTRATION | BOILER FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC5_CONCENTRATION_ARRAZI,.001) | 0.001
BOILER_FG_PROPANE_CONCENTRATION | BOILER FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_PROPANE_CONCENTRATION_ARRAZI,.343) | 0.343
BOILER_LHV | BOILER LHV | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | Kcal/Kg | (BOILER_A_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_A_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_A_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_A_FG_ETHYLENE_MASS_FRACTION*LHV_C2H4_ETHYLENE+BOILER_A_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_A_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPAN | 9984.6019
Boiler_E_Nox_Emission | Boiler E Nox Emission | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | ng/J | if(BOILER_E_STATUS==0,0,BOILER_E_NOX*46/24.45*1000000*2.07/10000000*20.9/(20.9-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | 0
COMPONENT_BUTANE_MW | COMPONENT BUTANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 58.12 | 58.12
COMPONENT_CO_MW | COMPONENT CO MW | LBM_preprocessing_inferred_tags_main | g/gmol | 28.01 | 28.01
COMPONENT_ETHANE_MW | COMPONENT ETHANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 30.07 | 30.07
COMPONENT_ETHYLENE_MW | COMPONENT ETHYLENE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 28.051 | 28.051
COMPONENT_HYDROGEN_MW | COMPONENT HYDROGEN MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 2.016 | 2.016
COMPONENT_METHANE_MW | COMPONENT METHANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 16.04 | 16.04
COMPONENT_NITROGEN_MW | COMPONENT NITROGEN MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 28.016 | 28.016
COMPONENT_PENTANE_MW | COMPONENT PENTANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 72.15 | 72.15
COMPONENT_PROPANE_MW | COMPONENT PROPANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 44.09 | 44.09
Calc_capacity | CALC CAPACITY | LBM_preprocessing_inferred_tags_main,LBM_postprocessing_capacity_utilization_inferred,LBM_optimum_inferred_tags_main | MT/ HR | (DESUPERHEATER_OUTLET_STEAM_FLOW+DESUPERHEATER_B_OUTLET_STEAM_FLOW+DESUPERHEATER_C_OUTLET_STEAM_FLOW+DESUPERHEATER_D_OUTLET_STEAM_FLOW+DESUPERHEATER_E_OUTLET_STEAM_FLOW) | 13739.292
FIRE_DUTY | FIRE DUTY | LBM_preprocessing_inferred_tags_main | MMBTU/ DAY | ((BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG*1000)*BOILER_A_STATUS+(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG*1000)*BOILER_B_STATUS+(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG*1000)*BOILER_C_STATUS+(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG*1000)*BOILER_D_STATUS+(BOILER_E_FG_FL | 0
LHV_BUTANE | LHV BUTANE | LBM_preprocessing_inferred_tags_main | MJ/KG | 45.689 | 45.689
LHV_C2H4_ETHYLENE | LHV C2H4 ETHYLENE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 47.178 | 47.178
LHV_C2H6_ETHANE | LHV C2H6 ETHANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 47.497 | 47.497
LHV_C3H8_PROPANE | LHV C3H8 PROPANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 46.362 | 46.362
LHV_CH4_METHANE | LHV CH4 METHANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 50.026 | 50.026
LHV_CO | LHV CO | LBM_preprocessing_inferred_tags_main | MJ/KG | 10.105 | 10.105
LHV_FG | LHV FG | LBM_preprocessing_inferred_tags_main | MJ/KG | 31316 | 31316
LHV_FG_E_DESIGN | LHV FG E | LBM_preprocessing_inferred_tags_main | - | 45108 | 45108
LHV_H2O_WATER | LHV H2O WATER | LBM_preprocessing_inferred_tags_main | MJ/KG | 0 | 0
LHV_H2_HYDROGEN | LHV H2 HYDROGEN | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 120.004 | 120.004
LHV_IC4 | LHV IC4 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.613 | 45.613
LHV_IC5 | LHV IC5 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.241 | 45.241
LHV_N2_NITROGEN | LHV N2 NITROGEN | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 0 | 0
LHV_NC4 | LHV NC4 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.75 | 45.75
LHV_NC5 | LHV NC5 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.36 | 45.36
LHV_PENTANE | LHV PENTANE | LBM_preprocessing_inferred_tags_main | MJ/KG | 45.35 | 45.35
NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | NORMALIZED BOILER A FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | 87.5988
NORMALIZED_BOILER_A_FG_CO2_CONCENTRATION | NORMALIZED BOILER A FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER A FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 1.5699
NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER A FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL)*100 | 0
NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER A FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | NORMALIZED BOILER A FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.097056
NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | NORMALIZED BOILER A FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.033019
NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | NORMALIZED BOILER A FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | 10.2419
NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | NORMALIZED BOILER A FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.11507
NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | NORMALIZED BOILER A FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.001001
NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER A FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | 0.3432
NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | NORMALIZED BOILER B FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | 87.5988
NORMALIZED_BOILER_B_FG_CO2_CONCENTRATION | NORMALIZED BOILER B FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER B FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 1.5699
NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER B FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL)*100 | 0
NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER B FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | NORMALIZED BOILER B FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.097056
NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | NORMALIZED BOILER B FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.033019
NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | NORMALIZED BOILER B FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | 10.2419
NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | NORMALIZED BOILER B FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.11507
NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | NORMALIZED BOILER B FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.001001
NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER B FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | 0.3432
NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | NORMALIZED BOILER C FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | 87.5988
NORMALIZED_BOILER_C_FG_CO2_CONCENTRATION | NORMALIZED BOILER C FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER C FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 1.5699
NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER C FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL)*100 | 0
NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER C FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | NORMALIZED BOILER C FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.097056
NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | NORMALIZED BOILER C FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.033019
NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | NORMALIZED BOILER C FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | 10.2419
NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | NORMALIZED BOILER C FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.11507
NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | NORMALIZED BOILER C FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.001001
NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER C FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | 0.3432
NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | NORMALIZED BOILER D FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | 87.5988
NORMALIZED_BOILER_D_FG_CO2_CONCENTRATION | NORMALIZED BOILER D FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER D FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 1.5699
NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER D FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL)*100 | 0
NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER D FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | NORMALIZED BOILER D FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.097056
NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | NORMALIZED BOILER D FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.033019
NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | NORMALIZED BOILER D FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | 10.2419
NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | NORMALIZED BOILER D FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.11507
NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | NORMALIZED BOILER D FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.001001
NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER D FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | 0.3432
NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | NORMALIZED BOILER E FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | 87.5988
NORMALIZED_BOILER_E_FG_CO2_CONCENTRATION | NORMALIZED BOILER E FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER E FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 1.5699
NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER E FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL)*100 | 0
NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER E FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0
NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | NORMALIZED BOILER E FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.097056
NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | NORMALIZED BOILER E FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.033019
NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | NORMALIZED BOILER E FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | 10.2419
NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | NORMALIZED BOILER E FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.11507
NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | NORMALIZED BOILER E FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.001001
NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER E FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | 0.3432
RELATIVE_HUMIDITY_CLEAN | RELATIVE HUMIDITY | LBM_preprocessing_inferred_tags_main | % | if((abs(RELATIVE_HUMIDITY)<1 && abs(RELATIVE_HUMIDITY)>0),abs(RELATIVE_HUMIDITY),0.6) | 0.17
TOTAL_BLOWDOWN_LOSS | TOTAL BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_BLOWDOWN_LOSS+BOILER_B_BLOWDOWN_LOSS+BOILER_C_BLOWDOWN_LOSS+BOILER_D_BLOWDOWN_LOSS+BOILER_E_BLOWDOWN_LOSS | 0
TOTAL_CO2_EMISSIONS | TOTAL CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | BOILER_A_CO2_EMISSIONS+BOILER_B_CO2_EMISSIONS+BOILER_C_CO2_EMISSIONS+BOILER_D_CO2_EMISSIONS+BOILER_E_CO2_EMISSIONS | 0
TOTAL_FUEL_COMPOSTION_MASS | TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_A_FG_CH4_MASS_PERCENTAGE+BOILER_A_FG_ETHANE_MASS_PERCENTAGE+BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_A_FG_PROPANE_MASS_PERCENTAGE+BOILER_A_FG_NC4_MASS_PERCENTAGE+BOILER_A_FG_IC4_MASS_PERCENTAGE+BOILER_A_FG_NC5_MASS_PERCENTAGE+BOILER_A_FG_IC5_MASS_PERCEN | 100
TOTAL_FUEL_CONSUMPTION_GCAL_H | TOTAL FUEL CONSUMPTION GCAL H | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | 0
TOTAL_FUEL_FLOW | TOTAL FUEL FLOW | LBM_preprocessing_inferred_tags_main | Ton/h | (BOILER_A_FUEL_GAS_FLOW+BOILER_B_FUEL_GAS_FLOW+BOILER_C_FUEL_GAS_FLOW+BOILER_D_FUEL_GAS_FLOW+BOILER_E_FUEL_GAS_FLOW/1.295)/1000 | 0.88188
TOTAL_FUEL_TO_AIR_RATIO | TOTAL FUEL TO AIR RATIO | LBM_preprocessing_inferred_tags_main | Kg/ Kg Fuel | BOILER_A_AIR_FUEL_MASS_RATIO+BOILER_B_AIR_FUEL_MASS_RATIO+BOILER_C_AIR_FUEL_MASS_RATIO+BOILER_D_AIR_FUEL_MASS_RATIO+BOILER_E_AIR_FUEL_MASS_RATIO | 72.66
TOTAL_STACK_LOSS_GCAL_H | TOTAL STACK LOSS GCAL/H | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_STACK_LOSS_CORRECTED+BOILER_B_STACK_LOSS_CORRECTED+BOILER_C_STACK_LOSS_CORRECTED+BOILER_D_STACK_LOSS_CORRECTED+BOILER_E_STACK_LOSS_CORRECTED | 0
TOTAL_STEAM_ENERGY | TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_TOTAL_STEAM_ENERGY+BOILER_B_TOTAL_STEAM_ENERGY+BOILER_C_TOTAL_STEAM_ENERGY+BOILER_D_TOTAL_STEAM_ENERGY+BOILER_E_TOTAL_STEAM_ENERGY | 0
TOTAL_STEAM_PRODUCTION | TOTAL STEAM PRODUCTION | LBM_preprocessing_inferred_tags_main | T/h | (DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_STATUS)/1000 | 0
VAPOUR_PRESSURE_OF_WATER | VAPOUR PRESSURE OF WATER | LBM_preprocessing_inferred_tags_main | mmhg | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
plant_status | plant status | LBM_preprocessing_inferred_tags_main | nan | if(BOILERS_ONLINE==0,0,1) | 0

## All_Results
tag_name | description | category | uom | formula | status | value | reason_if_not | missing_inputs | full_potential_value
ARRAZI_PLANT_LOAD_1 | ARRAZI PLANT LOAD 1 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | if(ARRAZI_PLANT_LOAD==MISSING_NUMERIC,0,ARRAZI_PLANT_LOAD) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_LOAD | ARRAZI_PLANT_LOAD | 0
ARRAZI_PLANT_STATUS | ARRAZI PLANT STATUS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_LOAD_1<70,0,1) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_LOAD_1 | ARRAZI_PLANT_LOAD_1 | 0
BFW_QUALITY_RATE | BFW QUALITY RATE | TRG_compute_inferred_post_pta | % | FLAG_BFW_QUALITY_PTA_actual*100/24 | NOT COMPUTED |  | eval_error: name 'FLAG_BFW_QUALITY_PTA_actual' is not defined
BLOWDOWN_CONDUCTIVITY | BLOWDOWN CONDUCTIVITY | LBM_preprocessing_inferred_tags_main | US/ CM | ((BOILER_A_CONDUCTIVITY*BOILER_A_STATUS)+(BOILER_B_CONDUCTIVITY*BOILER_B_STATUS)+(BOILER_C_CONDUCTIVITY*BOILER_C_STATUS)+(BOILER_D_CONDUCTIVITY*BOILER_D_STATUS)+(BOILER_E_CONDUCTIVITY*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_CONDUCTIVITY; BOILER_A_STATUS; BOILER_B_CONDUCTIVITY; BOILER_B_STATUS; BOILER_C_CONDUCTIVITY (+4 more) | BOILERS_ONLINE; BOILER_A_CONDUCTIVITY; BOILER_A_STATUS; BOILER_B_CONDUCTIVITY; BOILER_B_STATUS; BOILER_C_CONDUCTIVITY; BOILER_C_STATUS; BOILER_D_CONDUCTIVITY; BOILER_D_STATUS; BOILER_E_CONDUCTIVITY
BOILERS_ONLINE | BOILERS ONLINE | LBM_preprocessing_inferred_tags_main | - | BOILER_A_STATUS+BOILER_B_STATUS+BOILER_C_STATUS+BOILER_D_STATUS+BOILER_E_STATUS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | 0
BOILER_A_ACTUAL_SP_ENERGY_DELTA | BOILER A ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER A AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_A_AIR_CP_REF_T+BOILER_A_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | 0.24044
BOILER_A_AIR_CP_REF_T | BOILER A AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | COMPUTED | 6.96 |  |  | 6.96
BOILER_A_AIR_FUEL_MASS_RATIO | BOILER A AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_EXCESS_AIR+BOILER_A_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_EXCESS_AIR | BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_EXCESS_AIR | 14.5295
BOILER_A_AIR_MOISTURE | BOILER A AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_A_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_A_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645 |  |  | 0.000645
BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER A AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION | 13.7122
BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER A AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 14.4058
BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION | 0.43011
BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER A AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER A AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION | 0.04938
BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER A AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION | 0.020674
BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER A AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION | 0.058544
BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER A AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION | 0.000626
BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER A AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION | 0.13431
BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER A AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_A_CO2_FORMED/44.01+BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.85*BOILER_A_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_A_FLUE_GAS_MW)/BOILER_A_FLUE_GAS_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_MW; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_MW; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED | 0.21039
BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER A AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_A_FG_MW)/2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_A_FG_MW | BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_A_FG_MW | 0.4367
BOILER_A_BFW_ENERGY | BOILER A BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*BOILER_A_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_BFW_ENTHALPY; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS | BOILER_A_BFW_ENTHALPY; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS | 0
BOILER_A_BFW_ENTHALPY | BOILER A BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_A_INLET_TEMPERATURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_A_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_A_INLET_TEMPERATURE | 0
BOILER_A_BLOWDOWN_LOSS | BOILER A BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,((BOILER_A_CBD_BD/1000)*((STEAM_DRUM_A_PRESSURE*2.11087739028321+SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_A_CBD_BD; BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_A_CBD_BD; BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE | 0
BOILER_A_BOILER_INDIRECT_EFFICIENCY | BOILER A BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_A_BOILER_LOAD | BOILER A BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.7975 |  |  | 1.7975
BOILER_A_CALCULATED_AIRFLOW_NM3H | BOILER A CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_A_STATUS==0,0,BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS | BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS | 0
BOILER_A_CH4_CO2_COMBUSTION | BOILER A CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION | 2.1793
BOILER_A_CH4_H2O_COMBUSTION | BOILER A CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION | 1.7838
BOILER_A_CH4_N2_COMBUSTION | BOILER A CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION | 10.5432
BOILER_A_CO2_EMISSIONS | BOILER A CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_CO2_FORMED*BOILER_A_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS | BOILER_A_CO2_FORMED; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS | 0
BOILER_A_CO2_FORMED | BOILER A CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_CH4_CO2_COMBUSTION+BOILER_A_ETHANE_CO2_COMBUSTION+BOILER_A_ETHYLENE_CO2_COMBUSTION+BOILER_A_PROPANE_CO2_COMBUSTION+BOILER_A_NC4_CO2_COMBUSTION+BOILER_A_IC4_CO2_COMBUSTION+BOILER_A_NC5_CO2_COMBUSTION+BOILER_A_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CH4_CO2_COMBUSTION; BOILER_A_ETHANE_CO2_COMBUSTION; BOILER_A_ETHYLENE_CO2_COMBUSTION; BOILER_A_IC4_CO2_COMBUSTION; BOILER_A_IC5_CO2_COMBUSTION; BOILER_A_NC4_CO2_COMBUSTION (+2 more) | BOILER_A_CH4_CO2_COMBUSTION; BOILER_A_ETHANE_CO2_COMBUSTION; BOILER_A_ETHYLENE_CO2_COMBUSTION; BOILER_A_IC4_CO2_COMBUSTION; BOILER_A_IC5_CO2_COMBUSTION; BOILER_A_NC4_CO2_COMBUSTION; BOILER_A_NC5_CO2_COMBUSTION; BOILER_A_PROPANE_CO2_COMBUSTION | 2.3084
BOILER_A_CONVECTION_DUTY | BOILER A CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY+BOILER_A_SH_DUTY+BOILER_A_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_ECONOMIZER_DUTY; BOILER_A_SH_DUTY; BOILER_A_STACK_LOSS_CORRECTED; BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY; BOILER_A_SH_DUTY; BOILER_A_STACK_LOSS_CORRECTED; BOILER_A_STATUS | 0
BOILER_A_CONVECTION_SECTION_EFFICIENCY | BOILER A CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CONVECTION_DUTY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS
BOILER_A_CORRECTED_BFW_FLOW | BOILER A CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_A_STATUS==0,0,(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-DESUPERHEATER_OUTLET_STEAM_FLOW-BOILER_A_CBD_BD))/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_A; BFW_FLOW_TO_ECOMONIZER_A; BOILER_A_CBD_BD; BOILER_A_STATUS | BFW_FLOW_TO_DESUPERHEATER_A; BFW_FLOW_TO_ECOMONIZER_A; BOILER_A_CBD_BD; BOILER_A_STATUS | 0
BOILER_A_CORRECTED_COMBUSTION_AIR | BOILER A CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_A_AIR_MOISTURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 14.4151
BOILER_A_CORRECTED_COMBUTION_H2O_FORMED | BOILER A CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2O_FORMED+(BOILER_A_CORRECTED_COMBUSTION_AIR-BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_H2O_FORMED | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_A_CORRECTED_COMBUSTION_AIR; BOILER_A_H2O_FORMED | 1.8679
BOILER_A_CORRECTED_FUEL_FLOW | BOILER A CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW-((BOILER_A_FUEL_GAS_ENERGY_INPUT-(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY+BOILER_A_BLOWDOWN_LOSS+BOILER_A_STACK_LOSS+BOILER_A_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_A_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_BFW_ENERGY; BOILER_A_BLOWDOWN_LOSS; BOILER_A_FUEL_GAS_ENERGY_INPUT; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STACK_LOSS (+2 more) | BOILER_A_BFW_ENERGY; BOILER_A_BLOWDOWN_LOSS; BOILER_A_FUEL_GAS_ENERGY_INPUT; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STACK_LOSS; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY | 0
BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER A CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | 0
BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER A CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_COMBUSTION_AIR_TEMPERATURE | BOILER_A_COMBUSTION_AIR_TEMPERATURE | 6.9663
BOILER_A_CP_CH4_FUEL_TEMP | BOILER A CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 8.3614
BOILER_A_CP_ETHANE_FUEL_TEMP | BOILER A CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 12.0739
BOILER_A_CP_ETHYLENE_FUEL_TEMP | BOILER A CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 9.6651
BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER A CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6499 |  |  | 8.6499
BOILER_A_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER A CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3662 |  |  | 8.3662
BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER A CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586 |  |  | 6.9586
BOILER_A_CP_H2_FUEL_TEMP | BOILER A CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 6.8453
BOILER_A_CP_IC4_FUEL_TEMP | BOILER A CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 27.1103
BOILER_A_CP_IC5_FUEL_TEMP | BOILER A CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 25.8823
BOILER_A_CP_NC4_FUEL_TEMP | BOILER A CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 22.928
BOILER_A_CP_NC5_FUEL_TEMP | BOILER A CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 26.1654
BOILER_A_CP_OF_AIR_AT_STACK_TEMP | BOILER A CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_A_STACK_TEMPERATURE+273.15)/ | COMPUTED | 6.9676 |  |  | 6.9676
BOILER_A_CP_OF_H2O_AT_STACK_TEMP | BOILER A CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644 |  |  | 0.4644
BOILER_A_CP_PROPANE_FUEL_TEMP | BOILER A CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 17.047
BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER A CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_A_CP_H2_FUEL_TEMP+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_A_CP_CH4_FUEL_TEMP+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_A_CP_ETHYLENE_FUEL_TEMP+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CP_CH4_FUEL_TEMP; BOILER_A_CP_ETHANE_FUEL_TEMP; BOILER_A_CP_ETHYLENE_FUEL_TEMP; BOILER_A_CP_H2_FUEL_TEMP; BOILER_A_CP_IC4_FUEL_TEMP; BOILER_A_CP_IC5_FUEL_TEMP (+13 more) | BOILER_A_CP_CH4_FUEL_TEMP; BOILER_A_CP_ETHANE_FUEL_TEMP; BOILER_A_CP_ETHYLENE_FUEL_TEMP; BOILER_A_CP_H2_FUEL_TEMP; BOILER_A_CP_IC4_FUEL_TEMP; BOILER_A_CP_IC5_FUEL_TEMP; BOILER_A_CP_NC4_FUEL_TEMP; BOILER_A_CP_NC5_FUEL_TEMP; BOILER_A_CP_PROPANE_FUEL_TEMP; BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION; BOILER_A_FG_MW; BOILER_A_FG_NC4_MASS_FRACTION; BOILER_A_FG_NC5_MASS_FRACTION; BOILER_A_FG_PROPANE_MASS_FRACTION | 7.7287
BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER A CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_A_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION (+4 more) | BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION; BOILER_A_FG_MW; BOILER_A_FG_NC4_MASS_FRACTION; BOILER_A_FG_NC5_MASS_FRACTION; BOILER_A_FG_PROPANE_MASS_FRACTION | 7.7229
BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_A_EXCESS_AIR*(1-BOILER_A_AIR_MOISTURE)+BOILER_A_N2_FORMED+BOILER_A_CO2_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_N2_FORMED | 13.4993
BOILER_A_ECONOMIZER_DUTY | BOILER A ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*((STEAM_DRUM_A_PRESSURE*0.0336523715096497+ECONIMIZER_A_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_A_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE; STEAM_DRUM_A_PRESSURE | BFW_PRESSURE_TO_BOILER; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE; STEAM_DRUM_A_PRESSURE | 0
BOILER_A_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER A EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_BLOWDOWN_LOSS/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_BLOWDOWN_LOSS; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS | BOILER_A_BLOWDOWN_LOSS; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS
BOILER_A_ENERGY_GAINED | BOILER A ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_BFW_ENERGY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY | 0
BOILER_A_ETHANE_CO2_COMBUSTION | BOILER A ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION | 0.078103
BOILER_A_ETHANE_H2O_COMBUSTION | BOILER A ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION | 0.047977
BOILER_A_ETHANE_N2_COMBUSTION | BOILER A ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION | 0.33072
BOILER_A_ETHYLENE_CO2_COMBUSTION | BOILER A ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_A_ETHYLENE_H2O_COMBUSTION | BOILER A ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_A_ETHYLENE_N2_COMBUSTION | BOILER A ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_A_EXCESS_AIR | BOILER A EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_A_FLUE_GAS_OXGYGEN)*((BOILER_A_N2_FORMED/28.01)+(BOILER_A_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_A_CO2_FORMED/44.01))/(20.95-BOILER_A_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_CORRECTED_COMBUTION_H2O_FORMED; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED; BOILER_A_CORRECTED_COMBUTION_H2O_FORMED; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_N2_FORMED | 0.11442
BOILER_A_FG_CH4_MASS_FRACTION | BOILER A FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_CH4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_CH4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_A_FG_CH4_MASS_PERCENTAGE | BOILER A FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | 79.4217
BOILER_A_FG_DENSITY | BOILER A FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_A_FG_MW/22.414 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW | BOILER_A_FG_MW | 0.7893
BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER A FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | BOILER_A_FG_ETHANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_A_FG_ETHANE_MASS_PERCENTAGE | BOILER A FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | 2.6684
BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER A FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE | BOILER A FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | 0
BOILER_A_FG_FLOW_RATE | BOILER A FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_A_FUEL_GAS_FLOW/1000 | COMPUTED | 0.17548 |  |  | 0.17548
BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER A FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE | BOILER A FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | 0
BOILER_A_FG_IC4_MASS_FRACTION | BOILER A FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_IC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_A_FG_IC4_MASS_PERCENTAGE | BOILER A FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | 0.31885
BOILER_A_FG_IC5_MASS_FRACTION | BOILER A FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_IC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_A_FG_IC5_MASS_PERCENTAGE | BOILER A FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | 0.13466
BOILER_A_FG_MW | BOILER A FG MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | G/MOL | (NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW+NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_A_FG_PROPANE_CONCEN | NOT COMPUTED |  | Missing inputs (not in hierarchy): NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_A_FG_N2_CONCENTRATION; NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | 17.6914
BOILER_A_FG_NC4_MASS_FRACTION | BOILER A FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC4_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_A_FG_NC4_MASS_PERCENTAGE | BOILER A FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | 0.37802
BOILER_A_FG_NC5_MASS_FRACTION | BOILER A FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC5_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_A_FG_NC5_MASS_PERCENTAGE | BOILER A FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | 0.004081
BOILER_A_FG_NITROGEN_MASS_FRACTION | BOILER A FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NITROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | BOILER A FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | 16.219
BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER A FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_PROPANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_PROPANE_MASS_PERCENTAGE; TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_A_FG_PROPANE_MASS_PERCENTAGE | BOILER A FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | WT% | NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | BOILER_A_FG_MW; NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | 0.85531
BOILER_A_FLUE_GAS_MW | BOILER A FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_A_CO2_FORMED/44.01+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.96) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_CO2_FORMED; BOILER_A_EXCESS_AIR; BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_N2_FORMED; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | 27.6617
BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | 15.3673
BOILER_A_FOULING_INDEX | BOILER A FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_A_STATUS==0,0,1/BOILER_A_UA_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_UA_ECONOMIZER | BOILER_A_STATUS; BOILER_A_UA_ECONOMIZER
BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER A FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | (BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION | 99.942
BOILER_A_FUEL_CONSUMPTION | BOILER A FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | 0
BOILER_A_FUEL_GAIN_LOSS | BOILER A FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_A_FUEL_GAS_CORRECTED_TPH | BOILER A FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW; BOILER_A_STATUS | 0
BOILER_A_FUEL_GAS_ENERGY_INPUT | BOILER A FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_FG_FLOW_RATE*1000*BOILER_A_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | 0
BOILER_A_H2O_FORMED | BOILER A H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2_H2O_COMBUSTION+BOILER_A_CH4_H2O_COMBUSTION+BOILER_A_ETHANE_H2O_COMBUSTION+BOILER_A_ETHYLENE_H2O_COMBUSTION+BOILER_A_PROPANE_H2O_COMBUSTION+BOILER_A_IC4_H2O_COMBUSTION+BOILER_A_NC4_H2O_COMBUSTION+BOILER_A_IC5_H2O_COMBUSTION+BOILER_A_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CH4_H2O_COMBUSTION; BOILER_A_ETHANE_H2O_COMBUSTION; BOILER_A_ETHYLENE_H2O_COMBUSTION; BOILER_A_H2_H2O_COMBUSTION; BOILER_A_IC4_H2O_COMBUSTION; BOILER_A_IC5_H2O_COMBUSTION (+3 more) | BOILER_A_CH4_H2O_COMBUSTION; BOILER_A_ETHANE_H2O_COMBUSTION; BOILER_A_ETHYLENE_H2O_COMBUSTION; BOILER_A_H2_H2O_COMBUSTION; BOILER_A_IC4_H2O_COMBUSTION; BOILER_A_IC5_H2O_COMBUSTION; BOILER_A_NC4_H2O_COMBUSTION; BOILER_A_NC5_H2O_COMBUSTION; BOILER_A_PROPANE_H2O_COMBUSTION | 1.8586
BOILER_A_H2_CO2_COMBUSTION | BOILER A H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_A_H2_H2O_COMBUSTION | BOILER A H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_A_H2_N2_COMBUSTION | BOILER A H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER A HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_A_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS | BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS | 0
BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER A HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,9*(BOILER_A_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_A_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_A_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_STATUS | BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_STATUS | 0
BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER A HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_A_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | 0
BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER A HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,0*10^-6*28*5654*BOILER_A_BOILER_LOAD) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS | BOILER_A_STATUS | 0
BOILER_A_HP_STEAM_ENTHALPY | BOILER A HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS)+2.66244961166282*DESUPERHEATER_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS | 0
BOILER_A_IC4_CO2_COMBUSTION | BOILER A IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION | 0.009658
BOILER_A_IC4_H2O_COMBUSTION | BOILER A IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION | 0.005859
BOILER_A_IC4_N2_COMBUSTION | BOILER A IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION | 0.037969
BOILER_A_IC5_CO2_COMBUSTION | BOILER A IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION | 0.004107
BOILER_A_IC5_H2O_COMBUSTION | BOILER A IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION | 0.002017
BOILER_A_IC5_N2_COMBUSTION | BOILER A IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION | 0.015897
BOILER_A_LHV_DESIGN | BOILER A LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (LHV_FG/BOILER_A_FG_DENSITY)/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_DENSITY | BOILER_A_FG_DENSITY | 39.6755
BOILER_A_LMTD_ECONOMIZER | BOILER A LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_A_STATUS==0,0,((673-ECONIMIZER_A_OUTLET_TEMPERATURE)-(BOILER_A_STACK_TEMPERATURE-ECONOMIZER_A_INLET_TEMPERATURE))/ln((673-ECONIMIZER_A_OUTLET_TEMPERATURE)/(-ECONOMIZER_A_INLET_TEMPERATURE+BOILER_A_STACK_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE | BOILER_A_STATUS; ECONIMIZER_A_OUTLET_TEMPERATURE; ECONOMIZER_A_INLET_TEMPERATURE
BOILER_A_MIXED_LHV_PER_KG | BOILER A MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV | 9984.6019
BOILER_A_N2_FORMED | BOILER A N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_A_H2_N2_COMBUSTION+BOILER_A_CH4_N2_COMBUSTION+BOILER_A_ETHANE_N2_COMBUSTION+BOILER_A_ETHYLENE_N2_COMBUSTION+BOILER_A_PROPANE_N2_COMBUSTION+BOILER_A_IC4_N2_COMBUSTION+BOILER_A_NC4_N2_COMBUSTION+BOILER_A_IC5_N2_COMBUSTION+BOILER_A_NC5_N2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CH4_N2_COMBUSTION; BOILER_A_ETHANE_N2_COMBUSTION; BOILER_A_ETHYLENE_N2_COMBUSTION; BOILER_A_H2_N2_COMBUSTION; BOILER_A_IC4_N2_COMBUSTION; BOILER_A_IC5_N2_COMBUSTION (+3 more) | BOILER_A_CH4_N2_COMBUSTION; BOILER_A_ETHANE_N2_COMBUSTION; BOILER_A_ETHYLENE_N2_COMBUSTION; BOILER_A_H2_N2_COMBUSTION; BOILER_A_IC4_N2_COMBUSTION; BOILER_A_IC5_N2_COMBUSTION; BOILER_A_NC4_N2_COMBUSTION; BOILER_A_NC5_N2_COMBUSTION; BOILER_A_PROPANE_N2_COMBUSTION | 11.0766
BOILER_A_NC4_CO2_COMBUSTION | BOILER A NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION | 0.01145
BOILER_A_NC4_H2O_COMBUSTION | BOILER A NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION | 0.004942
BOILER_A_NC4_N2_COMBUSTION | BOILER A NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION | 0.045014
BOILER_A_NC5_CO2_COMBUSTION | BOILER A NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION | 0.000124
BOILER_A_NC5_H2O_COMBUSTION | BOILER A NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION | 6.1e-05
BOILER_A_NC5_N2_COMBUSTION | BOILER A NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION | 0.000482
BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER A PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS
BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER A PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_ENERGY_GAINED; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS | BOILER_A_ENERGY_GAINED; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS
BOILER_A_PROPANE_CO2_COMBUSTION | BOILER A PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION | 0.025608
BOILER_A_PROPANE_H2O_COMBUSTION | BOILER A PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION | 0.013976
BOILER_A_PROPANE_N2_COMBUSTION | BOILER A PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION | 0.10327
BOILER_A_RADIATION_DUTY | BOILER A RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_ENERGY_GAINED-BOILER_A_CONVECTION_DUTY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY; BOILER_A_ENERGY_GAINED; BOILER_A_STATUS | 0
BOILER_A_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER A RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_A_STATUS==0,0,BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_A_STATUS | BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_A_STATUS
BOILER_A_RADIATION_LOSSES | BOILER A RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_MIXED_LHV_PER_KG*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOAD^2-0.0899*BOILER_A_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | 0
BOILER_A_RADIATION_SECTION_EFFICIENCY | BOILER A RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_RADIATION_DUTY; BOILER_A_STATUS
BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER A SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_A_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_A_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_COMBUSTION_AIR_TEMPERATURE | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_A_COMBUSTION_AIR_TEMPERATURE | -50.8545
BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER A SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | 0
BOILER_A_SH_DUTY | BOILER A SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*((STEAM_DRUM_A_PRESSURE*-2.64315212289699+DESUPERHEATER_TEMPERATURE*3.58096116723573+1939.73413132244)-(STEAM_DRUM_A_PRESSURE*-4.27591051303366+SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; DESUPERHEATER_TEMPERATURE; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE | BOILER_A_STATUS; DESUPERHEATER_TEMPERATURE; STEAM_DRUM_A_PRESSURE; SUPERHEATER_INLET_TEMPERATURE | 0
BOILER_A_SH_PERFORMANCE | BOILER A SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,(BOILER_A_SH_SPECIFIC_DUTY)/0.128049016*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_SH_SPECIFIC_DUTY; BOILER_A_STATUS | BOILER_A_SH_SPECIFIC_DUTY; BOILER_A_STATUS | 0
BOILER_A_SH_SPECIFIC_DUTY | BOILER A SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_A_STATUS==0,0,BOILER_A_SH_DUTY/DESUPERHEATER_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_SH_DUTY; BOILER_A_STATUS | BOILER_A_SH_DUTY; BOILER_A_STATUS | 0
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER A SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS | 0
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER A SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION; BOILER_A_STATUS | 0
BOILER_A_STACK_LOSS | BOILER A STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_A_STACK_LOSS_CORRECTED | BOILER A STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_A_STATUS | BOILER A STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_A_BOILER_LOAD>25&&DESUPERHEATER_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS>40,1,0) | NOT COMPUTED |  | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS | HP_STEAM_PRESSURE_FROM_DS | 0
BOILER_A_STEAM_DRUM_TEMP | BOILER A STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_A_STATUS==0,0,4.02521999671835*log(STEAM_DRUM_A_PRESSURE*98.065)^3-4.64392873298701*log(STEAM_DRUM_A_PRESSURE*98.065)^2+11.2370106828649*log(STEAM_DRUM_A_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE | BOILER_A_STATUS; STEAM_DRUM_A_PRESSURE | 0
BOILER_A_STEAM_TO_FIRE_DUTY_RATIO | BOILER A STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW/(BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS | 0
BOILER_A_SUPERHEATED_STEAM_BFW_RATIO | BOILER A SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_A_STATUS==0,0,(DESUPERHEATER_OUTLET_STEAM_FLOW+BOILER_A_CBD_BD)/(BOILER_A_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CBD_BD; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS | BOILER_A_CBD_BD; BOILER_A_CORRECTED_BFW_FLOW; BOILER_A_STATUS
BOILER_A_THERMAL_EFFICIENCY | BOILER A THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_A_STATUS==0,0,(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY)/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_BFW_ENERGY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY; BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER A TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_A_STATUS | BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_A_STATUS | 0
BOILER_A_TOTAL_FLUE_GAS_CORRECTED | BOILER A TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_CORRECTED_TPH*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_FUEL_GAS_CORRECTED_TPH; BOILER_A_STATUS | 0
BOILER_A_TOTAL_FLUE_GAS_GENERATED | BOILER A TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW/1000*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_A_STATUS | 0
BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER A TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_TOTAL_MOISTURE_WITH_AIR+BOILER_A_H2O_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_H2O_FORMED; BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER_A_H2O_FORMED; BOILER_A_TOTAL_MOISTURE_WITH_AIR | 1.868
BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER A TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_A_STATUS; BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 0
BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER A TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_A_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_A_STATUS | 0
BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER A TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_A_RADIATION_LOSSES) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_RADIATION_LOSSES; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_RADIATION_LOSSES; BOILER_A_STATUS; BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER A TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_AIR_MOISTURE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO | 0.009372
BOILER_A_TOTAL_STEAM_ENERGY | BOILER A TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_HP_STEAM_ENTHALPY; BOILER_A_STATUS | BOILER_A_HP_STEAM_ENTHALPY; BOILER_A_STATUS | 0
BOILER_A_UA_ECONOMIZER | BOILER A UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY/BOILER_A_LMTD_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_ECONOMIZER_DUTY; BOILER_A_LMTD_ECONOMIZER; BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY; BOILER_A_LMTD_ECONOMIZER; BOILER_A_STATUS
BOILER_A_VAPOUR_PRESSURE_OF_H2O | BOILER A VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631 |  |  | 4.631
BOILER_B_ACTUAL_SP_ENERGY_DELTA | BOILER B ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER B AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_B_AIR_CP_REF_T+BOILER_B_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | 0.24044
BOILER_B_AIR_CP_REF_T | BOILER B AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | COMPUTED | 6.96 |  |  | 6.96
BOILER_B_AIR_FUEL_MASS_RATIO | BOILER B AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_EXCESS_AIR+BOILER_B_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_EXCESS_AIR | BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_EXCESS_AIR | 14.528
BOILER_B_AIR_MOISTURE | BOILER B AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_B_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_B_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645 |  |  | 0.000645
BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER B AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION | 13.7122
BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER B AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 14.4058
BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION | 0.43011
BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER B AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER B AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION | 0.04938
BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER B AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION | 0.020674
BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER B AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION | 0.058544
BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER B AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION | 0.000626
BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER B AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION | 0.13431
BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER B AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_B_CO2_FORMED/44.01+BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.85*BOILER_B_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_B_FLUE_GAS_MW)/BOILER_B_FLUE_GAS_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_MW; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_MW; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED | 0.21038
BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER B AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_B_FG_MW)/2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_B_FG_MW | BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_B_FG_MW | 0.43669
BOILER_B_BFW_ENERGY | BOILER B BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*BOILER_B_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_BFW_ENTHALPY; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS | BOILER_B_BFW_ENTHALPY; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS | 0
BOILER_B_BFW_ENTHALPY | BOILER B BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_B_INLET_TEMPERATURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_B_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_B_INLET_TEMPERATURE | 0
BOILER_B_BLOWDOWN_LOSS | BOILER B BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,((CBD_BLOW_DOWN_B/1000)*((BOILER_B_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_B | BFW_PRESSURE_TO_BOILER; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_B | 0
BOILER_B_BOILER_INDIRECT_EFFICIENCY | BOILER B BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_B_BOILER_LOAD | BOILER B BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_B_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.8401 |  |  | 1.8401
BOILER_B_CALCULATED_AIRFLOW_NM3H | BOILER B CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_B_STATUS==0,0,BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS | BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS | 0
BOILER_B_CH4_CO2_COMBUSTION | BOILER B CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION | 2.1793
BOILER_B_CH4_H2O_COMBUSTION | BOILER B CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION | 1.7838
BOILER_B_CH4_N2_COMBUSTION | BOILER B CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION | 10.5432
BOILER_B_CO2_EMISSIONS | BOILER B CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_CO2_FORMED*BOILER_B_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS | BOILER_B_CO2_FORMED; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS | 0
BOILER_B_CO2_FORMED | BOILER B CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_CH4_CO2_COMBUSTION+BOILER_B_ETHANE_CO2_COMBUSTION+BOILER_B_ETHYLENE_CO2_COMBUSTION+BOILER_B_PROPANE_CO2_COMBUSTION+BOILER_B_NC4_CO2_COMBUSTION+BOILER_B_IC4_CO2_COMBUSTION+BOILER_B_NC5_CO2_COMBUSTION+BOILER_B_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CH4_CO2_COMBUSTION; BOILER_B_ETHANE_CO2_COMBUSTION; BOILER_B_ETHYLENE_CO2_COMBUSTION; BOILER_B_IC4_CO2_COMBUSTION; BOILER_B_IC5_CO2_COMBUSTION; BOILER_B_NC4_CO2_COMBUSTION (+2 more) | BOILER_B_CH4_CO2_COMBUSTION; BOILER_B_ETHANE_CO2_COMBUSTION; BOILER_B_ETHYLENE_CO2_COMBUSTION; BOILER_B_IC4_CO2_COMBUSTION; BOILER_B_IC5_CO2_COMBUSTION; BOILER_B_NC4_CO2_COMBUSTION; BOILER_B_NC5_CO2_COMBUSTION; BOILER_B_PROPANE_CO2_COMBUSTION | 2.3084
BOILER_B_CONVECTION_DUTY | BOILER B CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY+BOILER_B_SH_DUTY+BOILER_B_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_ECONOMIZER_DUTY; BOILER_B_SH_DUTY; BOILER_B_STACK_LOSS_CORRECTED; BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY; BOILER_B_SH_DUTY; BOILER_B_STACK_LOSS_CORRECTED; BOILER_B_STATUS | 0
BOILER_B_CONVECTION_SECTION_EFFICIENCY | BOILER B CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CONVECTION_DUTY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS
BOILER_B_CORRECTED_BFW_FLOW | BOILER B CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_B_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-DESUPERHEATER_B_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_B))/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_B; BFW_FLOW_TO_ECONOMIZER_B; BOILER_B_STATUS; CBD_BLOW_DOWN_B | BFW_FLOW_TO_DESUPERHEATER_B; BFW_FLOW_TO_ECONOMIZER_B; BOILER_B_STATUS; CBD_BLOW_DOWN_B | 0
BOILER_B_CORRECTED_COMBUSTION_AIR | BOILER B CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_B_AIR_MOISTURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 14.4151
BOILER_B_CORRECTED_COMBUTION_H2O_FORMED | BOILER B CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2O_FORMED+(BOILER_B_CORRECTED_COMBUSTION_AIR-BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_H2O_FORMED | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_B_CORRECTED_COMBUSTION_AIR; BOILER_B_H2O_FORMED | 1.8679
BOILER_B_CORRECTED_FUEL_FLOW | BOILER B CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW-((BOILER_B_FUEL_GAS_ENERGY_INPUT-(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY+BOILER_B_BLOWDOWN_LOSS+BOILER_B_STACK_LOSS+BOILER_B_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_B_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_BFW_ENERGY; BOILER_B_BLOWDOWN_LOSS; BOILER_B_FUEL_GAS_ENERGY_INPUT; BOILER_B_FUEL_GAS_FLOW; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_MIXED_LHV_PER_KG (+3 more) | BOILER_B_BFW_ENERGY; BOILER_B_BLOWDOWN_LOSS; BOILER_B_FUEL_GAS_ENERGY_INPUT; BOILER_B_FUEL_GAS_FLOW; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STACK_LOSS; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY | 0
BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER B CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | 0
BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER B CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_COMBUSTION_AIR_TEMPERATURE | BOILER_B_COMBUSTION_AIR_TEMPERATURE | 6.9663
BOILER_B_CP_CH4_FUEL_TEMP | BOILER B CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 8.3613
BOILER_B_CP_ETHANE_FUEL_TEMP | BOILER B CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 12.0729
BOILER_B_CP_ETHYLENE_FUEL_TEMP | BOILER B CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 9.6644
BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER B CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6497 |  |  | 8.6497
BOILER_B_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER B CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3662 |  |  | 8.3662
BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER B CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586 |  |  | 6.9586
BOILER_B_CP_H2_FUEL_TEMP | BOILER B CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 6.8452
BOILER_B_CP_IC4_FUEL_TEMP | BOILER B CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 27.1072
BOILER_B_CP_IC5_FUEL_TEMP | BOILER B CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 25.8799
BOILER_B_CP_NC4_FUEL_TEMP | BOILER B CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 22.9262
BOILER_B_CP_NC5_FUEL_TEMP | BOILER B CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 26.1634
BOILER_B_CP_OF_AIR_AT_STACK_TEMP | BOILER B CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_B_STACK_TEMPERATURE+273.15)/ | COMPUTED | 6.9675 |  |  | 6.9675
BOILER_B_CP_OF_H2O_AT_STACK_TEMP | BOILER B CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644 |  |  | 0.4644
BOILER_B_CP_PROPANE_FUEL_TEMP | BOILER B CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 17.0456
BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER B CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_B_CP_H2_FUEL_TEMP+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_B_CP_CH4_FUEL_TEMP+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_B_CP_ETHYLENE_FUEL_TEMP+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CP_CH4_FUEL_TEMP; BOILER_B_CP_ETHANE_FUEL_TEMP; BOILER_B_CP_ETHYLENE_FUEL_TEMP; BOILER_B_CP_H2_FUEL_TEMP; BOILER_B_CP_IC4_FUEL_TEMP; BOILER_B_CP_IC5_FUEL_TEMP (+13 more) | BOILER_B_CP_CH4_FUEL_TEMP; BOILER_B_CP_ETHANE_FUEL_TEMP; BOILER_B_CP_ETHYLENE_FUEL_TEMP; BOILER_B_CP_H2_FUEL_TEMP; BOILER_B_CP_IC4_FUEL_TEMP; BOILER_B_CP_IC5_FUEL_TEMP; BOILER_B_CP_NC4_FUEL_TEMP; BOILER_B_CP_NC5_FUEL_TEMP; BOILER_B_CP_PROPANE_FUEL_TEMP; BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_ETHYLENE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_MW; BOILER_B_FG_NC4_MASS_FRACTION; BOILER_B_FG_NC5_MASS_FRACTION; BOILER_B_FG_PROPANE_MASS_FRACTION | 7.7286
BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER B CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_B_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_ETHYLENE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION (+4 more) | BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_ETHYLENE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_MW; BOILER_B_FG_NC4_MASS_FRACTION; BOILER_B_FG_NC5_MASS_FRACTION; BOILER_B_FG_PROPANE_MASS_FRACTION | 7.7229
BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_B_EXCESS_AIR*(1-BOILER_B_AIR_MOISTURE)+BOILER_B_N2_FORMED+BOILER_B_CO2_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_N2_FORMED | 13.4978
BOILER_B_ECONOMIZER_DUTY | BOILER B ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_B_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_B_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE | 0
BOILER_B_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER B EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_BLOWDOWN_LOSS/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_BLOWDOWN_LOSS; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS | BOILER_B_BLOWDOWN_LOSS; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS
BOILER_B_ENERGY_GAINED | BOILER B ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_BFW_ENERGY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY | 0
BOILER_B_ETHANE_CO2_COMBUSTION | BOILER B ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION | 0.078103
BOILER_B_ETHANE_H2O_COMBUSTION | BOILER B ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION | 0.047977
BOILER_B_ETHANE_N2_COMBUSTION | BOILER B ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION | 0.33072
BOILER_B_ETHYLENE_CO2_COMBUSTION | BOILER B ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_B_ETHYLENE_H2O_COMBUSTION | BOILER B ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_B_ETHYLENE_N2_COMBUSTION | BOILER B ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_B_EXCESS_AIR | BOILER B EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_B_FLUE_GAS_OXGYGEN)*((BOILER_B_N2_FORMED/28.01)+(BOILER_B_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_B_CO2_FORMED/44.01))/(20.95-BOILER_B_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_CORRECTED_COMBUTION_H2O_FORMED; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED; BOILER_B_CORRECTED_COMBUTION_H2O_FORMED; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_N2_FORMED | 0.11288
BOILER_B_FG_CH4_MASS_FRACTION | BOILER B FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_CH4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_B_FG_CH4_MASS_PERCENTAGE | BOILER B FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | 79.4217
BOILER_B_FG_DENSITY | BOILER B FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_B_FG_MW/22.414 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW | BOILER_B_FG_MW | 0.7893
BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER B FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_B_FG_ETHANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_B_FG_ETHANE_MASS_PERCENTAGE | BOILER B FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | 2.6684
BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER B FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE | BOILER B FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | 0
BOILER_B_FG_FLOW_RATE | BOILER B FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_B_FUEL_GAS_FLOW/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_FLOW | BOILER_B_FUEL_GAS_FLOW | 0.17548
BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER B FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE | BOILER B FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | 0
BOILER_B_FG_IC4_MASS_FRACTION | BOILER B FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_IC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_B_FG_IC4_MASS_PERCENTAGE | BOILER B FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | 0.31885
BOILER_B_FG_IC5_MASS_FRACTION | BOILER B FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_IC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_B_FG_IC5_MASS_PERCENTAGE | BOILER B FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | 0.13466
BOILER_B_FG_MW | BOILER B FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_B_FG_IC4_CONCENTRATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_B_FG_N2_CONCENTRATION; NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | 17.6914
BOILER_B_FG_NC4_MASS_FRACTION | BOILER B FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC4_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_B_FG_NC4_MASS_PERCENTAGE | BOILER B FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | 0.37802
BOILER_B_FG_NC5_MASS_FRACTION | BOILER B FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC5_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_B_FG_NC5_MASS_PERCENTAGE | BOILER B FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | 0.004081
BOILER_B_FG_NITROGEN_MASS_FRACTION | BOILER B FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NITROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_B_FG_NITROGEN_MASS_PERCENTAGE | BOILER B FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | 16.219
BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER B FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_PROPANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_PROPANE_MASS_PERCENTAGE; BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_B_FG_PROPANE_MASS_PERCENTAGE | BOILER B FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | BOILER_B_FG_MW; NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | 0.85531
BOILER_B_FLUE_GAS_MW | BOILER B FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_B_CO2_FORMED/44.01+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.96) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_CO2_FORMED; BOILER_B_EXCESS_AIR; BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_N2_FORMED; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | 27.6616
BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | 15.3658
BOILER_B_FOULING_INDEX | BOILER B FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_B_STATUS==0,0,1/BOILER_B_UA_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_UA_ECONOMIZER | BOILER_B_STATUS; BOILER_B_UA_ECONOMIZER
BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER B FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION | 99.942
BOILER_B_FUEL_CONSUMPTION | BOILER B FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | 0
BOILER_B_FUEL_GAIN_LOSS | BOILER B FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_B_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_B_FUEL_GAS_CORRECTED_TPH | BOILER B FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW; BOILER_B_STATUS | 0
BOILER_B_FUEL_GAS_ENERGY_INPUT | BOILER B FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_FG_FLOW_RATE*1000*BOILER_B_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | 0
BOILER_B_H2O_FORMED | BOILER B H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2_H2O_COMBUSTION+BOILER_B_CH4_H2O_COMBUSTION+BOILER_B_ETHANE_H2O_COMBUSTION+BOILER_B_ETHYLENE_H2O_COMBUSTION+BOILER_B_PROPANE_H2O_COMBUSTION+BOILER_B_IC4_H2O_COMBUSTION+BOILER_B_NC4_H2O_COMBUSTION+BOILER_B_IC5_H2O_COMBUSTION+BOILER_B_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CH4_H2O_COMBUSTION; BOILER_B_ETHANE_H2O_COMBUSTION; BOILER_B_ETHYLENE_H2O_COMBUSTION; BOILER_B_H2_H2O_COMBUSTION; BOILER_B_IC4_H2O_COMBUSTION; BOILER_B_IC5_H2O_COMBUSTION (+3 more) | BOILER_B_CH4_H2O_COMBUSTION; BOILER_B_ETHANE_H2O_COMBUSTION; BOILER_B_ETHYLENE_H2O_COMBUSTION; BOILER_B_H2_H2O_COMBUSTION; BOILER_B_IC4_H2O_COMBUSTION; BOILER_B_IC5_H2O_COMBUSTION; BOILER_B_NC4_H2O_COMBUSTION; BOILER_B_NC5_H2O_COMBUSTION; BOILER_B_PROPANE_H2O_COMBUSTION | 1.8586
BOILER_B_H2_CO2_COMBUSTION | BOILER B H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_B_H2_H2O_COMBUSTION | BOILER B H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_B_H2_N2_COMBUSTION | BOILER B H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER B HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_B_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_STATUS | BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_STATUS | 0
BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER B HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,9*(BOILER_B_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_B_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_B_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_STATUS | BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_STATUS | 0
BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER B HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_B_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_STATUS; BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | 0
BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER B HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,0*10^-6*28*5654*BOILER_B_BOILER_LOAD) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS | BOILER_B_STATUS | 0
BOILER_B_HP_STEAM_ENTHALPY | BOILER B HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_B)+2.66244961166282*DESUPERHEATER_B_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_B | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_B | 0
BOILER_B_IC4_CO2_COMBUSTION | BOILER B IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION | 0.009658
BOILER_B_IC4_H2O_COMBUSTION | BOILER B IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION | 0.005859
BOILER_B_IC4_N2_COMBUSTION | BOILER B IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION | 0.037969
BOILER_B_IC5_CO2_COMBUSTION | BOILER B IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION | 0.004107
BOILER_B_IC5_H2O_COMBUSTION | BOILER B IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION | 0.002017
BOILER_B_IC5_N2_COMBUSTION | BOILER B IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION | 0.015897
BOILER_B_LHV | BOILER B LHV | LBM_preprocessing_inferred_tags_main | Kcal/Kg | (BOILER_B_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_B_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_B_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_B_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_B_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_B_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_B_FG_N | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_NC4_MASS_FRACTION (+3 more) | BOILER_B_FG_CH4_MASS_FRACTION; BOILER_B_FG_ETHANE_MASS_FRACTION; BOILER_B_FG_HYDROGEN_MASS_FRACTION; BOILER_B_FG_IC4_MASS_FRACTION; BOILER_B_FG_IC5_MASS_FRACTION; BOILER_B_FG_NC4_MASS_FRACTION; BOILER_B_FG_NC5_MASS_FRACTION; BOILER_B_FG_NITROGEN_MASS_FRACTION; BOILER_B_FG_PROPANE_MASS_FRACTION | 9984.6019
BOILER_B_LHV_DESIGN | BOILER B LHV DESIGN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_B_FG_DENSITY)/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_DENSITY | BOILER_B_FG_DENSITY | 39.6755
BOILER_B_LMTD_ECONOMIZER | BOILER B LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_B_STATUS==0,0,((673-ECONOMIZER_B_OUTLET_TEMPERATURE)-(BOILER_B_STACK_TEMPERATURE-ECONOMIZER_B_INLET_TEMPERATURE))/ln((673-ECONOMIZER_B_OUTLET_TEMPERATURE)/(-ECONOMIZER_B_INLET_TEMPERATURE+BOILER_B_STACK_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE | BOILER_B_STATUS; ECONOMIZER_B_INLET_TEMPERATURE; ECONOMIZER_B_OUTLET_TEMPERATURE
BOILER_B_MIXED_LHV_PER_KG | BOILER B MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV | 9984.6019
BOILER_B_N2_FORMED | BOILER B N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_B_H2_N2_COMBUSTION+BOILER_B_CH4_N2_COMBUSTION+BOILER_B_ETHANE_N2_COMBUSTION+BOILER_B_ETHYLENE_N2_COMBUSTION+BOILER_B_PROPANE_N2_COMBUSTION+BOILER_B_IC4_N2_COMBUSTION+BOILER_B_NC4_N2_COMBUSTION+BOILER_B_IC5_N2_COMBUSTION+BOILER_B_NC5_N2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CH4_N2_COMBUSTION; BOILER_B_ETHANE_N2_COMBUSTION; BOILER_B_ETHYLENE_N2_COMBUSTION; BOILER_B_H2_N2_COMBUSTION; BOILER_B_IC4_N2_COMBUSTION; BOILER_B_IC5_N2_COMBUSTION (+3 more) | BOILER_B_CH4_N2_COMBUSTION; BOILER_B_ETHANE_N2_COMBUSTION; BOILER_B_ETHYLENE_N2_COMBUSTION; BOILER_B_H2_N2_COMBUSTION; BOILER_B_IC4_N2_COMBUSTION; BOILER_B_IC5_N2_COMBUSTION; BOILER_B_NC4_N2_COMBUSTION; BOILER_B_NC5_N2_COMBUSTION; BOILER_B_PROPANE_N2_COMBUSTION | 11.0766
BOILER_B_NC4_CO2_COMBUSTION | BOILER B NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION | 0.01145
BOILER_B_NC4_H2O_COMBUSTION | BOILER B NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION | 0.004942
BOILER_B_NC4_N2_COMBUSTION | BOILER B NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION | 0.045014
BOILER_B_NC5_CO2_COMBUSTION | BOILER B NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION | 0.000124
BOILER_B_NC5_H2O_COMBUSTION | BOILER B NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION | 6.1e-05
BOILER_B_NC5_N2_COMBUSTION | BOILER B NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION | 0.000482
BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER B PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS
BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER B PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_ENERGY_GAINED; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS | BOILER_B_ENERGY_GAINED; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS
BOILER_B_PROPANE_CO2_COMBUSTION | BOILER B PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION | 0.025608
BOILER_B_PROPANE_H2O_COMBUSTION | BOILER B PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION | 0.013976
BOILER_B_PROPANE_N2_COMBUSTION | BOILER B PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION | 0.10327
BOILER_B_RADIATION_DUTY | BOILER B RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_ENERGY_GAINED-BOILER_B_CONVECTION_DUTY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY; BOILER_B_ENERGY_GAINED; BOILER_B_STATUS | 0
BOILER_B_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER B RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_B_STATUS==0,0,BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_B_STATUS | BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_B_STATUS
BOILER_B_RADIATION_LOSSES | BOILER B RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_MIXED_LHV_PER_KG*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOAD^2-0.0899*BOILER_B_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | 0
BOILER_B_RADIATION_SECTION_EFFICIENCY | BOILER B RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_RADIATION_DUTY; BOILER_B_STATUS
BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER B SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_B_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_B_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_COMBUSTION_AIR_TEMPERATURE | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_B_COMBUSTION_AIR_TEMPERATURE | -50.7932
BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER B SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | 0
BOILER_B_SH_DUTY | BOILER B SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_B_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_B_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE | BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE; BOILER_B_SUPERHEATER_INLET_TEMPERATURE | 0
BOILER_B_SH_PERFORMANCE | BOILER B SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,(BOILER_B_SH_SPECIFIC_DUTY)/0.110075721*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_SH_SPECIFIC_DUTY; BOILER_B_STATUS | BOILER_B_SH_SPECIFIC_DUTY; BOILER_B_STATUS | 0
BOILER_B_SH_SPECIFIC_DUTY | BOILER B SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_B_STATUS==0,0,BOILER_B_SH_DUTY/DESUPERHEATER_B_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_SH_DUTY; BOILER_B_STATUS | BOILER_B_SH_DUTY; BOILER_B_STATUS | 0
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER B SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS | 0
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER B SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION; BOILER_B_STATUS | 0
BOILER_B_STACK_LOSS | BOILER B STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_B_STACK_LOSS_CORRECTED | BOILER B STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_B_STATUS | BOILER B STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_B_BOILER_LOAD>25&&DESUPERHEATER_B_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_B>40,1,0) | NOT COMPUTED |  | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS_B | HP_STEAM_PRESSURE_FROM_DS_B | 0
BOILER_B_STEAM_DRUM_TEMP | BOILER B STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_B_STATUS==0,0,4.02521999671835*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE | BOILER_B_STATUS; BOILER_B_STEAM_DRUM_PRESSURE | 0
BOILER_B_STEAM_TO_FIRE_DUTY_RATIO | BOILER B STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW/(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS | 0
BOILER_B_SUPERHEATED_STEAM_BFW_RATIO | BOILER B SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_B_STATUS==0,0,(DESUPERHEATER_B_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_B)/(BOILER_B_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; CBD_BLOW_DOWN_B | BOILER_B_CORRECTED_BFW_FLOW; BOILER_B_STATUS; CBD_BLOW_DOWN_B
BOILER_B_THERMAL_EFFICIENCY | BOILER B THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_B_STATUS==0,0,(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY)/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_BFW_ENERGY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER B TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_B_STATUS | BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_B_STATUS | 0
BOILER_B_TOTAL_FLUE_GAS_CORRECTED | BOILER B TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_CORRECTED_TPH*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_CORRECTED_TPH; BOILER_B_STATUS | 0
BOILER_B_TOTAL_FLUE_GAS_GENERATED | BOILER B TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW/1000*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_B_FUEL_GAS_FLOW; BOILER_B_STATUS | 0
BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER B TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_B_FG_CH4_MASS_PERCENTAGE+BOILER_B_FG_ETHANE_MASS_PERCENTAGE+BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_B_FG_PROPANE_MASS_PERCENTAGE+BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_B_FG_NITROGEN_MASS_PERCENTAGE+BOILER_B_FG_IC4_MASS_PERCENTAGE+BOILER_B_FG_NC4_MASS_PERCENTAGE+BOILER_B_FG_NC5_MASS_P | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_B_FG_CH4_MASS_PERCENTAGE; BOILER_B_FG_ETHANE_MASS_PERCENTAGE; BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_B_FG_IC4_MASS_PERCENTAGE; BOILER_B_FG_IC5_MASS_PERCENTAGE; BOILER_B_FG_NC4_MASS_PERCENTAGE; BOILER_B_FG_NC5_MASS_PERCENTAGE; BOILER_B_FG_NITROGEN_MASS_PERCENTAGE; BOILER_B_FG_PROPANE_MASS_PERCENTAGE | 100
BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER B TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_TOTAL_MOISTURE_WITH_AIR+BOILER_B_H2O_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_H2O_FORMED; BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER_B_H2O_FORMED; BOILER_B_TOTAL_MOISTURE_WITH_AIR | 1.868
BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER B TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_B_STATUS; BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 0
BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER B TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_B_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_MIXED_LHV_PER_KG; BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG; BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_B_STATUS | 0
BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER B TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_B_RADIATION_LOSSES) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_RADIATION_LOSSES; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_RADIATION_LOSSES; BOILER_B_STATUS; BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER B TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_AIR_MOISTURE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_AIR_FUEL_MASS_RATIO | BOILER_B_AIR_FUEL_MASS_RATIO | 0.009371
BOILER_B_TOTAL_STEAM_ENERGY | BOILER B TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_HP_STEAM_ENTHALPY; BOILER_B_STATUS | BOILER_B_HP_STEAM_ENTHALPY; BOILER_B_STATUS | 0
BOILER_B_UA_ECONOMIZER | BOILER B UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY/BOILER_B_LMTD_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_ECONOMIZER_DUTY; BOILER_B_LMTD_ECONOMIZER; BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY; BOILER_B_LMTD_ECONOMIZER; BOILER_B_STATUS
BOILER_B_VAPOUR_PRESSURE_OF_H2O | BOILER B VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631 |  |  | 4.631
BOILER_C_ACTUAL_SP_ENERGY_DELTA | BOILER C ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER C AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_C_AIR_CP_REF_T+BOILER_C_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | 0.24044
BOILER_C_AIR_CP_REF_T | BOILER C AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | COMPUTED | 6.96 |  |  | 6.96
BOILER_C_AIR_FUEL_MASS_RATIO | BOILER C AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_EXCESS_AIR+BOILER_C_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_EXCESS_AIR | BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_EXCESS_AIR | 14.5295
BOILER_C_AIR_MOISTURE | BOILER C AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_C_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_C_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645 |  |  | 0.000645
BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER C AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION | 13.7122
BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER C AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 14.4058
BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION | 0.43011
BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER C AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER C AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION | 0.04938
BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER C AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION | 0.020674
BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER C AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION | 0.058544
BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER C AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION | 0.000626
BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER C AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION | 0.13431
BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER C AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_C_CO2_FORMED/44.01+BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.85*BOILER_C_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_C_FLUE_GAS_MW)/BOILER_C_FLUE_GAS_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_MW; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_MW; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED | 0.21039
BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER C AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_C_FG_MW)/2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_C_FG_MW | BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_C_FG_MW | 0.43669
BOILER_C_BFW_ENERGY | BOILER C BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*BOILER_C_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_BFW_ENTHALPY; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS | BOILER_C_BFW_ENTHALPY; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS | 0
BOILER_C_BFW_ENTHALPY | BOILER C BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_C_INLET_TEMPERATURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_C_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_C_INLET_TEMPERATURE | 0
BOILER_C_BLOWDOWN_LOSS | BOILER C BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,((CBD_BLOW_DOWN_C/1000)*((BOILER_C_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_C | BFW_PRESSURE_TO_BOILER; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_C | 0
BOILER_C_BOILER_INDIRECT_EFFICIENCY | BOILER C BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_C_BOILER_LOAD | BOILER C BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_C_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.7993 |  |  | 1.7993
BOILER_C_CALCULATED_AIRFLOW_NM3H | BOILER C CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_C_STATUS==0,0,BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS | BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS | 0
BOILER_C_CH4_CO2_COMBUSTION | BOILER C CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION | 2.1793
BOILER_C_CH4_H2O_COMBUSTION | BOILER C CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION | 1.7838
BOILER_C_CH4_N2_COMBUSTION | BOILER C CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION | 10.5432
BOILER_C_CO2_EMISSIONS | BOILER C CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_CO2_FORMED*BOILER_C_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS | BOILER_C_CO2_FORMED; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS | 0
BOILER_C_CO2_FORMED | BOILER C CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_CH4_CO2_COMBUSTION+BOILER_C_ETHANE_CO2_COMBUSTION+BOILER_C_ETHYLENE_CO2_COMBUSTION+BOILER_C_PROPANE_CO2_COMBUSTION+BOILER_C_NC4_CO2_COMBUSTION+BOILER_C_IC4_CO2_COMBUSTION+BOILER_C_NC5_CO2_COMBUSTION+BOILER_C_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CH4_CO2_COMBUSTION; BOILER_C_ETHANE_CO2_COMBUSTION; BOILER_C_ETHYLENE_CO2_COMBUSTION; BOILER_C_IC4_CO2_COMBUSTION; BOILER_C_IC5_CO2_COMBUSTION; BOILER_C_NC4_CO2_COMBUSTION (+2 more) | BOILER_C_CH4_CO2_COMBUSTION; BOILER_C_ETHANE_CO2_COMBUSTION; BOILER_C_ETHYLENE_CO2_COMBUSTION; BOILER_C_IC4_CO2_COMBUSTION; BOILER_C_IC5_CO2_COMBUSTION; BOILER_C_NC4_CO2_COMBUSTION; BOILER_C_NC5_CO2_COMBUSTION; BOILER_C_PROPANE_CO2_COMBUSTION | 2.3084
BOILER_C_CONVECTION_DUTY | BOILER C CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY+BOILER_C_SH_DUTY+BOILER_C_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_ECONOMIZER_DUTY; BOILER_C_SH_DUTY; BOILER_C_STACK_LOSS_CORRECTED; BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY; BOILER_C_SH_DUTY; BOILER_C_STACK_LOSS_CORRECTED; BOILER_C_STATUS | 0
BOILER_C_CONVECTION_SECTION_EFFICIENCY | BOILER C CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CONVECTION_DUTY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS
BOILER_C_CORRECTED_BFW_FLOW | BOILER C CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_C_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-DESUPERHEATER_C_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_C))/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_C; BFW_FLOW_TO_ECONOMIZER_C; BOILER_C_STATUS; CBD_BLOW_DOWN_C | BFW_FLOW_TO_DESUPERHEATER_C; BFW_FLOW_TO_ECONOMIZER_C; BOILER_C_STATUS; CBD_BLOW_DOWN_C | 0
BOILER_C_CORRECTED_COMBUSTION_AIR | BOILER C CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_C_AIR_MOISTURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 14.4151
BOILER_C_CORRECTED_COMBUTION_H2O_FORMED | BOILER C CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2O_FORMED+(BOILER_C_CORRECTED_COMBUSTION_AIR-BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_H2O_FORMED | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_C_CORRECTED_COMBUSTION_AIR; BOILER_C_H2O_FORMED | 1.8679
BOILER_C_CORRECTED_FUEL_FLOW | BOILER C CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW-((BOILER_C_FUEL_GAS_ENERGY_INPUT-(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY+BOILER_C_BLOWDOWN_LOSS+BOILER_C_STACK_LOSS+BOILER_C_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_C_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_BFW_ENERGY; BOILER_C_BLOWDOWN_LOSS; BOILER_C_FUEL_GAS_ENERGY_INPUT; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STACK_LOSS (+2 more) | BOILER_C_BFW_ENERGY; BOILER_C_BLOWDOWN_LOSS; BOILER_C_FUEL_GAS_ENERGY_INPUT; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STACK_LOSS; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY | 0
BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER C CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | 0
BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER C CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_COMBUSTION_AIR_TEMPERATURE | BOILER_C_COMBUSTION_AIR_TEMPERATURE | 6.9663
BOILER_C_CP_CH4_FUEL_TEMP | BOILER C CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 8.3611
BOILER_C_CP_ETHANE_FUEL_TEMP | BOILER C CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 12.0719
BOILER_C_CP_ETHYLENE_FUEL_TEMP | BOILER C CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 9.6636
BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER C CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6502 |  |  | 8.6502
BOILER_C_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER C CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3662 |  |  | 8.3662
BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER C CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586 |  |  | 6.9586
BOILER_C_CP_H2_FUEL_TEMP | BOILER C CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 6.8451
BOILER_C_CP_IC4_FUEL_TEMP | BOILER C CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 27.104
BOILER_C_CP_IC5_FUEL_TEMP | BOILER C CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 25.8774
BOILER_C_CP_NC4_FUEL_TEMP | BOILER C CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 22.9243
BOILER_C_CP_NC5_FUEL_TEMP | BOILER C CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 26.1613
BOILER_C_CP_OF_AIR_AT_STACK_TEMP | BOILER C CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_C_STACK_TEMPERATURE+273.15)/ | COMPUTED | 6.9676 |  |  | 6.9676
BOILER_C_CP_OF_H2O_AT_STACK_TEMP | BOILER C CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644 |  |  | 0.4644
BOILER_C_CP_PROPANE_FUEL_TEMP | BOILER C CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 17.0441
BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER C CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_C_CP_H2_FUEL_TEMP+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_C_CP_CH4_FUEL_TEMP+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_C_CP_ETHYLENE_FUEL_TEMP+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CP_CH4_FUEL_TEMP; BOILER_C_CP_ETHANE_FUEL_TEMP; BOILER_C_CP_ETHYLENE_FUEL_TEMP; BOILER_C_CP_H2_FUEL_TEMP; BOILER_C_CP_IC4_FUEL_TEMP; BOILER_C_CP_IC5_FUEL_TEMP (+13 more) | BOILER_C_CP_CH4_FUEL_TEMP; BOILER_C_CP_ETHANE_FUEL_TEMP; BOILER_C_CP_ETHYLENE_FUEL_TEMP; BOILER_C_CP_H2_FUEL_TEMP; BOILER_C_CP_IC4_FUEL_TEMP; BOILER_C_CP_IC5_FUEL_TEMP; BOILER_C_CP_NC4_FUEL_TEMP; BOILER_C_CP_NC5_FUEL_TEMP; BOILER_C_CP_PROPANE_FUEL_TEMP; BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_ETHYLENE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_MW; BOILER_C_FG_NC4_MASS_FRACTION; BOILER_C_FG_NC5_MASS_FRACTION; BOILER_C_FG_PROPANE_MASS_FRACTION | 7.7284
BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER C CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_C_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_ETHYLENE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION (+4 more) | BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_ETHYLENE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_MW; BOILER_C_FG_NC4_MASS_FRACTION; BOILER_C_FG_NC5_MASS_FRACTION; BOILER_C_FG_PROPANE_MASS_FRACTION | 7.7229
BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_C_EXCESS_AIR*(1-BOILER_C_AIR_MOISTURE)+BOILER_C_N2_FORMED+BOILER_C_CO2_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_N2_FORMED | 13.4993
BOILER_C_ECONOMIZER_DUTY | BOILER C ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_C_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_C_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE | 0
BOILER_C_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER C EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_BLOWDOWN_LOSS/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_BLOWDOWN_LOSS; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS | BOILER_C_BLOWDOWN_LOSS; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS
BOILER_C_ENERGY_GAINED | BOILER C ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_BFW_ENERGY; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY | 0
BOILER_C_ETHANE_CO2_COMBUSTION | BOILER C ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION | 0.078103
BOILER_C_ETHANE_H2O_COMBUSTION | BOILER C ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION | 0.047977
BOILER_C_ETHANE_N2_COMBUSTION | BOILER C ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION | 0.33072
BOILER_C_ETHYLENE_CO2_COMBUSTION | BOILER C ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_C_ETHYLENE_H2O_COMBUSTION | BOILER C ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_C_ETHYLENE_N2_COMBUSTION | BOILER C ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_C_EXCESS_AIR | BOILER C EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_C_FLUE_GAS_OXGYGEN)*((BOILER_C_N2_FORMED/28.01)+(BOILER_C_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_C_CO2_FORMED/44.01))/(20.95-BOILER_C_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_CORRECTED_COMBUTION_H2O_FORMED; BOILER_C_FLUE_GAS_OXGYGEN; BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED; BOILER_C_CORRECTED_COMBUTION_H2O_FORMED; BOILER_C_FLUE_GAS_OXGYGEN; BOILER_C_N2_FORMED | 0.11442
BOILER_C_FG_CH4_MASS_FRACTION | BOILER C FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_CH4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_C_FG_CH4_MASS_PERCENTAGE | BOILER C FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | 79.4217
BOILER_C_FG_DENSITY | BOILER C FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_C_FG_MW/22.414 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW | BOILER_C_FG_MW | 0.7893
BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER C FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_C_FG_ETHANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_C_FG_ETHANE_MASS_PERCENTAGE | BOILER C FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | 2.6684
BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER C FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE | BOILER C FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | 0
BOILER_C_FG_FLOW_RATE | BOILER C FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_C_FUEL_GAS_FLOW/1000 | COMPUTED | 0.1755 |  |  | 0.1755
BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER C FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE | BOILER C FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | 0
BOILER_C_FG_IC4_MASS_FRACTION | BOILER C FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_IC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_C_FG_IC4_MASS_PERCENTAGE | BOILER C FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | 0.31885
BOILER_C_FG_IC5_MASS_FRACTION | BOILER C FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_IC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_C_FG_IC5_MASS_PERCENTAGE | BOILER C FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | 0.13466
BOILER_C_FG_MW | BOILER C FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_C_FG_IC4_CONCENTRATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_C_FG_N2_CONCENTRATION; NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | 17.6914
BOILER_C_FG_NC4_MASS_FRACTION | BOILER C FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC4_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_C_FG_NC4_MASS_PERCENTAGE | BOILER C FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | 0.37802
BOILER_C_FG_NC5_MASS_FRACTION | BOILER C FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC5_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_C_FG_NC5_MASS_PERCENTAGE | BOILER C FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | 0.004081
BOILER_C_FG_NITROGEN_MASS_FRACTION | BOILER C FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NITROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_C_FG_NITROGEN_MASS_PERCENTAGE | BOILER C FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | 16.219
BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER C FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_PROPANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_PROPANE_MASS_PERCENTAGE; BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_C_FG_PROPANE_MASS_PERCENTAGE | BOILER C FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | BOILER_C_FG_MW; NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | 0.85531
BOILER_C_FLUE_GAS_MW | BOILER C FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_C_CO2_FORMED/44.01+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.96) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_CO2_FORMED; BOILER_C_EXCESS_AIR; BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_N2_FORMED; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | 27.6617
BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | 15.3673
BOILER_C_FOULING_INDEX | BOILER C FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_C_STATUS==0,0,1/BOILER_C_UA_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_UA_ECONOMIZER | BOILER_C_STATUS; BOILER_C_UA_ECONOMIZER
BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER C FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION | 99.942
BOILER_C_FUEL_CONSUMPTION | BOILER C FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | 0
BOILER_C_FUEL_GAIN_LOSS | BOILER C FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_C_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_C_FUEL_GAS_CORRECTED_TPH | BOILER C FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW; BOILER_C_STATUS | 0
BOILER_C_FUEL_GAS_ENERGY_INPUT | BOILER C FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_FG_FLOW_RATE*1000*BOILER_C_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | 0
BOILER_C_H2O_FORMED | BOILER C H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2_H2O_COMBUSTION+BOILER_C_CH4_H2O_COMBUSTION+BOILER_C_ETHANE_H2O_COMBUSTION+BOILER_C_ETHYLENE_H2O_COMBUSTION+BOILER_C_PROPANE_H2O_COMBUSTION+BOILER_C_IC4_H2O_COMBUSTION+BOILER_C_NC4_H2O_COMBUSTION+BOILER_C_IC5_H2O_COMBUSTION+BOILER_C_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CH4_H2O_COMBUSTION; BOILER_C_ETHANE_H2O_COMBUSTION; BOILER_C_ETHYLENE_H2O_COMBUSTION; BOILER_C_H2_H2O_COMBUSTION; BOILER_C_IC4_H2O_COMBUSTION; BOILER_C_IC5_H2O_COMBUSTION (+3 more) | BOILER_C_CH4_H2O_COMBUSTION; BOILER_C_ETHANE_H2O_COMBUSTION; BOILER_C_ETHYLENE_H2O_COMBUSTION; BOILER_C_H2_H2O_COMBUSTION; BOILER_C_IC4_H2O_COMBUSTION; BOILER_C_IC5_H2O_COMBUSTION; BOILER_C_NC4_H2O_COMBUSTION; BOILER_C_NC5_H2O_COMBUSTION; BOILER_C_PROPANE_H2O_COMBUSTION | 1.8586
BOILER_C_H2_CO2_COMBUSTION | BOILER C H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_C_H2_H2O_COMBUSTION | BOILER C H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_C_H2_N2_COMBUSTION | BOILER C H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER C HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_C_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS | BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS | 0
BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER C HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,9*(BOILER_C_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_C_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_C_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_STATUS | BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_STATUS | 0
BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER C HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_C_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | 0
BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER C HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,0*10^-6*28*5654*BOILER_C_BOILER_LOAD) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS | BOILER_C_STATUS | 0
BOILER_C_HP_STEAM_ENTHALPY | BOILER C HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_C)+2.66244961166282*DESUPERHEATER_C_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_C | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_C | 0
BOILER_C_IC4_CO2_COMBUSTION | BOILER C IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION | 0.009658
BOILER_C_IC4_H2O_COMBUSTION | BOILER C IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION | 0.005859
BOILER_C_IC4_N2_COMBUSTION | BOILER C IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION | 0.037969
BOILER_C_IC5_CO2_COMBUSTION | BOILER C IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION | 0.004107
BOILER_C_IC5_H2O_COMBUSTION | BOILER C IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION | 0.002017
BOILER_C_IC5_N2_COMBUSTION | BOILER C IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION | 0.015897
BOILER_C_LHV | BOILER C LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_C_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_C_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_C_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_C_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_C_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_C_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_C_FG_N | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_NC4_MASS_FRACTION (+3 more) | BOILER_C_FG_CH4_MASS_FRACTION; BOILER_C_FG_ETHANE_MASS_FRACTION; BOILER_C_FG_HYDROGEN_MASS_FRACTION; BOILER_C_FG_IC4_MASS_FRACTION; BOILER_C_FG_IC5_MASS_FRACTION; BOILER_C_FG_NC4_MASS_FRACTION; BOILER_C_FG_NC5_MASS_FRACTION; BOILER_C_FG_NITROGEN_MASS_FRACTION; BOILER_C_FG_PROPANE_MASS_FRACTION | 9984.6019
BOILER_C_LHV_DESIGEN | BOILER C LHV DESIGEN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_C_FG_DENSITY)/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_DENSITY | BOILER_C_FG_DENSITY | 39.6755
BOILER_C_LMTD_ECONOMIZER | BOILER C LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_C_STATUS==0,0,((673-ECONOMIZER_C_OUTLET_TEMPERATURE)-(BOILER_C_STACK_TEMPERATURE-ECONOMIZER_C_INLET_TEMPERATURE))/ln((673-ECONOMIZER_C_OUTLET_TEMPERATURE)/(-ECONOMIZER_C_INLET_TEMPERATURE+BOILER_C_STACK_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE | BOILER_C_STATUS; ECONOMIZER_C_INLET_TEMPERATURE; ECONOMIZER_C_OUTLET_TEMPERATURE
BOILER_C_MIXED_LHV_PER_KG | BOILER C MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV | 9984.6019
BOILER_C_N2_FORMED | BOILER C N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_C_H2_N2_COMBUSTION+BOILER_C_CH4_N2_COMBUSTION+BOILER_C_ETHANE_N2_COMBUSTION+BOILER_C_ETHYLENE_N2_COMBUSTION+BOILER_C_PROPANE_N2_COMBUSTION+BOILER_C_IC4_N2_COMBUSTION+BOILER_C_NC4_N2_COMBUSTION+BOILER_C_IC5_N2_COMBUSTION+BOILER_C_NC5_N2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CH4_N2_COMBUSTION; BOILER_C_ETHANE_N2_COMBUSTION; BOILER_C_ETHYLENE_N2_COMBUSTION; BOILER_C_H2_N2_COMBUSTION; BOILER_C_IC4_N2_COMBUSTION; BOILER_C_IC5_N2_COMBUSTION (+3 more) | BOILER_C_CH4_N2_COMBUSTION; BOILER_C_ETHANE_N2_COMBUSTION; BOILER_C_ETHYLENE_N2_COMBUSTION; BOILER_C_H2_N2_COMBUSTION; BOILER_C_IC4_N2_COMBUSTION; BOILER_C_IC5_N2_COMBUSTION; BOILER_C_NC4_N2_COMBUSTION; BOILER_C_NC5_N2_COMBUSTION; BOILER_C_PROPANE_N2_COMBUSTION | 11.0766
BOILER_C_NC4_CO2_COMBUSTION | BOILER C NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION | 0.01145
BOILER_C_NC4_H2O_COMBUSTION | BOILER C NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION | 0.004942
BOILER_C_NC4_N2_COMBUSTION | BOILER C NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION | 0.045014
BOILER_C_NC5_CO2_COMBUSTION | BOILER C NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION | 0.000124
BOILER_C_NC5_H2O_COMBUSTION | BOILER C NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION | 6.1e-05
BOILER_C_NC5_N2_COMBUSTION | BOILER C NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION | 0.000482
BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER C PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS
BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER C PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_ENERGY_GAINED; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS | BOILER_C_ENERGY_GAINED; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS
BOILER_C_PROPANE_CO2_COMBUSTION | BOILER C PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION | 0.025608
BOILER_C_PROPANE_H2O_COMBUSTION | BOILER C PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION | 0.013976
BOILER_C_PROPANE_N2_COMBUSTION | BOILER C PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION | 0.10327
BOILER_C_RADIATION_DUTY | BOILER C RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_ENERGY_GAINED-BOILER_C_CONVECTION_DUTY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY; BOILER_C_ENERGY_GAINED; BOILER_C_STATUS | 0
BOILER_C_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER C RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_C_STATUS==0,0,BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_C_STATUS | BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_C_STATUS
BOILER_C_RADIATION_LOSSES | BOILER C RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_MIXED_LHV_PER_KG*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOAD^2-0.0899*BOILER_C_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | 0
BOILER_C_RADIATION_SECTION_EFFICIENCY | BOILER C RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_RADIATION_DUTY; BOILER_C_STATUS
BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER C SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_C_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_C_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_COMBUSTION_AIR_TEMPERATURE | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_C_COMBUSTION_AIR_TEMPERATURE | -50.7916
BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER C SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | 0
BOILER_C_SH_DUTY | BOILER C SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_C_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_C_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE | BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE; BOILER_C_SUPERHEATER_INLET_TEMPERATURE | 0
BOILER_C_SH_PERFORMANCE | BOILER C SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,(BOILER_C_SH_SPECIFIC_DUTY)/0.110075721*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_SH_SPECIFIC_DUTY; BOILER_C_STATUS | BOILER_C_SH_SPECIFIC_DUTY; BOILER_C_STATUS | 0
BOILER_C_SH_SPECIFIC_DUTY | BOILER C SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_C_STATUS==0,0,BOILER_C_SH_DUTY/DESUPERHEATER_C_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_SH_DUTY; BOILER_C_STATUS | BOILER_C_SH_DUTY; BOILER_C_STATUS | 0
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER C SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS | 0
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER C SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION; BOILER_C_STATUS | 0
BOILER_C_STACK_LOSS | BOILER C STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_C_STACK_LOSS_CORRECTED | BOILER C STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_C_STATUS | BOILER C STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_C_BOILER_LOAD>25&&DESUPERHEATER_C_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_C>40,1,0) | NOT COMPUTED |  | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS_C | HP_STEAM_PRESSURE_FROM_DS_C | 0
BOILER_C_STEAM_DRUM_TEMP | BOILER C STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_C_STATUS==0,0,4.02521999671835*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE | BOILER_C_STATUS; BOILER_C_STEAM_DRUM_PRESSURE | 0
BOILER_C_STEAM_TO_FIRE_DUTY_RATIO | BOILER C STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW/(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS | 0
BOILER_C_SUPERHEATED_STEAM_BFW_RATIO | BOILER C SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_C_STATUS==0,0,(DESUPERHEATER_C_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_C)/(BOILER_C_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; CBD_BLOW_DOWN_C | BOILER_C_CORRECTED_BFW_FLOW; BOILER_C_STATUS; CBD_BLOW_DOWN_C
BOILER_C_THERMAL_EFFICIENCY | BOILER C THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_C_STATUS==0,0,(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY)/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_BFW_ENERGY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER C TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_C_STATUS | BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_C_STATUS | 0
BOILER_C_TOTAL_FLUE_GAS_CORRECTED | BOILER C TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_CORRECTED_TPH*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_FUEL_GAS_CORRECTED_TPH; BOILER_C_STATUS | 0
BOILER_C_TOTAL_FLUE_GAS_GENERATED | BOILER C TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW/1000*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_C_STATUS | 0
BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER C TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_C_FG_CH4_MASS_PERCENTAGE+BOILER_C_FG_ETHANE_MASS_PERCENTAGE+BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_C_FG_PROPANE_MASS_PERCENTAGE+BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_C_FG_NITROGEN_MASS_PERCENTAGE+BOILER_C_FG_IC4_MASS_PERCENTAGE+BOILER_C_FG_NC4_MASS_PERCENTAGE+BOILER_C_FG_NC5_MASS_P | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_C_FG_CH4_MASS_PERCENTAGE; BOILER_C_FG_ETHANE_MASS_PERCENTAGE; BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_C_FG_IC4_MASS_PERCENTAGE; BOILER_C_FG_IC5_MASS_PERCENTAGE; BOILER_C_FG_NC4_MASS_PERCENTAGE; BOILER_C_FG_NC5_MASS_PERCENTAGE; BOILER_C_FG_NITROGEN_MASS_PERCENTAGE; BOILER_C_FG_PROPANE_MASS_PERCENTAGE | 100
BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER C TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_TOTAL_MOISTURE_WITH_AIR+BOILER_C_H2O_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_H2O_FORMED; BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER_C_H2O_FORMED; BOILER_C_TOTAL_MOISTURE_WITH_AIR | 1.868
BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER C TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_C_STATUS; BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 0
BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER C TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_C_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_MIXED_LHV_PER_KG; BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG; BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_C_STATUS | 0
BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER C TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_C_RADIATION_LOSSES) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_RADIATION_LOSSES; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_RADIATION_LOSSES; BOILER_C_STATUS; BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER C TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_AIR_MOISTURE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_AIR_FUEL_MASS_RATIO | BOILER_C_AIR_FUEL_MASS_RATIO | 0.009372
BOILER_C_TOTAL_STEAM_ENERGY | BOILER C TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_HP_STEAM_ENTHALPY; BOILER_C_STATUS | BOILER_C_HP_STEAM_ENTHALPY; BOILER_C_STATUS | 0
BOILER_C_UA_ECONOMIZER | BOILER C UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY/BOILER_C_LMTD_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_ECONOMIZER_DUTY; BOILER_C_LMTD_ECONOMIZER; BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY; BOILER_C_LMTD_ECONOMIZER; BOILER_C_STATUS
BOILER_C_VAPOUR_PRESSURE_OF_H2O | BOILER C VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631 |  |  | 4.631
BOILER_D_ACTUAL_SP_ENERGY_DELTA | BOILER D ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER D AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_D_AIR_CP_REF_T+BOILER_D_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | 0.24044
BOILER_D_AIR_CP_REF_T | BOILER D AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | COMPUTED | 6.96 |  |  | 6.96
BOILER_D_AIR_FUEL_MASS_RATIO | BOILER D AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_EXCESS_AIR+BOILER_D_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_EXCESS_AIR | BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_EXCESS_AIR | 14.5272
BOILER_D_AIR_MOISTURE | BOILER D AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_D_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_D_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645 |  |  | 0.000645
BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER D AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION | 13.7122
BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER D AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 14.4058
BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION | 0.43011
BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER D AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER D AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION | 0.04938
BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER D AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION | 0.020674
BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER D AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION | 0.058544
BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER D AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION | 0.000626
BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER D AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION | 0.13431
BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER D AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_D_CO2_FORMED/44.01+BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.85*BOILER_D_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_D_FLUE_GAS_MW)/BOILER_D_FLUE_GAS_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_MW; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_MW; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED | 0.21038
BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER D AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_D_FG_MW)/2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_D_FG_MW | BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_D_FG_MW | 0.43669
BOILER_D_BFW_ENERGY | BOILER D BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*BOILER_D_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_BFW_ENTHALPY; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS | BOILER_D_BFW_ENTHALPY; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS | 0
BOILER_D_BFW_ENTHALPY | BOILER D BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_D_INLET_TEMPERATURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_D_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_D_INLET_TEMPERATURE | 0
BOILER_D_BLOWDOWN_LOSS | BOILER D BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,((CBD_BLOW_DOWN_D/1000)*((BOILER_D_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_D | BFW_PRESSURE_TO_BOILER; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE; CBD_BLOW_DOWN_D | 0
BOILER_D_BOILER_INDIRECT_EFFICIENCY | BOILER D BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_D_BOILER_LOAD | BOILER D BOILER LOAD | LBM_preprocessing_inferred_tags_main | % | DESUPERHEATER_D_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.8534 |  |  | 1.8534
BOILER_D_CALCULATED_AIRFLOW_NM3H | BOILER D CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_D_STATUS==0,0,BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS | BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS | 0
BOILER_D_CH4_CO2_COMBUSTION | BOILER D CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION | 2.1793
BOILER_D_CH4_H2O_COMBUSTION | BOILER D CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION | 1.7838
BOILER_D_CH4_N2_COMBUSTION | BOILER D CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION | 10.5432
BOILER_D_CO2_EMISSIONS | BOILER D CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_CO2_FORMED*BOILER_D_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS | BOILER_D_CO2_FORMED; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS | 0
BOILER_D_CO2_FORMED | BOILER D CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_CH4_CO2_COMBUSTION+BOILER_D_ETHANE_CO2_COMBUSTION+BOILER_D_ETHYLENE_CO2_COMBUSTION+BOILER_D_PROPANE_CO2_COMBUSTION+BOILER_D_NC4_CO2_COMBUSTION+BOILER_D_IC4_CO2_COMBUSTION+BOILER_D_NC5_CO2_COMBUSTION+BOILER_D_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CH4_CO2_COMBUSTION; BOILER_D_ETHANE_CO2_COMBUSTION; BOILER_D_ETHYLENE_CO2_COMBUSTION; BOILER_D_IC4_CO2_COMBUSTION; BOILER_D_IC5_CO2_COMBUSTION; BOILER_D_NC4_CO2_COMBUSTION (+2 more) | BOILER_D_CH4_CO2_COMBUSTION; BOILER_D_ETHANE_CO2_COMBUSTION; BOILER_D_ETHYLENE_CO2_COMBUSTION; BOILER_D_IC4_CO2_COMBUSTION; BOILER_D_IC5_CO2_COMBUSTION; BOILER_D_NC4_CO2_COMBUSTION; BOILER_D_NC5_CO2_COMBUSTION; BOILER_D_PROPANE_CO2_COMBUSTION | 2.3084
BOILER_D_CONVECTION_DUTY | BOILER D CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY+BOILER_D_SH_DUTY+BOILER_D_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_ECONOMIZER_DUTY; BOILER_D_SH_DUTY; BOILER_D_STACK_LOSS_CORRECTED; BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY; BOILER_D_SH_DUTY; BOILER_D_STACK_LOSS_CORRECTED; BOILER_D_STATUS | 0
BOILER_D_CONVECTION_SECTION_EFFICIENCY | BOILER D CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CONVECTION_DUTY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS
BOILER_D_CORRECTED_BFW_FLOW | BOILER D CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_D_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-DESUPERHEATER_D_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_D))/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_D; BFW_FLOW_TO_ECONOMIZER_D; BOILER_D_STATUS; CBD_BLOW_DOWN_D | BFW_FLOW_TO_DESUPERHEATER_D; BFW_FLOW_TO_ECONOMIZER_D; BOILER_D_STATUS; CBD_BLOW_DOWN_D | 0
BOILER_D_CORRECTED_COMBUSTION_AIR | BOILER D CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_D_AIR_MOISTURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 14.4151
BOILER_D_CORRECTED_COMBUTION_H2O_FORMED | BOILER D CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2O_FORMED+(BOILER_D_CORRECTED_COMBUSTION_AIR-BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_H2O_FORMED | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_D_CORRECTED_COMBUSTION_AIR; BOILER_D_H2O_FORMED | 1.8679
BOILER_D_CORRECTED_FUEL_FLOW | BOILER D CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW-((BOILER_D_FUEL_GAS_ENERGY_INPUT-(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY+BOILER_D_BLOWDOWN_LOSS+BOILER_D_STACK_LOSS+BOILER_D_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_D_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_BFW_ENERGY; BOILER_D_BLOWDOWN_LOSS; BOILER_D_FUEL_GAS_ENERGY_INPUT; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STACK_LOSS (+2 more) | BOILER_D_BFW_ENERGY; BOILER_D_BLOWDOWN_LOSS; BOILER_D_FUEL_GAS_ENERGY_INPUT; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STACK_LOSS; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY | 0
BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER D CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | 0
BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER D CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*( | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_COMBUSTION_AIR_TEMPERATURE | BOILER_D_COMBUSTION_AIR_TEMPERATURE | 6.9662
BOILER_D_CP_CH4_FUEL_TEMP | BOILER D CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 8.3611
BOILER_D_CP_ETHANE_FUEL_TEMP | BOILER D CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 12.072
BOILER_D_CP_ETHYLENE_FUEL_TEMP | BOILER D CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 9.6636
BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER D CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6481 |  |  | 8.6481
BOILER_D_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER D CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3661 |  |  | 8.3661
BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER D CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586 |  |  | 6.9586
BOILER_D_CP_H2_FUEL_TEMP | BOILER D CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 6.8451
BOILER_D_CP_IC4_FUEL_TEMP | BOILER D CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 27.1042
BOILER_D_CP_IC5_FUEL_TEMP | BOILER D CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 25.8775
BOILER_D_CP_NC4_FUEL_TEMP | BOILER D CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 22.9244
BOILER_D_CP_NC5_FUEL_TEMP | BOILER D CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 26.1614
BOILER_D_CP_OF_AIR_AT_STACK_TEMP | BOILER D CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_D_STACK_TEMPERATURE+273.15)/ | COMPUTED | 6.9675 |  |  | 6.9675
BOILER_D_CP_OF_H2O_AT_STACK_TEMP | BOILER D CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644 |  |  | 0.4644
BOILER_D_CP_PROPANE_FUEL_TEMP | BOILER D CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 17.0442
BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER D CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_D_CP_H2_FUEL_TEMP+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_D_CP_CH4_FUEL_TEMP+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_D_CP_ETHYLENE_FUEL_TEMP+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CP_CH4_FUEL_TEMP; BOILER_D_CP_ETHANE_FUEL_TEMP; BOILER_D_CP_ETHYLENE_FUEL_TEMP; BOILER_D_CP_H2_FUEL_TEMP; BOILER_D_CP_IC4_FUEL_TEMP; BOILER_D_CP_IC5_FUEL_TEMP (+13 more) | BOILER_D_CP_CH4_FUEL_TEMP; BOILER_D_CP_ETHANE_FUEL_TEMP; BOILER_D_CP_ETHYLENE_FUEL_TEMP; BOILER_D_CP_H2_FUEL_TEMP; BOILER_D_CP_IC4_FUEL_TEMP; BOILER_D_CP_IC5_FUEL_TEMP; BOILER_D_CP_NC4_FUEL_TEMP; BOILER_D_CP_NC5_FUEL_TEMP; BOILER_D_CP_PROPANE_FUEL_TEMP; BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_ETHYLENE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_MW; BOILER_D_FG_NC4_MASS_FRACTION; BOILER_D_FG_NC5_MASS_FRACTION; BOILER_D_FG_PROPANE_MASS_FRACTION | 7.7284
BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER D CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_D_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_ETHYLENE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION (+4 more) | BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_ETHYLENE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_MW; BOILER_D_FG_NC4_MASS_FRACTION; BOILER_D_FG_NC5_MASS_FRACTION; BOILER_D_FG_PROPANE_MASS_FRACTION | 7.7229
BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_D_EXCESS_AIR*(1-BOILER_D_AIR_MOISTURE)+BOILER_D_N2_FORMED+BOILER_D_CO2_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_N2_FORMED | 13.497
BOILER_D_ECONOMIZER_DUTY | BOILER D ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_D_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_D_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE | 0
BOILER_D_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER D EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_BLOWDOWN_LOSS/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_BLOWDOWN_LOSS; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS | BOILER_D_BLOWDOWN_LOSS; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS
BOILER_D_ENERGY_GAINED | BOILER D ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_BFW_ENERGY; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY | 0
BOILER_D_ETHANE_CO2_COMBUSTION | BOILER D ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION | 0.078103
BOILER_D_ETHANE_H2O_COMBUSTION | BOILER D ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION | 0.047977
BOILER_D_ETHANE_N2_COMBUSTION | BOILER D ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION | 0.33072
BOILER_D_ETHYLENE_CO2_COMBUSTION | BOILER D ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_D_ETHYLENE_H2O_COMBUSTION | BOILER D ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_D_ETHYLENE_N2_COMBUSTION | BOILER D ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_D_EXCESS_AIR | BOILER D EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_D_FLUE_GAS_OXGYGEN)*((BOILER_D_N2_FORMED/28.01)+(BOILER_D_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_D_CO2_FORMED/44.01))/(20.95-BOILER_D_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_CORRECTED_COMBUTION_H2O_FORMED; BOILER_D_FLUE_GAS_OXGYGEN; BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED; BOILER_D_CORRECTED_COMBUTION_H2O_FORMED; BOILER_D_FLUE_GAS_OXGYGEN; BOILER_D_N2_FORMED | 0.1121
BOILER_D_FG_CH4_MASS_FRACTION | BOILER D FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_CH4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_D_FG_CH4_MASS_PERCENTAGE | BOILER D FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | 79.4217
BOILER_D_FG_DENSITY | BOILER D FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_D_FG_MW/22.414 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW | BOILER_D_FG_MW | 0.7893
BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER D FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_D_FG_ETHANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_D_FG_ETHANE_MASS_PERCENTAGE | BOILER D FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | 2.6684
BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER D FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE | BOILER D FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | 0
BOILER_D_FG_FLOW_RATE | BOILER D FG FLOW RATE | LBM_preprocessing_inferred_tags_main | TPH | BOILER_D_FUEL_GAS_FLOW/1000 | COMPUTED | 0.17549 |  |  | 0.17549
BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER D FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE | BOILER D FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | 0
BOILER_D_FG_IC4_MASS_FRACTION | BOILER D FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_IC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_D_FG_IC4_MASS_PERCENTAGE | BOILER D FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | 0.31885
BOILER_D_FG_IC5_MASS_FRACTION | BOILER D FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_IC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_D_FG_IC5_MASS_PERCENTAGE | BOILER D FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | 0.13466
BOILER_D_FG_MW | BOILER D FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_D_FG_IC4_CONCENTRATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_D_FG_N2_CONCENTRATION; NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | 17.6914
BOILER_D_FG_NC4_MASS_FRACTION | BOILER D FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC4_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_D_FG_NC4_MASS_PERCENTAGE | BOILER D FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | 0.37802
BOILER_D_FG_NC5_MASS_FRACTION | BOILER D FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC5_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_D_FG_NC5_MASS_PERCENTAGE | BOILER D FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | 0.004081
BOILER_D_FG_NITROGEN_MASS_FRACTION | BOILER D FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NITROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_D_FG_NITROGEN_MASS_PERCENTAGE | BOILER D FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | 16.219
BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER D FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_PROPANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_PROPANE_MASS_PERCENTAGE; BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_D_FG_PROPANE_MASS_PERCENTAGE | BOILER D FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | BOILER_D_FG_MW; NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | 0.85531
BOILER_D_FLUE_GAS_MW | BOILER D FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_D_CO2_FORMED/44.01+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.96) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_CO2_FORMED; BOILER_D_EXCESS_AIR; BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_N2_FORMED; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | 27.6615
BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | 15.365
BOILER_D_FOULING_INDEX | BOILER D FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_D_STATUS==0,0,1/BOILER_D_UA_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_UA_ECONOMIZER | BOILER_D_STATUS; BOILER_D_UA_ECONOMIZER
BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER D FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION | 99.942
BOILER_D_FUEL_CONSUMPTION | BOILER D FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | 0
BOILER_D_FUEL_GAIN_LOSS | BOILER D FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_D_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_D_FUEL_GAS_CORRECTED_TPH | BOILER D FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW; BOILER_D_STATUS | 0
BOILER_D_FUEL_GAS_ENERGY_INPUT | BOILER D FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_FG_FLOW_RATE*1000*BOILER_D_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | 0
BOILER_D_H2O_FORMED | BOILER D H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2_H2O_COMBUSTION+BOILER_D_CH4_H2O_COMBUSTION+BOILER_D_ETHANE_H2O_COMBUSTION+BOILER_D_ETHYLENE_H2O_COMBUSTION+BOILER_D_PROPANE_H2O_COMBUSTION+BOILER_D_IC4_H2O_COMBUSTION+BOILER_D_NC4_H2O_COMBUSTION+BOILER_D_IC5_H2O_COMBUSTION+BOILER_D_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CH4_H2O_COMBUSTION; BOILER_D_ETHANE_H2O_COMBUSTION; BOILER_D_ETHYLENE_H2O_COMBUSTION; BOILER_D_H2_H2O_COMBUSTION; BOILER_D_IC4_H2O_COMBUSTION; BOILER_D_IC5_H2O_COMBUSTION (+3 more) | BOILER_D_CH4_H2O_COMBUSTION; BOILER_D_ETHANE_H2O_COMBUSTION; BOILER_D_ETHYLENE_H2O_COMBUSTION; BOILER_D_H2_H2O_COMBUSTION; BOILER_D_IC4_H2O_COMBUSTION; BOILER_D_IC5_H2O_COMBUSTION; BOILER_D_NC4_H2O_COMBUSTION; BOILER_D_NC5_H2O_COMBUSTION; BOILER_D_PROPANE_H2O_COMBUSTION | 1.8586
BOILER_D_H2_CO2_COMBUSTION | BOILER D H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_D_H2_H2O_COMBUSTION | BOILER D H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_D_H2_N2_COMBUSTION | BOILER D H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER D HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_D_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS | BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS | 0
BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER D HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,9*(BOILER_D_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_D_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_D_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_STATUS | BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_STATUS | 0
BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER D HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_D_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | 0
BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER D HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,0*10^-6*28*5654*BOILER_D_BOILER_LOAD) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS | BOILER_D_STATUS | 0
BOILER_D_HP_STEAM_ENTHALPY | BOILER D HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_D)+2.66244961166282*DESUPERHEATER_D_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_D | BOILER_A_STATUS; HP_STEAM_PRESSURE_FROM_DS_D | 0
BOILER_D_IC4_CO2_COMBUSTION | BOILER D IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION | 0.009658
BOILER_D_IC4_H2O_COMBUSTION | BOILER D IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION | 0.005859
BOILER_D_IC4_N2_COMBUSTION | BOILER D IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION | 0.037969
BOILER_D_IC5_CO2_COMBUSTION | BOILER D IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION | 0.004107
BOILER_D_IC5_H2O_COMBUSTION | BOILER D IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION | 0.002017
BOILER_D_IC5_N2_COMBUSTION | BOILER D IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION | 0.015897
BOILER_D_LHV | BOILER D LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_D_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_D_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_D_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_D_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_D_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_D_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_D_FG_N | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_NC4_MASS_FRACTION (+3 more) | BOILER_D_FG_CH4_MASS_FRACTION; BOILER_D_FG_ETHANE_MASS_FRACTION; BOILER_D_FG_HYDROGEN_MASS_FRACTION; BOILER_D_FG_IC4_MASS_FRACTION; BOILER_D_FG_IC5_MASS_FRACTION; BOILER_D_FG_NC4_MASS_FRACTION; BOILER_D_FG_NC5_MASS_FRACTION; BOILER_D_FG_NITROGEN_MASS_FRACTION; BOILER_D_FG_PROPANE_MASS_FRACTION | 9984.6019
BOILER_D_LHV_DESIGEN | BOILER D LHV DESIGEN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_D_FG_DENSITY)/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_DENSITY | BOILER_D_FG_DENSITY | 39.6755
BOILER_D_LMTD_ECONOMIZER | BOILER D LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_D_STATUS==0,0,((673-ECONOMIZER_D_OUTLET_TEMPERATURE)-(BOILER_D_STACK_TEMPERATURE-ECONOMIZER_D_INLET_TEMPERATURE))/ln((673-ECONOMIZER_D_OUTLET_TEMPERATURE)/(-ECONOMIZER_D_INLET_TEMPERATURE+BOILER_D_STACK_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE | BOILER_D_STATUS; ECONOMIZER_D_INLET_TEMPERATURE; ECONOMIZER_D_OUTLET_TEMPERATURE
BOILER_D_MIXED_LHV_PER_KG | BOILER D MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main | Kcal/kg | (BOILER_LHV) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV | 9984.6019
BOILER_D_N2_FORMED | BOILER D N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_D_H2_N2_COMBUSTION+BOILER_D_CH4_N2_COMBUSTION+BOILER_D_ETHANE_N2_COMBUSTION+BOILER_D_ETHYLENE_N2_COMBUSTION+BOILER_D_PROPANE_N2_COMBUSTION+BOILER_D_IC4_N2_COMBUSTION+BOILER_D_NC4_N2_COMBUSTION+BOILER_D_IC5_N2_COMBUSTION+BOILER_D_NC5_N2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CH4_N2_COMBUSTION; BOILER_D_ETHANE_N2_COMBUSTION; BOILER_D_ETHYLENE_N2_COMBUSTION; BOILER_D_H2_N2_COMBUSTION; BOILER_D_IC4_N2_COMBUSTION; BOILER_D_IC5_N2_COMBUSTION (+3 more) | BOILER_D_CH4_N2_COMBUSTION; BOILER_D_ETHANE_N2_COMBUSTION; BOILER_D_ETHYLENE_N2_COMBUSTION; BOILER_D_H2_N2_COMBUSTION; BOILER_D_IC4_N2_COMBUSTION; BOILER_D_IC5_N2_COMBUSTION; BOILER_D_NC4_N2_COMBUSTION; BOILER_D_NC5_N2_COMBUSTION; BOILER_D_PROPANE_N2_COMBUSTION | 11.0766
BOILER_D_NC4_CO2_COMBUSTION | BOILER D NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION | 0.01145
BOILER_D_NC4_H2O_COMBUSTION | BOILER D NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION | 0.004942
BOILER_D_NC4_N2_COMBUSTION | BOILER D NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION | 0.045014
BOILER_D_NC5_CO2_COMBUSTION | BOILER D NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION | 0.000124
BOILER_D_NC5_H2O_COMBUSTION | BOILER D NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION | 6.1e-05
BOILER_D_NC5_N2_COMBUSTION | BOILER D NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION | 0.000482
BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER D PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS
BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER D PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_ENERGY_GAINED; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS | BOILER_D_ENERGY_GAINED; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS
BOILER_D_PROPANE_CO2_COMBUSTION | BOILER D PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION | 0.025608
BOILER_D_PROPANE_H2O_COMBUSTION | BOILER D PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION | 0.013976
BOILER_D_PROPANE_N2_COMBUSTION | BOILER D PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION | 0.10327
BOILER_D_RADIATION_DUTY | BOILER D RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_ENERGY_GAINED-BOILER_D_CONVECTION_DUTY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY; BOILER_D_ENERGY_GAINED; BOILER_D_STATUS | 0
BOILER_D_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER D RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_D_STATUS==0,0,BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_D_STATUS | BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION; BOILER_D_STATUS
BOILER_D_RADIATION_LOSSES | BOILER D RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_MIXED_LHV_PER_KG*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOAD^2-0.0899*BOILER_D_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | 0
BOILER_D_RADIATION_SECTION_EFFICIENCY | BOILER D RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_RADIATION_DUTY; BOILER_D_STATUS
BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER D SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_D_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_D_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_COMBUSTION_AIR_TEMPERATURE | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_D_COMBUSTION_AIR_TEMPERATURE | -51.4889
BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER D SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | 0
BOILER_D_SH_DUTY | BOILER D SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_D_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_D_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE | BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE; BOILER_D_SUPERHEATER_INLET_TEMPERATURE | 0
BOILER_D_SH_PERFORMANCE | BOILER D SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,(BOILER_D_SH_SPECIFIC_DUTY)/0.110075721*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_SH_SPECIFIC_DUTY; BOILER_D_STATUS | BOILER_D_SH_SPECIFIC_DUTY; BOILER_D_STATUS | 0
BOILER_D_SH_SPECIFIC_DUTY | BOILER D SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_D_STATUS==0,0,BOILER_D_SH_DUTY/DESUPERHEATER_D_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_SH_DUTY; BOILER_D_STATUS | BOILER_D_SH_DUTY; BOILER_D_STATUS | 0
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER D SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS | 0
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER D SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION; BOILER_D_STATUS | 0
BOILER_D_STACK_LOSS | BOILER D STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_D_STACK_LOSS_CORRECTED | BOILER D STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_D_STATUS | BOILER D STATUS | LBM_preprocessing_inferred_tags_main | - | if(BOILER_D_BOILER_LOAD>25&&DESUPERHEATER_D_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_D>40,1,0) | NOT COMPUTED |  | Missing inputs (not in hierarchy): HP_STEAM_PRESSURE_FROM_DS_D | HP_STEAM_PRESSURE_FROM_DS_D | 0
BOILER_D_STEAM_DRUM_TEMP | BOILER D STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_D_STATUS==0,0,4.02521999671835*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE | BOILER_D_STATUS; BOILER_D_STEAM_DRUM_PRESSURE | 0
BOILER_D_STEAM_TO_FIRE_DUTY_RATIO | BOILER D STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main | KG/ KCAL | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW/(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS | 0
BOILER_D_SUPERHEATED_STEAM_BFW_RATIO | BOILER D SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_D_STATUS==0,0,(DESUPERHEATER_D_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_D)/(BOILER_D_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; CBD_BLOW_DOWN_D | BOILER_D_CORRECTED_BFW_FLOW; BOILER_D_STATUS; CBD_BLOW_DOWN_D
BOILER_D_THERMAL_EFFICIENCY | BOILER D THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_D_STATUS==0,0,(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY)/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_BFW_ENERGY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER D TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_D_STATUS | BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4; BOILER_D_STATUS | 0
BOILER_D_TOTAL_FLUE_GAS_CORRECTED | BOILER D TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_CORRECTED_TPH*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_FUEL_GAS_CORRECTED_TPH; BOILER_D_STATUS | 0
BOILER_D_TOTAL_FLUE_GAS_GENERATED | BOILER D TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW/1000*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_D_STATUS | 0
BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER D TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_D_FG_CH4_MASS_PERCENTAGE+BOILER_D_FG_ETHANE_MASS_PERCENTAGE+BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_D_FG_PROPANE_MASS_PERCENTAGE+BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_D_FG_NITROGEN_MASS_PERCENTAGE+BOILER_D_FG_IC4_MASS_PERCENTAGE+BOILER_D_FG_NC4_MASS_PERCENTAGE+BOILER_D_FG_NC5_MASS_P | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_D_FG_CH4_MASS_PERCENTAGE; BOILER_D_FG_ETHANE_MASS_PERCENTAGE; BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_D_FG_IC4_MASS_PERCENTAGE; BOILER_D_FG_IC5_MASS_PERCENTAGE; BOILER_D_FG_NC4_MASS_PERCENTAGE; BOILER_D_FG_NC5_MASS_PERCENTAGE; BOILER_D_FG_NITROGEN_MASS_PERCENTAGE; BOILER_D_FG_PROPANE_MASS_PERCENTAGE | 100
BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER D TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_TOTAL_MOISTURE_WITH_AIR+BOILER_D_H2O_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_H2O_FORMED; BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER_D_H2O_FORMED; BOILER_D_TOTAL_MOISTURE_WITH_AIR | 1.868
BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER D TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_D_STATUS; BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 0
BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER D TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_D_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_MIXED_LHV_PER_KG; BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG; BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL; BOILER_D_STATUS | 0
BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER D TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_D_RADIATION_LOSSES) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_RADIATION_LOSSES; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_RADIATION_LOSSES; BOILER_D_STATUS; BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER D TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_AIR_MOISTURE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_AIR_FUEL_MASS_RATIO | BOILER_D_AIR_FUEL_MASS_RATIO | 0.009371
BOILER_D_TOTAL_STEAM_ENERGY | BOILER D TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_HP_STEAM_ENTHALPY; BOILER_D_STATUS | BOILER_D_HP_STEAM_ENTHALPY; BOILER_D_STATUS | 0
BOILER_D_UA_ECONOMIZER | BOILER D UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY/BOILER_D_LMTD_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_ECONOMIZER_DUTY; BOILER_D_LMTD_ECONOMIZER; BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY; BOILER_D_LMTD_ECONOMIZER; BOILER_D_STATUS
BOILER_D_VAPOUR_PRESSURE_OF_H2O | BOILER D VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631 |  |  | 4.631
BOILER_E_ACTUAL_SP_ENERGY_DELTA | BOILER E ACTUAL SP ENERGY DELTA | TRG_compute_inferred_pre_pta | GJ/ T | if((BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER E AIR CP FOR SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_E_AIR_CP_REF_T+BOILER_E_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | 0.24044
BOILER_E_AIR_CP_REF_T | BOILER E AIR CP REF T | LBM_preprocessing_inferred_tags_main | cal/kgK | 6.96 | COMPUTED | 6.96 |  |  | 6.96
BOILER_E_AIR_FUEL_MASS_RATIO | BOILER E AIR FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_EXCESS_AIR+BOILER_E_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_EXCESS_AIR | BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_EXCESS_AIR | 14.5458
BOILER_E_AIR_MOISTURE | BOILER E AIR MOISTURE | LBM_preprocessing_inferred_tags_main | KG MOIST/KG AIR | BOILER_E_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_E_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645 |  |  | 0.000645
BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER E AIR REQUIRED FOR CH4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION | 13.7122
BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER E AIR REQUIRED FOR COMPLETE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION+BO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION (+3 more) | BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION; BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 14.4058
BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION | 0.43011
BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHYLENE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER E AIR REQUIRED FOR H2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER E AIR REQUIRED FOR IC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION | 0.04938
BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER E AIR REQUIRED FOR IC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION | 0.020674
BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER E AIR REQUIRED FOR NC4 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION | 0.058544
BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER E AIR REQUIRED FOR NC5 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION | 0.000626
BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER E AIR REQUIRED FOR PROPANE COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION | 0.13431
BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER E AVG CP OF FLUE GAS AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_E_CO2_FORMED/44.01+BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.85*BOILER_E_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_E_FLUE_GAS_MW)/BOILER_E_FLUE_GAS_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_MW; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_MW; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED | 0.21045
BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER E AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | ((BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_E_FG_MW)/2 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_E_FG_MW | BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP; BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP; BOILER_E_FG_MW | 0.43677
BOILER_E_BFW_ENERGY | BOILER E BFW ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*BOILER_E_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_BFW_ENTHALPY; BOILER_E_CORRECTED_BFW_FLOW | BOILER_E_BFW_ENTHALPY; BOILER_E_CORRECTED_BFW_FLOW | 0
BOILER_E_BFW_ENTHALPY | BOILER E BFW ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,ECONOMIZER_E_INLET_TEMPERATURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; ECONOMIZER_E_INLET_TEMPERATURE | BOILER_A_STATUS; ECONOMIZER_E_INLET_TEMPERATURE | 0
BOILER_E_BLOWDOWN_LOSS | BOILER E BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,((CBD_BLOW_DOWN_E/1000)*((BOILER_E_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_E_STEAM_DRUM_TEMP*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_E_STEAM_DRUM_TEMP*4.22416911685416-3.01717714574329)*0.2390006))/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; CBD_BLOW_DOWN_E | BFW_PRESSURE_TO_BOILER; CBD_BLOW_DOWN_E | 0
BOILER_E_BOILER_INDIRECT_EFFICIENCY | BOILER E BOILER INDIRECT EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_E_BOILER_LOAD | BOILER E BOILER LOAD | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | DESUPERHEATER_E_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.8692 |  |  | 1.8692
BOILER_E_CALCULATED_AIRFLOW_NM3H | BOILER E CALCULATED AIRFLOW NM3H | LBM_preprocessing_inferred_tags_main | Nm3/h | if(BOILER_E_STATUS==0,0,BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_CORRECTED_FUEL_FLOW | 0
BOILER_E_CH4_CO2_COMBUSTION | BOILER E CH4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION | 2.1793
BOILER_E_CH4_H2O_COMBUSTION | BOILER E CH4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION | 1.7838
BOILER_E_CH4_N2_COMBUSTION | BOILER E CH4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION | 10.5432
BOILER_E_CO2_EMISSIONS | BOILER E CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_CO2_FORMED*BOILER_E_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_CO2_FORMED; BOILER_E_FUEL_GAS_CORRECTED_TPH | 0
BOILER_E_CO2_FORMED | BOILER E CO2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_CH4_CO2_COMBUSTION+BOILER_E_ETHANE_CO2_COMBUSTION+BOILER_E_ETHYLENE_CO2_COMBUSTION+BOILER_E_PROPANE_CO2_COMBUSTION+BOILER_E_NC4_CO2_COMBUSTION+BOILER_E_IC4_CO2_COMBUSTION+BOILER_E_NC5_CO2_COMBUSTION+BOILER_E_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CH4_CO2_COMBUSTION; BOILER_E_ETHANE_CO2_COMBUSTION; BOILER_E_ETHYLENE_CO2_COMBUSTION; BOILER_E_IC4_CO2_COMBUSTION; BOILER_E_IC5_CO2_COMBUSTION; BOILER_E_NC4_CO2_COMBUSTION (+2 more) | BOILER_E_CH4_CO2_COMBUSTION; BOILER_E_ETHANE_CO2_COMBUSTION; BOILER_E_ETHYLENE_CO2_COMBUSTION; BOILER_E_IC4_CO2_COMBUSTION; BOILER_E_IC5_CO2_COMBUSTION; BOILER_E_NC4_CO2_COMBUSTION; BOILER_E_NC5_CO2_COMBUSTION; BOILER_E_PROPANE_CO2_COMBUSTION | 2.3084
BOILER_E_CONVECTION_DUTY | BOILER E CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY+BOILER_E_SH_DUTY+BOILER_E_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_ECONOMIZER_DUTY; BOILER_E_STACK_LOSS_CORRECTED | BOILER_E_ECONOMIZER_DUTY; BOILER_E_STACK_LOSS_CORRECTED | 0
BOILER_E_CONVECTION_SECTION_EFFICIENCY | BOILER E CONVECTION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CONVECTION_DUTY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_CONVECTION_DUTY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
BOILER_E_CORRECTED_BFW_FLOW | BOILER E CORRECTED BFW FLOW | LBM_preprocessing_inferred_tags_main | T/h | if(BOILER_E_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-DESUPERHEATER_E_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_E))/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_FLOW_TO_DESUPERHEATER_E; BFW_FLOW_TO_ECONOMIZER_E; CBD_BLOW_DOWN_E | BFW_FLOW_TO_DESUPERHEATER_E; BFW_FLOW_TO_ECONOMIZER_E; CBD_BLOW_DOWN_E | 0
BOILER_E_CORRECTED_COMBUSTION_AIR | BOILER E CORRECTED COMBUSTION AIR | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_E_AIR_MOISTURE) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 14.4151
BOILER_E_CORRECTED_COMBUTION_H2O_FORMED | BOILER E CORRECTED COMBUTION H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2O_FORMED+(BOILER_E_CORRECTED_COMBUSTION_AIR-BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_H2O_FORMED | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION; BOILER_E_CORRECTED_COMBUSTION_AIR; BOILER_E_H2O_FORMED | 1.8679
BOILER_E_CORRECTED_FUEL_FLOW | BOILER E CORRECTED FUEL FLOW | LBM_preprocessing_inferred_tags_main | kg/hr | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295-((BOILER_E_FUEL_GAS_ENERGY_INPUT-(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY+BOILER_E_BLOWDOWN_LOSS+BOILER_E_STACK_LOSS+BOILER_E_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_E_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOIL | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_BFW_ENERGY; BOILER_E_BLOWDOWN_LOSS; BOILER_E_FUEL_GAS_ENERGY_INPUT; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_E_MIXED_LHV_PER_KG; BOILER_E_STACK_LOSS (+1 more) | BOILER_E_BFW_ENERGY; BOILER_E_BLOWDOWN_LOSS; BOILER_E_FUEL_GAS_ENERGY_INPUT; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3; BOILER_E_MIXED_LHV_PER_KG; BOILER_E_STACK_LOSS; BOILER_E_TOTAL_STEAM_ENERGY | 0
BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER E CORRECTED FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG | 0
BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER E CP AT COMBUSTION TEMPERATURE | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)-9.647459*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2+16.63537*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^3+(0.000117/((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_COMBUSTION_AIR_TEM | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_COMBUSTION_AIR_TEMP | BOILER_E_COMBUSTION_AIR_TEMP | 6.9665
BOILER_E_CP_CH4_FUEL_TEMP | BOILER E CP CH4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((-0.703029)+108.4773*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 8.3641
BOILER_E_CP_ETHANE_FUEL_TEMP | BOILER E CP ETHANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (6.08160993967773+173.58246031667*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 12.0902
BOILER_E_CP_ETHYLENE_FUEL_TEMP | BOILER E CP ETHYLENE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-6.38788+184.4019*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 9.6778
BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER E CP FLUE GAS CO2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((24.99735)+55.18696*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6572 |  |  | 8.6572
BOILER_E_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER E CP FLUE GAS H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | 8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3667 |  |  | 8.3667
BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER E CP FLUE GAS N2 AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9587 |  |  | 6.9587
BOILER_E_CP_H2_FUEL_TEMP | BOILER E CP H2 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((33.066178)-11.363417*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 6.8465
BOILER_E_CP_IC4_FUEL_TEMP | BOILER E CP IC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (8.32665517242186+344.923323425655*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 27.1642
BOILER_E_CP_IC5_FUEL_TEMP | BOILER E CP IC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-16.1426869390769+517.363683637786*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 25.9245
BOILER_E_CP_NC4_FUEL_TEMP | BOILER E CP NC4 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (22.1581076705715+292.589410831127*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 22.9597
BOILER_E_CP_NC5_FUEL_TEMP | BOILER E CP NC5 FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (-36.7350853904756+580.375772029461*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))* | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 26.2004
BOILER_E_CP_OF_AIR_AT_STACK_TEMP | BOILER E CP OF AIR AT STACK TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_STACK_TEMPERATURE+273.15)/ | COMPUTED | 6.9677 |  |  | 6.9677
BOILER_E_CP_OF_H2O_AT_STACK_TEMP | BOILER E CP OF H2O AT STACK TEMP | LBM_preprocessing_inferred_tags_main | KCAL/Kg°C | (8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.46443 |  |  | 0.46443
BOILER_E_CP_PROPANE_FUEL_TEMP | BOILER E CP PROPANE FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | (12.6608072783283+232.070245794953*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 17.0717
BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER E CP TOTAL FUEL AT FUEL TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_E_CP_H2_FUEL_TEMP+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_E_CP_CH4_FUEL_TEMP+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_E_CP_ETHYLENE_FUEL_TEMP+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHA | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CP_CH4_FUEL_TEMP; BOILER_E_CP_ETHANE_FUEL_TEMP; BOILER_E_CP_ETHYLENE_FUEL_TEMP; BOILER_E_CP_H2_FUEL_TEMP; BOILER_E_CP_IC4_FUEL_TEMP; BOILER_E_CP_IC5_FUEL_TEMP (+13 more) | BOILER_E_CP_CH4_FUEL_TEMP; BOILER_E_CP_ETHANE_FUEL_TEMP; BOILER_E_CP_ETHYLENE_FUEL_TEMP; BOILER_E_CP_H2_FUEL_TEMP; BOILER_E_CP_IC4_FUEL_TEMP; BOILER_E_CP_IC5_FUEL_TEMP; BOILER_E_CP_NC4_FUEL_TEMP; BOILER_E_CP_NC5_FUEL_TEMP; BOILER_E_CP_PROPANE_FUEL_TEMP; BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_ETHYLENE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_MW; BOILER_E_FG_NC4_MASS_FRACTION; BOILER_E_FG_NC5_MASS_FRACTION; BOILER_E_FG_PROPANE_MASS_FRACTION | 7.7312
BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER E CP TOTAL FUEL AT REF TEMP | LBM_preprocessing_inferred_tags_main | CAL/MOL °C | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_E_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_ETHYLENE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION (+4 more) | BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_ETHYLENE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_MW; BOILER_E_FG_NC4_MASS_FRACTION; BOILER_E_FG_NC5_MASS_FRACTION; BOILER_E_FG_PROPANE_MASS_FRACTION | 7.7229
BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E DRY FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_E_EXCESS_AIR*(1-BOILER_E_AIR_MOISTURE)+BOILER_E_N2_FORMED+BOILER_E_CO2_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_N2_FORMED | 13.5156
BOILER_E_ECONOMIZER_DUTY | BOILER E ECONOMIZER DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_E_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_E_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_PRESSURE_TO_BOILER; BOILER_E_CORRECTED_BFW_FLOW; ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE | BFW_PRESSURE_TO_BOILER; BOILER_E_CORRECTED_BFW_FLOW; ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE | 0
BOILER_E_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER E EFFICIENCY LOSS DUE TO BLOWDOWN | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_BLOWDOWN_LOSS/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_BLOWDOWN_LOSS; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_BLOWDOWN_LOSS; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
BOILER_E_ENERGY_GAINED | BOILER E ENERGY GAINED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_BFW_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY | 0
BOILER_E_ETHANE_CO2_COMBUSTION | BOILER E ETHANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION | 0.078103
BOILER_E_ETHANE_H2O_COMBUSTION | BOILER E ETHANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION | 0.047977
BOILER_E_ETHANE_N2_COMBUSTION | BOILER E ETHANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION | 0.33072
BOILER_E_ETHYLENE_CO2_COMBUSTION | BOILER E ETHYLENE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_E_ETHYLENE_H2O_COMBUSTION | BOILER E ETHYLENE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_E_ETHYLENE_N2_COMBUSTION | BOILER E ETHYLENE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION | 0
BOILER_E_EXCESS_AIR | BOILER E EXCESS AIR | LBM_preprocessing_inferred_tags_main | KG | ((28.96*BOILER_E_FLUE_GAS_OXGYGEN_NEW)*((BOILER_E_N2_FORMED/28.01)+(BOILER_E_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_E_CO2_FORMED/44.01))/(20.95-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_CORRECTED_COMBUTION_H2O_FORMED; BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED; BOILER_E_CORRECTED_COMBUTION_H2O_FORMED; BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_N2_FORMED | 0.13068
BOILER_E_FG_CH4_MASS_FRACTION | BOILER E FG CH4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_CH4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.79422
BOILER_E_FG_CH4_MASS_PERCENTAGE | BOILER E FG CH4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | 79.4217
BOILER_E_FG_DENSITY | BOILER E FG DENSITY | LBM_preprocessing_inferred_tags_main | KG/NM3 | BOILER_E_FG_MW/22.414 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW | BOILER_E_FG_MW | 0.7893
BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER E FG ETHANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_E_FG_ETHANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.026684
BOILER_E_FG_ETHANE_MASS_PERCENTAGE | BOILER E FG ETHANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | 2.6684
BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER E FG ETHYLENE MASS FRACTION | LBM_preprocessing_inferred_tags_main | - | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE | BOILER E FG ETHYLENE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | 0
BOILER_E_FG_FLOW_RATE | BOILER E FG FLOW RATE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | TPH | BOILER_E_FUEL_GAS_FLOW/1.295/1000 | COMPUTED | 0.17993 |  |  | 0.17993
BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER E FG HYDROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0
BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE | BOILER E FG HYDROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | 0
BOILER_E_FG_IC4_MASS_FRACTION | BOILER E FG IC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_IC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.003188
BOILER_E_FG_IC4_MASS_PERCENTAGE | BOILER E FG IC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | 0.31885
BOILER_E_FG_IC5_MASS_FRACTION | BOILER E FG IC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_IC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.001347
BOILER_E_FG_IC5_MASS_PERCENTAGE | BOILER E FG IC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | % | NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | 0.13466
BOILER_E_FG_MW | BOILER E FG MW | LBM_preprocessing_inferred_tags_main | G/MOL | (NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_E_FG_IC4_CONCENTRATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION (+4 more) | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION; NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION; NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION; NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION; NORMALIZED_BOILER_E_FG_N2_CONCENTRATION; NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION; NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION; NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | 17.6914
BOILER_E_FG_NC4_MASS_FRACTION | BOILER E FG NC4 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC4_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.00378
BOILER_E_FG_NC4_MASS_PERCENTAGE | BOILER E FG NC4 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | 0.37802
BOILER_E_FG_NC5_MASS_FRACTION | BOILER E FG NC5 MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC5_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 4.1e-05
BOILER_E_FG_NC5_MASS_PERCENTAGE | BOILER E FG NC5 MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | 0.004081
BOILER_E_FG_NITROGEN_MASS_FRACTION | BOILER E FG NITROGEN MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NITROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.16219
BOILER_E_FG_NITROGEN_MASS_PERCENTAGE | BOILER E FG NITROGEN MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | 16.219
BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER E FG PROPANE MASS FRACTION | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_PROPANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_PROPANE_MASS_PERCENTAGE; BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 0.008553
BOILER_E_FG_PROPANE_MASS_PERCENTAGE | BOILER E FG PROPANE MASS PERCENTAGE | LBM_preprocessing_inferred_tags_main | WT% | NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | BOILER_E_FG_MW; NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | 0.85531
BOILER_E_FLUE_GAS_MW | BOILER E FLUE GAS MW | LBM_preprocessing_inferred_tags_main | kg/kmol | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_E_CO2_FORMED/44.01+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.96) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_CO2_FORMED; BOILER_E_EXCESS_AIR; BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_N2_FORMED; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | 27.663
BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E FLUE GAS PER FUEL MASS RATIO | LBM_preprocessing_inferred_tags_main | KG/KG fuel | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | 15.3836
BOILER_E_FOULING_INDEX | BOILER E FOULING INDEX | LBM_preprocessing_inferred_tags_main | DEGC h/Gcal | if(BOILER_E_STATUS==0,0,1/BOILER_E_UA_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_UA_ECONOMIZER | BOILER_E_UA_ECONOMIZER
BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER E FUEL COMPOSITION TOTAL | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION (+3 more) | BOILER_FG_CH4_CONCENTRATION; BOILER_FG_ETHANE_CONCENTRATION; BOILER_FG_HYDROGEN_CONCENTRATION; BOILER_FG_IC4_CONCENTRATION; BOILER_FG_IC5_CONCENTRATION; BOILER_FG_N2_CONCENTRATION; BOILER_FG_NC4_CONCENTRATION; BOILER_FG_NC5_CONCENTRATION; BOILER_FG_PROPANE_CONCENTRATION | 99.942
BOILER_E_FUEL_CONSUMPTION | BOILER E FUEL CONSUMPTION | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW; BOILER_E_MIXED_LHV_PER_KG | 0
BOILER_E_FUEL_GAIN_LOSS | BOILER E FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | ([BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_E_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER E FUEL GAS CORRECTED TPH | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_CORRECTED_FUEL_FLOW | 0
BOILER_E_FUEL_GAS_ENERGY_INPUT | BOILER E FUEL GAS ENERGY INPUT | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_FG_FLOW_RATE*1000*BOILER_E_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG | 0
BOILER_E_H2O_FORMED | BOILER E H2O FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2_H2O_COMBUSTION+BOILER_E_CH4_H2O_COMBUSTION+BOILER_E_ETHANE_H2O_COMBUSTION+BOILER_E_ETHYLENE_H2O_COMBUSTION+BOILER_E_PROPANE_H2O_COMBUSTION+BOILER_E_IC4_H2O_COMBUSTION+BOILER_E_NC4_H2O_COMBUSTION+BOILER_E_IC5_H2O_COMBUSTION+BOILER_E_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CH4_H2O_COMBUSTION; BOILER_E_ETHANE_H2O_COMBUSTION; BOILER_E_ETHYLENE_H2O_COMBUSTION; BOILER_E_H2_H2O_COMBUSTION; BOILER_E_IC4_H2O_COMBUSTION; BOILER_E_IC5_H2O_COMBUSTION (+3 more) | BOILER_E_CH4_H2O_COMBUSTION; BOILER_E_ETHANE_H2O_COMBUSTION; BOILER_E_ETHYLENE_H2O_COMBUSTION; BOILER_E_H2_H2O_COMBUSTION; BOILER_E_IC4_H2O_COMBUSTION; BOILER_E_IC5_H2O_COMBUSTION; BOILER_E_NC4_H2O_COMBUSTION; BOILER_E_NC5_H2O_COMBUSTION; BOILER_E_PROPANE_H2O_COMBUSTION | 1.8586
BOILER_E_H2_CO2_COMBUSTION | BOILER E H2 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_E_H2_H2O_COMBUSTION | BOILER E H2 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_E_H2_N2_COMBUSTION | BOILER E H2 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER E HEAT LOSS DUE TO DRY FLUE GAS L1 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_E_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP; BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 0
BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER E HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,9*(BOILER_E_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_E_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_E_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION | 0
BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER E HEAT LOSS DUE TO H2O IN STACK L3 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_E_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | 0
BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER E HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,0*10^-6*28*5654*BOILER_E_BOILER_LOAD) | COMPUTED | 0 |  |  | 0
BOILER_E_HP_STEAM_ENTHALPY | BOILER E HP STEAM ENTHALPY | LBM_preprocessing_inferred_tags_main | Kcal/Kg | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_E)+2.66244961166282*DESUPERHEATER_E_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS | BOILER_A_STATUS | 0
BOILER_E_IC4_CO2_COMBUSTION | BOILER E IC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION | 0.009658
BOILER_E_IC4_H2O_COMBUSTION | BOILER E IC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION | 0.005859
BOILER_E_IC4_N2_COMBUSTION | BOILER E IC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION | 0.037969
BOILER_E_IC5_CO2_COMBUSTION | BOILER E IC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION | 0.004107
BOILER_E_IC5_H2O_COMBUSTION | BOILER E IC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION | 0.002017
BOILER_E_IC5_N2_COMBUSTION | BOILER E IC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION | 0.015897
BOILER_E_LHV | BOILER E LHV | LBM_preprocessing_inferred_tags_main | MJ/KG | (BOILER_E_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_E_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_E_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_E_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_E_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_E_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_E_FG_N | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_NC4_MASS_FRACTION (+3 more) | BOILER_E_FG_CH4_MASS_FRACTION; BOILER_E_FG_ETHANE_MASS_FRACTION; BOILER_E_FG_HYDROGEN_MASS_FRACTION; BOILER_E_FG_IC4_MASS_FRACTION; BOILER_E_FG_IC5_MASS_FRACTION; BOILER_E_FG_NC4_MASS_FRACTION; BOILER_E_FG_NC5_MASS_FRACTION; BOILER_E_FG_NITROGEN_MASS_FRACTION; BOILER_E_FG_PROPANE_MASS_FRACTION | 9984.6019
BOILER_E_LHV_DESIGN | BOILER E LHV DESIGN | LBM_preprocessing_inferred_tags_main | - | (LHV_FG/BOILER_E_FG_DENSITY)/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_DENSITY | BOILER_E_FG_DENSITY | 39.6755
BOILER_E_LMTD_ECONOMIZER | BOILER E LMTD ECONOMIZER | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_E_STATUS==0,0,((673-ECONOMIZER_E_OUTLET_TEMPERATURE)-(BOILER_E_STACK_TEMPERATURE-ECONOMIZER_E_INLET_TEMPERATURE))/ln((673-ECONOMIZER_E_OUTLET_TEMPERATURE)/(-ECONOMIZER_E_INLET_TEMPERATURE+BOILER_E_STACK_TEMPERATURE))) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE | ECONOMIZER_E_INLET_TEMPERATURE; ECONOMIZER_E_OUTLET_TEMPERATURE
BOILER_E_MIXED_LHV_PER_KG | BOILER E MIXED LHV PER KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | Kcal/kg | (BOILER_LHV) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_LHV | BOILER_LHV | 9984.6019
BOILER_E_N2_FORMED | BOILER E N2 FORMED | LBM_preprocessing_inferred_tags_main | KG | BOILER_E_H2_N2_COMBUSTION+BOILER_E_CH4_N2_COMBUSTION+BOILER_E_ETHANE_N2_COMBUSTION+BOILER_E_ETHYLENE_N2_COMBUSTION+BOILER_E_PROPANE_N2_COMBUSTION+BOILER_E_IC4_N2_COMBUSTION+BOILER_E_NC4_N2_COMBUSTION+BOILER_E_IC5_N2_COMBUSTION+BOILER_E_NC5_N2_COMBUSTION | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CH4_N2_COMBUSTION; BOILER_E_ETHANE_N2_COMBUSTION; BOILER_E_ETHYLENE_N2_COMBUSTION; BOILER_E_H2_N2_COMBUSTION; BOILER_E_IC4_N2_COMBUSTION; BOILER_E_IC5_N2_COMBUSTION (+3 more) | BOILER_E_CH4_N2_COMBUSTION; BOILER_E_ETHANE_N2_COMBUSTION; BOILER_E_ETHYLENE_N2_COMBUSTION; BOILER_E_H2_N2_COMBUSTION; BOILER_E_IC4_N2_COMBUSTION; BOILER_E_IC5_N2_COMBUSTION; BOILER_E_NC4_N2_COMBUSTION; BOILER_E_NC5_N2_COMBUSTION; BOILER_E_PROPANE_N2_COMBUSTION | 11.0766
BOILER_E_NC4_CO2_COMBUSTION | BOILER E NC4 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION | 0.01145
BOILER_E_NC4_H2O_COMBUSTION | BOILER E NC4 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION | 0.004942
BOILER_E_NC4_N2_COMBUSTION | BOILER E NC4 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION | 0.045014
BOILER_E_NC5_CO2_COMBUSTION | BOILER E NC5 CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION | 0.000124
BOILER_E_NC5_H2O_COMBUSTION | BOILER E NC5 H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION | 6.1e-05
BOILER_E_NC5_N2_COMBUSTION | BOILER E NC5 N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION | 0.000482
BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER E PERC DUTY GAINED IN CONVECTION SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED
BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER E PER DUTY GAINED IN RADIANT SECTION | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_ENERGY_GAINED*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_ENERGY_GAINED; BOILER_E_RADIATION_DUTY | BOILER_E_ENERGY_GAINED; BOILER_E_RADIATION_DUTY
BOILER_E_PROPANE_CO2_COMBUSTION | BOILER E PROPANE CO2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION | 0.025608
BOILER_E_PROPANE_H2O_COMBUSTION | BOILER E PROPANE H2O COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION | 0.013976
BOILER_E_PROPANE_N2_COMBUSTION | BOILER E PROPANE N2 COMBUSTION | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION | 0.10327
BOILER_E_RADIATION_DUTY | BOILER E RADIATION DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_ENERGY_GAINED-BOILER_E_CONVECTION_DUTY) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY; BOILER_E_ENERGY_GAINED | 0
BOILER_E_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER E RADIATION DUTY/CONVECTION DUTY | LBM_preprocessing_inferred_tags_main | [-] | if(BOILER_E_STATUS==0,0,BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION; BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION
BOILER_E_RADIATION_LOSSES | BOILER E RADIATION LOSSES | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_MIXED_LHV_PER_KG*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOILER_LOAD^2-0.0899*BOILER_E_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG | 0
BOILER_E_RADIATION_SECTION_EFFICIENCY | BOILER E RADIATION SECTION EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_RADIATION_DUTY | BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_RADIATION_DUTY
BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER E SENSBILE HEAT CORRECTION FOR AIR | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_E_COMBUSTION_AIR_TEMP-15.6)*BOILER_E_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_COMBUSTION_AIR_TEMP | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED; BOILER_E_AIR_FUEL_MASS_RATIO; BOILER_E_COMBUSTION_AIR_TEMP | -48.2191
BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER E SENSIBLE HEAT CORRECTION FOR FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED; BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | 0
BOILER_E_SH_DUTY | BOILER E SH DUTY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_E_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_E_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_E_STEAM_DRUM_TEMP*3.45877718874616+2082.10231045632))*0.239006/10000 | COMPUTED | 0 |  |  | 0
BOILER_E_SH_PERFORMANCE | BOILER E SH PERFORMANCE | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,(BOILER_E_SH_SPECIFIC_DUTY)/0.110075721*100) | COMPUTED | 0 |  |  | 0
BOILER_E_SH_SPECIFIC_DUTY | BOILER E SH SPECIFIC DUTY | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_E_STATUS==0,0,BOILER_E_SH_DUTY/DESUPERHEATER_E_OUTLET_STEAM_FLOW*1000) | COMPUTED | 0 |  |  | 0
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER E SPECIFIC ENERGY CONSUMPTION IN GCAL | LBM_preprocessing_inferred_tags_main | Gcal/t | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION | 0
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER E SPECIFIC ENERGY CONSUMPTION IN GJ | LBM_preprocessing_inferred_tags_main | GJ/t | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION | 0
BOILER_E_STACK_LOSS | BOILER E STACK LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_FLOW/1.295/(1000*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_E_STACK_LOSS_CORRECTED | BOILER E STACK LOSS CORRECTED | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_GAS_CORRECTED_TPH; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_FUEL_GAS_CORRECTED_TPH; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_E_STATUS | BOILER E STATUS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | - | if(BOILER_E_BOILER_LOAD>25&&DESUPERHEATER_E_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_E>40,1,0) | COMPUTED | 0 |  |  | 0
BOILER_E_STEAM_DRUM_PRESSURE | BOILER E STEAM DRUM PRESSURE | LBM_preprocessing_inferred_tags_main | nan | if(HP_STEAM_PRESSURE_FROM_DS_E==MISSING_NUMERIC,0,HP_STEAM_PRESSURE_FROM_DS_E) | COMPUTED | 1.884 |  |  | 1.884
BOILER_E_STEAM_DRUM_TEMP | BOILER E STEAM DRUM TEMP | LBM_preprocessing_inferred_tags_main | DEGC | if(BOILER_E_STATUS==0,0,4.02521999671835*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | COMPUTED | 0 |  |  | 0
BOILER_E_STEAM_TO_FIRE_DUTY_RATIO | BOILER E STEAM TO FIRE DUTY RATIO | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | KG/ KCAL | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW/(BOILER_E_FG_FLOW_RATE*BOILER_E_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG | 0
BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER E SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | - | if(BOILER_E_STATUS==0,0,(DESUPERHEATER_E_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_E)/(BOILER_E_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_CORRECTED_BFW_FLOW; CBD_BLOW_DOWN_E | BOILER_E_CORRECTED_BFW_FLOW; CBD_BLOW_DOWN_E
BOILER_E_THERMAL_EFFICIENCY | BOILER E THERMAL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | if(BOILER_E_STATUS==0,0,(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY)/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_BFW_ENERGY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER E TOTAL BOILER STACK LOSS PER KG FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1; BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2; BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | 0
BOILER_E_TOTAL_FLUE_GAS_CORRECTED | BOILER E TOTAL FLUE GAS CORRECTED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_CORRECTED_TPH*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO; BOILER_E_FUEL_GAS_CORRECTED_TPH | 0
BOILER_E_TOTAL_FLUE_GAS_GENERATED | BOILER E TOTAL FLUE GAS GENERATED | LBM_preprocessing_inferred_tags_main | t/h | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295/1000*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | 0
BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER E TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main | % | BOILER_E_FG_CH4_MASS_PERCENTAGE+BOILER_E_FG_ETHANE_MASS_PERCENTAGE+BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_E_FG_PROPANE_MASS_PERCENTAGE+BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_E_FG_NITROGEN_MASS_PERCENTAGE+BOILER_E_FG_IC4_MASS_PERCENTAGE+BOILER_E_FG_NC4_MASS_PERCENTAGE+BOILER_E_FG_NC5_MASS_P | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_E_FG_CH4_MASS_PERCENTAGE; BOILER_E_FG_ETHANE_MASS_PERCENTAGE; BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_E_FG_IC4_MASS_PERCENTAGE; BOILER_E_FG_IC5_MASS_PERCENTAGE; BOILER_E_FG_NC4_MASS_PERCENTAGE; BOILER_E_FG_NC5_MASS_PERCENTAGE; BOILER_E_FG_NITROGEN_MASS_PERCENTAGE; BOILER_E_FG_PROPANE_MASS_PERCENTAGE | 100
BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER E TOTAL H2O PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_TOTAL_MOISTURE_WITH_AIR+BOILER_E_H2O_FORMED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_H2O_FORMED; BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER_E_H2O_FORMED; BOILER_E_TOTAL_MOISTURE_WITH_AIR | 1.868
BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER E TOTAL HEAT ABSORBED PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL; BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 0
BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER E TOTAL HEAT INPUT PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_E_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_MIXED_LHV_PER_KG; BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER_E_MIXED_LHV_PER_KG; BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR; BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | 0
BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER E TOTAL HEAT LOSS PER KG OF FUEL | LBM_preprocessing_inferred_tags_main | KCAL/KG Fuel | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_E_RADIATION_LOSSES) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_RADIATION_LOSSES; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_RADIATION_LOSSES; BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 0
BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER E TOTAL MOISTURE WITH AIR | LBM_preprocessing_inferred_tags_main | KG/ KG FUEL | BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_AIR_MOISTURE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_E_AIR_FUEL_MASS_RATIO | 0.009383
BOILER_E_TOTAL_STEAM_ENERGY | BOILER E TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_HP_STEAM_ENTHALPY | BOILER_E_HP_STEAM_ENTHALPY | 0
BOILER_E_UA_ECONOMIZER | BOILER E UA ECONOMIZER | LBM_preprocessing_inferred_tags_main | Gcal/h/DEGC | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY/BOILER_E_LMTD_ECONOMIZER) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_ECONOMIZER_DUTY; BOILER_E_LMTD_ECONOMIZER | BOILER_E_ECONOMIZER_DUTY; BOILER_E_LMTD_ECONOMIZER
BOILER_E_VAPOUR_PRESSURE_OF_H2O | BOILER E VAPOUR PRESSURE OF H2O | LBM_preprocessing_inferred_tags_main | MMHG | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631 |  |  | 4.631
BOILER_FG_CH4_CONCENTRATION | BOILER FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CH4_CONCENTRATION_ARRAZI,87.548) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 87.548
BOILER_FG_CO2_CONCENTRATION | BOILER FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CO2_CONCENTRATION_ARRAZI,0) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 0
BOILER_FG_ETHANE_CONCENTRATION | BOILER FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_ETHANE_CONCENTRATION_ARRAZI,1.569) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 1.569
BOILER_FG_ETHYLENE_CONCENTRATION | BOILER FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 0 | COMPUTED | 0 |  |  | 0
BOILER_FG_HYDROGEN_CONCENTRATION | BOILER FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,0,0) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 0
BOILER_FG_IC4_CONCENTRATION | BOILER FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC4_CONCENTRATION_ARRAZI,.097) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 0.097
BOILER_FG_IC5_CONCENTRATION | BOILER FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC5_CONCENTRATION_ARRAZI,.033) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 0.033
BOILER_FG_N2_CONCENTRATION | BOILER FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_N2_CONCENTRATION_ARRAZI,10.236) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 10.236
BOILER_FG_NC4_CONCENTRATION | BOILER FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC4_CONCENTRATION_ARRAZI,.115) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 0.115
BOILER_FG_NC5_CONCENTRATION | BOILER FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC5_CONCENTRATION_ARRAZI,.001) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 0.001
BOILER_FG_PROPANE_CONCENTRATION | BOILER FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_PROPANE_CONCENTRATION_ARRAZI,.343) | NOT COMPUTED |  | Missing inputs (not in hierarchy): ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS | 0.343
BOILER_LHV | BOILER LHV | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | Kcal/Kg | (BOILER_A_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_A_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_A_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_A_FG_ETHYLENE_MASS_FRACTION*LHV_C2H4_ETHYLENE+BOILER_A_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_A_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPAN | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION (+4 more) | BOILER_A_FG_CH4_MASS_FRACTION; BOILER_A_FG_ETHANE_MASS_FRACTION; BOILER_A_FG_ETHYLENE_MASS_FRACTION; BOILER_A_FG_HYDROGEN_MASS_FRACTION; BOILER_A_FG_IC4_MASS_FRACTION; BOILER_A_FG_IC5_MASS_FRACTION; BOILER_A_FG_NC4_MASS_FRACTION; BOILER_A_FG_NC5_MASS_FRACTION; BOILER_A_FG_NITROGEN_MASS_FRACTION; BOILER_A_FG_PROPANE_MASS_FRACTION | 9984.6019
BOILER_OVERALL_EFFICIENCY | BOILER OVERALL EFFICIENCY | LBM_preprocessing_inferred_tags_main | % | (BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_BOILER_INDIRECT_EFFICIENCY*BOILER_A_STATUS+BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_BOILER_INDIRECT_EFFICIENCY*BOILER_B_STATUS+BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_BOILER_INDIRECT_EFFICIENCY*BOILER_C_STATUS+BOILER_D_TOTAL_STEAM_ENERGY*BOILER_D_BOILER_INDIRECT_EFFICI | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_BOILER_INDIRECT_EFFICIENCY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_BOILER_INDIRECT_EFFICIENCY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY (+9 more) | BOILER_A_BOILER_INDIRECT_EFFICIENCY; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_BOILER_INDIRECT_EFFICIENCY; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_BOILER_INDIRECT_EFFICIENCY; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_BOILER_INDIRECT_EFFICIENCY; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_BOILER_INDIRECT_EFFICIENCY; BOILER_E_TOTAL_STEAM_ENERGY; TOTAL_STEAM_ENERGY
Boiler_E_Nox_Emission | Boiler E Nox Emission | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | ng/J | if(BOILER_E_STATUS==0,0,BOILER_E_NOX*46/24.45*1000000*2.07/10000000*20.9/(20.9-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_NOX | BOILER_E_FLUE_GAS_OXGYGEN_NEW; BOILER_E_NOX | 0
Boiler_E_Nox_Emission_Actual_Value | Boiler E Nox Emission Actual Value | 362_DM_ | nan |  | NOT COMPUTED |  | No formula and no PI value available
Boiler_E_Nox_Emission_Forecast | Boiler E Nox Emission Forecast | 362_DM_ | ng/J |  | NOT COMPUTED |  | No formula and no PI value available
Boiler_E_Nox_Emission_Max_Forecast | Boiler E Nox Emission Max Forecast | 362_DM_ | ng/J |  | NOT COMPUTED |  | No formula and no PI value available
Boiler_E_Nox_Emission_Timestamp_Max_Forecast | Boiler E Nox Emission Timestamp Max Forecast | 362_DM_ | nan |  | NOT COMPUTED |  | No formula and no PI value available
CAPACITY_UTILIZATION_1 | CAPACITY UTILIZATION 1 | LBM_preprocessing_inferred_tags_main | % | [TOTAL_STEAM_PRODUCTION]/750000*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
COMBUSTION_AIR_TEMP | COMBUSTION AIR TEMP | LBM_preprocessing_inferred_tags_main | DEG C | ((BOILER_A_COMBUSTION_AIR_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_COMBUSTION_AIR_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_COMBUSTION_AIR_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_COMBUSTION_AIR_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_COMBUSTION_AIR_TEMP*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_COMBUSTION_AIR_TEMPERATURE; BOILER_A_STATUS; BOILER_B_COMBUSTION_AIR_TEMPERATURE; BOILER_B_STATUS; BOILER_C_COMBUSTION_AIR_TEMPERATURE (+4 more) | BOILERS_ONLINE; BOILER_A_COMBUSTION_AIR_TEMPERATURE; BOILER_A_STATUS; BOILER_B_COMBUSTION_AIR_TEMPERATURE; BOILER_B_STATUS; BOILER_C_COMBUSTION_AIR_TEMPERATURE; BOILER_C_STATUS; BOILER_D_COMBUSTION_AIR_TEMPERATURE; BOILER_D_STATUS; BOILER_E_COMBUSTION_AIR_TEMP
COMPONENT_BUTANE_MW | COMPONENT BUTANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 58.12 | COMPUTED | 58.12 |  |  | 58.12
COMPONENT_CO_MW | COMPONENT CO MW | LBM_preprocessing_inferred_tags_main | g/gmol | 28.01 | COMPUTED | 28.01 |  |  | 28.01
COMPONENT_ETHANE_MW | COMPONENT ETHANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 30.07 | COMPUTED | 30.07 |  |  | 30.07
COMPONENT_ETHYLENE_MW | COMPONENT ETHYLENE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 28.051 | COMPUTED | 28.051 |  |  | 28.051
COMPONENT_HYDROGEN_MW | COMPONENT HYDROGEN MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 2.016 | COMPUTED | 2.016 |  |  | 2.016
COMPONENT_METHANE_MW | COMPONENT METHANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 16.04 | COMPUTED | 16.04 |  |  | 16.04
COMPONENT_NITROGEN_MW | COMPONENT NITROGEN MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 28.016 | COMPUTED | 28.016 |  |  | 28.016
COMPONENT_PENTANE_MW | COMPONENT PENTANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 72.15 | COMPUTED | 72.15 |  |  | 72.15
COMPONENT_PROPANE_MW | COMPONENT PROPANE MW | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | g/gmol | 44.09 | COMPUTED | 44.09 |  |  | 44.09
Calc_capacity | CALC CAPACITY | LBM_preprocessing_inferred_tags_main,LBM_postprocessing_capacity_utilization_inferred,LBM_optimum_inferred_tags_main | MT/ HR | (DESUPERHEATER_OUTLET_STEAM_FLOW+DESUPERHEATER_B_OUTLET_STEAM_FLOW+DESUPERHEATER_C_OUTLET_STEAM_FLOW+DESUPERHEATER_D_OUTLET_STEAM_FLOW+DESUPERHEATER_E_OUTLET_STEAM_FLOW) | COMPUTED | 13739.292 |  |  | 13739.292
Capacity_Utilization | CAPACITY UTILIZATION | LBM_ | % |  | NOT COMPUTED |  | No formula and no PI value available
ENERGY_NUMBER | ENERGY NUMBER | TRG_compute_inferred_pre_pta | MMBTU/ HR | ((BOILER_A_FG_FLOW_RATE_actual*BOILER_A_MIXED_LHV_PER_KG_actual*1000)*BOILER_A_STATUS_actual+(BOILER_B_FG_FLOW_RATE_actual*BOILER_B_MIXED_LHV_PER_KG_actual*1000)*BOILER_B_STATUS_actual+(BOILER_C_FG_FLOW_RATE_actual*BOILER_C_MIXED_LHV_PER_KG_actual*1000)*BOILER_C_STATUS_actual+(BOILER_D_FG_FLOW_RATE_ | NOT COMPUTED |  | eval_error: name 'BOILER_A_FG_FLOW_RATE_actual' is not defined
ENVIRONMENT_NUMBER | ENVIRONMENT NUMBER | TRG_compute_inferred_pre_pta | MT/ HR | ([ENERGY_NUMBER_actual]/0.0468/1000)*2.75 | NOT COMPUTED |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
EQUIVALENT_FUEL | EQUIVALENT FUEL | TRG_compute_inferred_pre_pta | MT/ HR | [OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual]/0.0468/1000 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
EQUIVALENT_FUEL_DAY | EQUIVALENT FUEL DAY | TRG_compute_inferred_pre_pta | MT/ DAY | [EQUIVALENT_FUEL_actual]*24 | NOT COMPUTED |  | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
EXCESS_O2 | EXCESS O2 | LBM_preprocessing_inferred_tags_main | % | ((BOILER_A_FLUE_GAS_OXGYGEN*BOILER_A_STATUS)+(BOILER_B_FLUE_GAS_OXGYGEN*BOILER_B_STATUS)+(BOILER_C_FLUE_GAS_OXGYGEN*BOILER_C_STATUS)+(BOILER_D_FLUE_GAS_OXGYGEN*BOILER_D_STATUS)+(BOILER_E_FLUE_GAS_OXGYGEN_NEW*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_STATUS; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_STATUS; BOILER_C_FLUE_GAS_OXGYGEN (+4 more) | BOILERS_ONLINE; BOILER_A_FLUE_GAS_OXGYGEN; BOILER_A_STATUS; BOILER_B_FLUE_GAS_OXGYGEN; BOILER_B_STATUS; BOILER_C_FLUE_GAS_OXGYGEN; BOILER_C_STATUS; BOILER_D_FLUE_GAS_OXGYGEN; BOILER_D_STATUS; BOILER_E_FLUE_GAS_OXGYGEN_NEW
FIRE_DUTY | FIRE DUTY | LBM_preprocessing_inferred_tags_main | MMBTU/ DAY | ((BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG*1000)*BOILER_A_STATUS+(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG*1000)*BOILER_B_STATUS+(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG*1000)*BOILER_C_STATUS+(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG*1000)*BOILER_D_STATUS+(BOILER_E_FG_FL | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS; BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS; BOILER_C_MIXED_LHV_PER_KG (+4 more) | BOILER_A_MIXED_LHV_PER_KG; BOILER_A_STATUS; BOILER_B_FG_FLOW_RATE; BOILER_B_MIXED_LHV_PER_KG; BOILER_B_STATUS; BOILER_C_MIXED_LHV_PER_KG; BOILER_C_STATUS; BOILER_D_MIXED_LHV_PER_KG; BOILER_D_STATUS; BOILER_E_MIXED_LHV_PER_KG | 0
FLAG_BFW_QUALITY | FLAG BFW QUALITY | LBM_preprocessing_inferred_tags_main | % | if([BFW_OXYGEN]>7ll[BFW_SILICA]>20ll[BFW_SODIUM]>20[BFW_PH]>9.6ll[BFW_PH]<9.2ll[BFW_CONDUCTIVITY]>10,0,1) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BFW_CONDUCTIVITY; BFW_OXYGEN; BFW_PH; BFW_SILICA; BFW_SODIUM | BFW_CONDUCTIVITY; BFW_OXYGEN; BFW_PH; BFW_SILICA; BFW_SODIUM
FLAG_BFW_QUALITY_PTA | FLAG BFW QUALITY PTA | TRG_compute_pta | % |  | NOT COMPUTED |  | No formula and no PI value available
FLAG_QUALITY_RATE | FLAG QUALITY RATE | LBM_preprocessing_inferred_tags_main | % | if(([STEAM_TEMP]>390&&[STEAM_PRESS]>40),1,0) | NOT COMPUTED |  | Missing inputs (not in hierarchy): STEAM_PRESS; STEAM_TEMP | STEAM_PRESS; STEAM_TEMP
FLAG_QUALITY_RATE_PTA | FLAG QUALITY RATE PTA | TRG_compute_pta | % |  | NOT COMPUTED |  | No formula and no PI value available
LHV_BUTANE | LHV BUTANE | LBM_preprocessing_inferred_tags_main | MJ/KG | 45.689 | COMPUTED | 45.689 |  |  | 45.689
LHV_C2H4_ETHYLENE | LHV C2H4 ETHYLENE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 47.178 | COMPUTED | 47.178 |  |  | 47.178
LHV_C2H6_ETHANE | LHV C2H6 ETHANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 47.497 | COMPUTED | 47.497 |  |  | 47.497
LHV_C3H8_PROPANE | LHV C3H8 PROPANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 46.362 | COMPUTED | 46.362 |  |  | 46.362
LHV_CH4_METHANE | LHV CH4 METHANE | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 50.026 | COMPUTED | 50.026 |  |  | 50.026
LHV_CO | LHV CO | LBM_preprocessing_inferred_tags_main | MJ/KG | 10.105 | COMPUTED | 10.105 |  |  | 10.105
LHV_FG | LHV FG | LBM_preprocessing_inferred_tags_main | MJ/KG | 31316 | COMPUTED | 31316 |  |  | 31316
LHV_FG_E_DESIGN | LHV FG E | LBM_preprocessing_inferred_tags_main | - | 45108 | COMPUTED | 45108 |  |  | 45108
LHV_H2O_WATER | LHV H2O WATER | LBM_preprocessing_inferred_tags_main | MJ/KG | 0 | COMPUTED | 0 |  |  | 0
LHV_H2_HYDROGEN | LHV H2 HYDROGEN | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 120.004 | COMPUTED | 120.004 |  |  | 120.004
LHV_IC4 | LHV IC4 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.613 | COMPUTED | 45.613 |  |  | 45.613
LHV_IC5 | LHV IC5 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.241 | COMPUTED | 45.241 |  |  | 45.241
LHV_N2_NITROGEN | LHV N2 NITROGEN | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 0 | COMPUTED | 0 |  |  | 0
LHV_NC4 | LHV NC4 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.75 | COMPUTED | 45.75 |  |  | 45.75
LHV_NC5 | LHV NC5 | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MJ/KG | 45.36 | COMPUTED | 45.36 |  |  | 45.36
LHV_PENTANE | LHV PENTANE | LBM_preprocessing_inferred_tags_main | MJ/KG | 45.35 | COMPUTED | 45.35 |  |  | 45.35
NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | NORMALIZED BOILER A FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | 87.5988
NORMALIZED_BOILER_A_FG_CO2_CONCENTRATION | NORMALIZED BOILER A FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | 0
NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER A FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | 1.5699
NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER A FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER_A_FUEL_COMPOSITION_TOTAL | 0
NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER A FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | 0
NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | NORMALIZED BOILER A FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | 0.097056
NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | NORMALIZED BOILER A FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | 0.033019
NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | NORMALIZED BOILER A FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | 10.2419
NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | NORMALIZED BOILER A FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | 0.11507
NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | NORMALIZED BOILER A FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | 0.001001
NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER A FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | 0.3432
NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | NORMALIZED BOILER B FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | 87.5988
NORMALIZED_BOILER_B_FG_CO2_CONCENTRATION | NORMALIZED BOILER B FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | 0
NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER B FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | 1.5699
NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER B FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER_B_FUEL_COMPOSITION_TOTAL | 0
NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER B FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | 0
NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | NORMALIZED BOILER B FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | 0.097056
NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | NORMALIZED BOILER B FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | 0.033019
NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | NORMALIZED BOILER B FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | 10.2419
NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | NORMALIZED BOILER B FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | 0.11507
NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | NORMALIZED BOILER B FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | 0.001001
NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER B FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | 0.3432
NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | NORMALIZED BOILER C FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | 87.5988
NORMALIZED_BOILER_C_FG_CO2_CONCENTRATION | NORMALIZED BOILER C FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | 0
NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER C FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | 1.5699
NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER C FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER_C_FUEL_COMPOSITION_TOTAL | 0
NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER C FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | 0
NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | NORMALIZED BOILER C FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | 0.097056
NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | NORMALIZED BOILER C FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | 0.033019
NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | NORMALIZED BOILER C FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | 10.2419
NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | NORMALIZED BOILER C FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | 0.11507
NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | NORMALIZED BOILER C FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | 0.001001
NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER C FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | 0.3432
NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | NORMALIZED BOILER D FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | 87.5988
NORMALIZED_BOILER_D_FG_CO2_CONCENTRATION | NORMALIZED BOILER D FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | 0
NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER D FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | 1.5699
NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER D FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER_D_FUEL_COMPOSITION_TOTAL | 0
NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER D FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | 0
NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | NORMALIZED BOILER D FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | 0.097056
NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | NORMALIZED BOILER D FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | 0.033019
NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | NORMALIZED BOILER D FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | 10.2419
NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | NORMALIZED BOILER D FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | 0.11507
NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | NORMALIZED BOILER D FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | 0.001001
NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER D FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | 0.3432
NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | NORMALIZED BOILER E FG CH4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_CH4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CH4_CONCENTRATION | 87.5988
NORMALIZED_BOILER_E_FG_CO2_CONCENTRATION | NORMALIZED BOILER E FG CO2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_CO2_CONCENTRATION | 0
NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER E FG ETHANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_ETHANE_CONCENTRATION | 1.5699
NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER E FG ETHYLENE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER_E_FUEL_COMPOSITION_TOTAL | 0
NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER E FG HYDROGEN CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_HYDROGEN_CONCENTRATION | 0
NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | NORMALIZED BOILER E FG IC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC4_CONCENTRATION | 0.097056
NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | NORMALIZED BOILER E FG IC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_IC5_CONCENTRATION | 0.033019
NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | NORMALIZED BOILER E FG N2 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | BOILER_FG_N2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_N2_CONCENTRATION | 10.2419
NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | NORMALIZED BOILER E FG NC4 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC4_CONCENTRATION | 0.11507
NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | NORMALIZED BOILER E FG NC5 CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_NC5_CONCENTRATION | 0.001001
NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER E FG PROPANE CONCENTRATION | LBM_preprocessing_inferred_tags_main | MOLE% | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL; BOILER_FG_PROPANE_CONCENTRATION | 0.3432
NUMBER_OF_BOILERS_ONLINE | Number of boilers running | LBM_preprocessing_inferred_tags_main | nan | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS]) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
NUMBER_OF_BOILERS_OPTIMUM | Optimum number of boilers that can be run considering steam margin. | LBM_preprocessing_inferred_tags_main | nan | if([STEAM_MARGIN_NUMBER]>2.0,([NUMBER_OF_BOILERS_ONLINE]-1),[NUMBER_OF_BOILERS_ONLINE]) | NOT COMPUTED |  | Missing inputs (not in hierarchy): NUMBER_OF_BOILERS_ONLINE; STEAM_MARGIN_NUMBER | NUMBER_OF_BOILERS_ONLINE; STEAM_MARGIN_NUMBER
OVERALL_ENERGY_CONSUMPTION_DAY | OVERALL ENERGY CONSUMPTION DAY | TRG_compute_inferred_pre_pta | GJ/ DAY | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_DELTA | OVERALL ENERGY CONSUMPTION DAY DELTA | TRG_compute_inferred_pre_pta | GJ/ DAY | abs(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24)*TOTAL_STEAM_PRODUCTION_MT_DAY_actual | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_benchmark | OVERALL ENERGY CONSUMPTION DAY BENCHMARK | TRG_compute_inferred_pre_pta | GJ/ DAY | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark' is not defined
OVERALL_SUPERHEATED_STEAM_BFW_RATIO | OVERALL SUPERHEATED STEAM BFW RATIO | LBM_preprocessing_inferred_tags_main | [-] | (BOILER_A_SUPERHEATED_STEAM_BFW_RATIO+BOILER_B_SUPERHEATED_STEAM_BFW_RATIO+BOILER_C_SUPERHEATED_STEAM_BFW_RATIO+BOILER_D_SUPERHEATED_STEAM_BFW_RATIO+BOILER_E_SUPERHEATED_STEAM_BFW_RATIO)/5 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_SUPERHEATED_STEAM_BFW_RATIO; BOILER_B_SUPERHEATED_STEAM_BFW_RATIO; BOILER_C_SUPERHEATED_STEAM_BFW_RATIO; BOILER_D_SUPERHEATED_STEAM_BFW_RATIO; BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER_A_SUPERHEATED_STEAM_BFW_RATIO; BOILER_B_SUPERHEATED_STEAM_BFW_RATIO; BOILER_C_SUPERHEATED_STEAM_BFW_RATIO; BOILER_D_SUPERHEATED_STEAM_BFW_RATIO; BOILER_E_SUPERHEATED_STEAM_BFW_RATIO
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION | OVER ALL SPECIFIC ENERGY CONSUMPTION | LBM_preprocessing_inferred_tags_main | GJ/T | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_I | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY (+8 more) | BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_C_STATUS; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_D_STATUS; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_E_TOTAL_STEAM_ENERGY
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA | OVER ALL SPECIFIC ENERGY CONSUMPTION DELTA | TRG_compute_inferred_pre_pta | nan | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark<0,0,(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark)) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
QUALITY_RATE | QUALITY RATE | TRG_compute_inferred_post_pta | % | FLAG_QUALITY_RATE_PTA_actual*100/24 | NOT COMPUTED |  | eval_error: name 'FLAG_QUALITY_RATE_PTA_actual' is not defined
RELATIVE_HUMIDITY_CLEAN | RELATIVE HUMIDITY | LBM_preprocessing_inferred_tags_main | % | if((abs(RELATIVE_HUMIDITY)<1 && abs(RELATIVE_HUMIDITY)>0),abs(RELATIVE_HUMIDITY),0.6) | COMPUTED | 0.17 |  |  | 0.17
SPECIFIC_ENERGY_AVG | SPECIFIC ENERGY AVG | LBM_preprocessing_inferred_tags_main | KG/ KCAL | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_D_STATUS+BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_E_STATUS)/BOI | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ (+4 more) | BOILERS_ONLINE; BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_A_STATUS; BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_B_STATUS; BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_C_STATUS; BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ; BOILER_D_STATUS; BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ
STACK_TEMP | STACK TEMP | LBM_preprocessing_inferred_tags_main | DEG C | ((BOILER_A_STACK_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_STACK_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_STACK_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_STACK_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_STACK_TEMPERATURE*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
STEAM_MARGIN_NUMBER | Available steam margin divided by 150 | LBM_preprocessing_inferred_tags_main | nan | [STEAM_MARGIN_TPH]/150 | NOT COMPUTED |  | Missing inputs (not in hierarchy): STEAM_MARGIN_TPH | STEAM_MARGIN_TPH
STEAM_MARGIN_TPH | Steam margin available in running boilers in TPH | LBM_preprocessing_inferred_tags_main | TPH | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS])*150-[TOTAL_STEAM_PRODUCTION] | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; TOTAL_STEAM_PRODUCTION | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; TOTAL_STEAM_PRODUCTION
STEAM_PRESS | STEAM PRESS | LBM_preprocessing_inferred_tags_main | BARG | ((HP_STEAM_PRESSURE_FROM_DS*BOILER_A_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_B*BOILER_B_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_C*BOILER_C_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_D*BOILER_D_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_E*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; HP_STEAM_PRESSURE_FROM_DS (+3 more) | BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS; HP_STEAM_PRESSURE_FROM_DS; HP_STEAM_PRESSURE_FROM_DS_B; HP_STEAM_PRESSURE_FROM_DS_C; HP_STEAM_PRESSURE_FROM_DS_D
STEAM_TEMP | STEAM TEMP | LBM_preprocessing_inferred_tags_main | DEG C | (DESUPERHEATER_OUTLET_TEMPERATURE*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_TEMPERATURE*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_TEMPERATURE*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_TEMPERATURE*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_TEMPERATURE*BOILER_E_STATUS)/BOILERS_ONLINE | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILERS_ONLINE; BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS
TOTAL_BLOWDOWN_LOSS | TOTAL BLOWDOWN LOSS | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_BLOWDOWN_LOSS+BOILER_B_BLOWDOWN_LOSS+BOILER_C_BLOWDOWN_LOSS+BOILER_D_BLOWDOWN_LOSS+BOILER_E_BLOWDOWN_LOSS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_BLOWDOWN_LOSS; BOILER_B_BLOWDOWN_LOSS; BOILER_C_BLOWDOWN_LOSS; BOILER_D_BLOWDOWN_LOSS; BOILER_E_BLOWDOWN_LOSS | BOILER_A_BLOWDOWN_LOSS; BOILER_B_BLOWDOWN_LOSS; BOILER_C_BLOWDOWN_LOSS; BOILER_D_BLOWDOWN_LOSS; BOILER_E_BLOWDOWN_LOSS | 0
TOTAL_CO2_EMISSIONS | TOTAL CO2 EMISSIONS | LBM_preprocessing_inferred_tags_main | t/h | BOILER_A_CO2_EMISSIONS+BOILER_B_CO2_EMISSIONS+BOILER_C_CO2_EMISSIONS+BOILER_D_CO2_EMISSIONS+BOILER_E_CO2_EMISSIONS | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CO2_EMISSIONS; BOILER_B_CO2_EMISSIONS; BOILER_C_CO2_EMISSIONS; BOILER_D_CO2_EMISSIONS; BOILER_E_CO2_EMISSIONS | BOILER_A_CO2_EMISSIONS; BOILER_B_CO2_EMISSIONS; BOILER_C_CO2_EMISSIONS; BOILER_D_CO2_EMISSIONS; BOILER_E_CO2_EMISSIONS | 0
TOTAL_CO2_GAP | TOTAL CO2 GAP | TRG_compute_inferred_pre_pta | MMBTU/ DAY | [EQUIVALENT_FUEL_actual]*2.75*24 | NOT COMPUTED |  | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
TOTAL_ENERGY_GAP | TOTAL ENERGY GAP | TRG_compute_inferred_pre_pta | MT/ DAY | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
TOTAL_FUEL_COMPOSTION_MASS | TOTAL FUEL COMPOSTION MASS | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | % | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_A_FG_CH4_MASS_PERCENTAGE+BOILER_A_FG_ETHANE_MASS_PERCENTAGE+BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_A_FG_PROPANE_MASS_PERCENTAGE+BOILER_A_FG_NC4_MASS_PERCENTAGE+BOILER_A_FG_IC4_MASS_PERCENTAGE+BOILER_A_FG_NC5_MASS_PERCENTAGE+BOILER_A_FG_IC5_MASS_PERCEN | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_FG_CH4_MASS_PERCENTAGE; BOILER_A_FG_ETHANE_MASS_PERCENTAGE; BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_A_FG_IC4_MASS_PERCENTAGE; BOILER_A_FG_IC5_MASS_PERCENTAGE (+4 more) | BOILER_A_FG_CH4_MASS_PERCENTAGE; BOILER_A_FG_ETHANE_MASS_PERCENTAGE; BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE; BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE; BOILER_A_FG_IC4_MASS_PERCENTAGE; BOILER_A_FG_IC5_MASS_PERCENTAGE; BOILER_A_FG_NC4_MASS_PERCENTAGE; BOILER_A_FG_NC5_MASS_PERCENTAGE; BOILER_A_FG_NITROGEN_MASS_PERCENTAGE; BOILER_A_FG_PROPANE_MASS_PERCENTAGE | 100
TOTAL_FUEL_CONSUMPTION_GCAL_H | TOTAL FUEL CONSUMPTION GCAL H | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT; BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | 0
TOTAL_FUEL_FLOW | TOTAL FUEL FLOW | LBM_preprocessing_inferred_tags_main | Ton/h | (BOILER_A_FUEL_GAS_FLOW+BOILER_B_FUEL_GAS_FLOW+BOILER_C_FUEL_GAS_FLOW+BOILER_D_FUEL_GAS_FLOW+BOILER_E_FUEL_GAS_FLOW/1.295)/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_B_FUEL_GAS_FLOW | BOILER_B_FUEL_GAS_FLOW | 0.88188
TOTAL_FUEL_GAIN_LOSS | TOTAL FUEL GAIN LOSS | TRG_compute_inferred_pre_pta | MT/ DAY | BOILER_A_FUEL_GAIN_LOSS_actual+BOILER_B_FUEL_GAIN_LOSS_actual+BOILER_C_FUEL_GAIN_LOSS_actual+BOILER_D_FUEL_GAIN_LOSS_actual+BOILER_E_FUEL_GAIN_LOSS_actual | NOT COMPUTED |  | eval_error: name 'BOILER_A_FUEL_GAIN_LOSS_actual' is not defined
TOTAL_FUEL_TO_AIR_RATIO | TOTAL FUEL TO AIR RATIO | LBM_preprocessing_inferred_tags_main | Kg/ Kg Fuel | BOILER_A_AIR_FUEL_MASS_RATIO+BOILER_B_AIR_FUEL_MASS_RATIO+BOILER_C_AIR_FUEL_MASS_RATIO+BOILER_D_AIR_FUEL_MASS_RATIO+BOILER_E_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO; BOILER_B_AIR_FUEL_MASS_RATIO; BOILER_C_AIR_FUEL_MASS_RATIO; BOILER_D_AIR_FUEL_MASS_RATIO; BOILER_E_AIR_FUEL_MASS_RATIO | 72.66
TOTAL_STACK_LOSS_GCAL_H | TOTAL STACK LOSS GCAL/H | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_STACK_LOSS_CORRECTED+BOILER_B_STACK_LOSS_CORRECTED+BOILER_C_STACK_LOSS_CORRECTED+BOILER_D_STACK_LOSS_CORRECTED+BOILER_E_STACK_LOSS_CORRECTED | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STACK_LOSS_CORRECTED; BOILER_B_STACK_LOSS_CORRECTED; BOILER_C_STACK_LOSS_CORRECTED; BOILER_D_STACK_LOSS_CORRECTED; BOILER_E_STACK_LOSS_CORRECTED | BOILER_A_STACK_LOSS_CORRECTED; BOILER_B_STACK_LOSS_CORRECTED; BOILER_C_STACK_LOSS_CORRECTED; BOILER_D_STACK_LOSS_CORRECTED; BOILER_E_STACK_LOSS_CORRECTED | 0
TOTAL_STEAM_ENERGY | TOTAL STEAM ENERGY | LBM_preprocessing_inferred_tags_main | Gcal/h | BOILER_A_TOTAL_STEAM_ENERGY+BOILER_B_TOTAL_STEAM_ENERGY+BOILER_C_TOTAL_STEAM_ENERGY+BOILER_D_TOTAL_STEAM_ENERGY+BOILER_E_TOTAL_STEAM_ENERGY | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY | BOILER_A_TOTAL_STEAM_ENERGY; BOILER_B_TOTAL_STEAM_ENERGY; BOILER_C_TOTAL_STEAM_ENERGY; BOILER_D_TOTAL_STEAM_ENERGY; BOILER_E_TOTAL_STEAM_ENERGY | 0
TOTAL_STEAM_PRODUCTION | TOTAL STEAM PRODUCTION | LBM_preprocessing_inferred_tags_main | T/h | (DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_STATUS)/1000 | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | BOILER_A_STATUS; BOILER_B_STATUS; BOILER_C_STATUS; BOILER_D_STATUS | 0
TOTAL_STEAM_PRODUCTION_MT_DAY | TOTAL STEAM PRODUCTION IN MT PER DAY | LBM_preprocessing_inferred_tags_main | MT/ DAY | [TOTAL_STEAM_PRODUCTION]*24 | NOT COMPUTED |  | Missing inputs (not in hierarchy): TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
Timestamp | Timestamp | fixed,LBM_,362_DM_ | nan |  | NOT COMPUTED |  | No formula and no PI value available
VAPOUR_PRESSURE_OF_WATER | VAPOUR PRESSURE OF WATER | LBM_preprocessing_inferred_tags_main | mmhg | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631 |  |  | 4.631
index_energy | INDEX ENERGY | TRG_compute_inferred_pre_pta | % | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 | NOT COMPUTED |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
index_environment | INDEX ENVIRONMENT | TRG_compute_inferred_pre_pta | % | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 | NOT COMPUTED |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
index_process | INDEX PROCESS | TRG_compute_inferred_pre_pta | % | (TOTAL_STEAM_PRODUCTION_actual/(TOTAL_STEAM_PRODUCTION_actual+opportunity_production_actual/24))*100*0+100 | NOT COMPUTED |  | eval_error: name 'TOTAL_STEAM_PRODUCTION_actual' is not defined
opportunity_energy | OPPORTUNITY ENERGY | TRG_compute_inferred_pre_pta | MMBTU/ DAY | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
opportunity_environment | OPPORTUNITY ENVIRONMENT | TRG_compute_inferred_pre_pta | MT/ DAY | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[EQUIVALENT_FUEL_actual]*2.75*24) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
opportunity_production | OPPORTUNITY PRODUCTION | TRG_compute_inferred_pre_pta | MT/ DAY | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual])*24/([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark])*0 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
plant_status | plant status | LBM_preprocessing_inferred_tags_main | nan | if(BOILERS_ONLINE==0,0,1) | NOT COMPUTED |  | Missing inputs (not in hierarchy): BOILERS_ONLINE | BOILERS_ONLINE | 0