## Summary
Metric | Value
Hierarchy sensor IDs in _hierarchy_index.csv | 133
PEEO pi_tags total | 295
PI tags matched to hierarchy (seeds) | 35
Seeds with actual values | 35
──────────────────────────────────────── | ──────────
Total inferred tags evaluated | 929
Tags with formula | 921
Tags without formula | 8
──────────────────────────────────────── | ──────────
COMPUTED (value produced) | 85
NOT COMPUTED — total | 844
└─ Unknown/no sensor: ARRAZI_PLANT_STATUS | 10
└─ PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPE | 10
└─ PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPE | 10
└─ PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPE | 10
└─ PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPE | 10
└─ PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPE | 10
└─ No formula defined and no PI value | 8
└─ Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_E | 5
└─ Unknown/no sensor: BOILER_LHV | 5
└─ PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[senso | 5
└─ Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | 5
└─ Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | 5
└─ Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | 4
└─ Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILE | 3
└─ Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STAT | 3
└─ Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STAT | 3
└─ Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STAT | 3
└─ Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_FRACTION | 3
└─ Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG | 3
└─ eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actua | 3
└─ eval_error: name 'ENERGY_NUMBER_actual' is not defined | 3
└─ eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA | 3
└─ PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[se | 2
└─ PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_B[ | 2
└─ PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_C[ | 2
└─ PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_D[ | 2
└─ Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_ | 2
└─ PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMP | 2
└─ Unknown/no sensor: BOILER_A_STATUS | 2
└─ Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_M | 2
└─ Unknown/no sensor: BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STAT | 2
└─ Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERG | 2
└─ PI exists but NOT in hierarchy: BOILER_B_COMBUSTION_AIR_TEMP | 2
└─ Unknown/no sensor: BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LH | 2
└─ Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_M | 2
└─ Unknown/no sensor: BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STAT | 2
└─ Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERG | 2
└─ PI exists but NOT in hierarchy: BOILER_C_COMBUSTION_AIR_TEMP | 2
└─ Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_M | 2
└─ Unknown/no sensor: BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STAT | 2
└─ Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERG | 2
└─ PI exists but NOT in hierarchy: BOILER_D_COMBUSTION_AIR_TEMP | 2
└─ Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_M | 2
└─ Unknown/no sensor: BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STAT | 2
└─ Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERG | 2
└─ PI exists but NOT in hierarchy: BOILER_E_COMBUSTION_AIR_TEMP | 2
└─ Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_M | 2
└─ Unknown/no sensor: BOILER_E_FUEL_CONSUMPTION | 2
└─ Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERG | 2
└─ Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER | 2
└─ eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state | 2
└─ Unknown/no sensor: TOTAL_STEAM_PRODUCTION | 2
└─ eval_error: name 'EQUIVALENT_FUEL_actual' is not defined | 2
└─ Unknown/no sensor: BOILERS_ONLINE | 1
└─ PI exists but NOT in hierarchy: ARRAZI_PLANT_LOAD[sensor:AR. | 1
└─ Unknown/no sensor: ARRAZI_PLANT_LOAD_1 | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_C | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_E | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_E | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_P | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_N | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_H | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_I | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_N | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_N | 1
└─ Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_I | 1
└─ Unknown/no sensor: BOILER_A_FG_MW | 1
└─ Unknown/no sensor: BOILER_A_FG_DENSITY | 1
└─ Unknown/no sensor: BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ TOTAL_F | 1
└─ Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ TOTA | 1
└─ Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ TO | 1
└─ Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_PERCENTAGE ¦ TOT | 1
└─ Unknown/no sensor: BOILER_A_FG_NITROGEN_MASS_PERCENTAGE ¦ TO | 1
└─ Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ TO | 1
└─ Unknown/no sensor: BOILER_A_FG_IC4_MASS_PERCENTAGE ¦ TOTAL_F | 1
└─ Unknown/no sensor: BOILER_A_FG_NC4_MASS_PERCENTAGE ¦ TOTAL_F | 1
└─ Unknown/no sensor: BOILER_A_FG_NC5_MASS_PERCENTAGE ¦ TOTAL_F | 1
└─ Unknown/no sensor: BOILER_A_FG_IC5_MASS_PERCENTAGE ¦ TOTAL_F | 1
└─ Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1
└─ Unknown/no sensor: BOILER_A_CH4_CO2_COMBUSTION ¦ BOILER_A_ET | 1
└─ Unknown/no sensor: BOILER_A_CH4_N2_COMBUSTION ¦ BOILER_A_ETH | 1
└─ Unknown/no sensor: BOILER_A_CH4_H2O_COMBUSTION ¦ BOILER_A_ET | 1
└─ Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ PI exists but NOT in hierarchy: BOILER_A_FLUE_GAS_OXGYGEN[se | 1
└─ Unknown/no sensor: BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILE | 1
└─ Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_A_H2O_FORMED ¦ BOILER_A_TOTAL_MOIS | 1
└─ Unknown/no sensor: BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | 1
└─ Unknown/no sensor: BOILER_A_CP_CH4_FUEL_TEMP ¦ BOILER_A_CP_E | 1
└─ Unknown/no sensor: BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOI | 1
└─ Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_SENS | 1
└─ Unknown/no sensor: BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1
└─ Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_H2O_PER_ | 1
└─ Unknown/no sensor: BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1
└─ Unknown/no sensor: BOILER_A_RADIATION_LOSSES ¦ BOILER_A_STAT | 1
└─ Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_INP | 1
└─ Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_ABS | 1
└─ Unknown/no sensor: BOILER_A_HP_STEAM_ENTHALPY ¦ BOILER_A_STA | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_A_INLET_TEMPERATU | 1
└─ PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_A[ | 1
└─ Unknown/no sensor: BOILER_A_BFW_ENTHALPY ¦ BOILER_A_CORRECTE | 1
└─ PI exists but NOT in hierarchy: STEAM_DRUM_A_PRESSURE[sensor | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ Unknown/no sensor: BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_S | 1
└─ Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_BLOWDOWN_L | 1
└─ Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_CORRECTED_ | 1
└─ Unknown/no sensor: BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_CORRECT | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ PI exists but NOT in hierarchy: ECONIMIZER_A_OUTLET_TEMPERAT | 1
└─ Unknown/no sensor: BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_LMTD_ | 1
└─ Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_UA_ECONOMIZER | 1
└─ PI exists but NOT in hierarchy: DESUPERHEATER_TEMPERATURE[se | 1
└─ Unknown/no sensor: BOILER_A_SH_DUTY ¦ BOILER_A_STATUS | 1
└─ Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_S | 1
└─ Unknown/no sensor: BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_ | 1
└─ PI exists but NOT in hierarchy: BOILER_A_CBD_BD[sensor:UN.UO | 1
└─ Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_FUEL_GAS_C | 1
└─ Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_A_C | 1
└─ Unknown/no sensor: BOILER_A_SH_SPECIFIC_DUTY ¦ BOILER_A_STAT | 1
└─ Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_STATUS ¦ B | 1
└─ Unknown/no sensor: BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_SH_DU | 1
└─ Unknown/no sensor: BOILER_A_ENERGY_GAINED ¦ BOILER_A_RADIATI | 1
└─ Unknown/no sensor: BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_S | 1
└─ Unknown/no sensor: BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | 1
└─ Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_CORRE | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_C | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_E | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_E | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_P | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_N | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_H | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_I | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_N | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_N | 1
└─ Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_I | 1
└─ Unknown/no sensor: BOILER_B_FG_MW | 1
└─ Unknown/no sensor: BOILER_B_FG_DENSITY | 1
└─ Unknown/no sensor: BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_PERCENTAGE ¦ BOI | 1
└─ Unknown/no sensor: BOILER_B_FG_NITROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_B_FG_IC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FG_NC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FG_NC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FG_IC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_ | 1
└─ Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1
└─ Unknown/no sensor: BOILER_B_CH4_CO2_COMBUSTION ¦ BOILER_B_ET | 1
└─ Unknown/no sensor: BOILER_B_CH4_N2_COMBUSTION ¦ BOILER_B_ETH | 1
└─ Unknown/no sensor: BOILER_B_CH4_H2O_COMBUSTION ¦ BOILER_B_ET | 1
└─ Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ PI exists but NOT in hierarchy: BOILER_B_FLUE_GAS_OXGYGEN[se | 1
└─ Unknown/no sensor: BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILE | 1
└─ Unknown/no sensor: BOILER_B_AIR_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_B_H2O_FORMED ¦ BOILER_B_TOTAL_MOIS | 1
└─ Unknown/no sensor: BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | 1
└─ Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_ | 1
└─ Unknown/no sensor: BOILER_B_CP_CH4_FUEL_TEMP ¦ BOILER_B_CP_E | 1
└─ Unknown/no sensor: BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOI | 1
└─ Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_SENS | 1
└─ Unknown/no sensor: BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1
└─ Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_H2O_PER_ | 1
└─ Unknown/no sensor: BOILER_B_STATUS | 1
└─ Unknown/no sensor: BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1
└─ Unknown/no sensor: BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STAT | 1
└─ Unknown/no sensor: BOILER_B_RADIATION_LOSSES ¦ BOILER_B_STAT | 1
└─ Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_INP | 1
└─ Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_ABS | 1
└─ Unknown/no sensor: BOILER_B_HP_STEAM_ENTHALPY ¦ BOILER_B_STA | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_B_INLET_TEMPERATU | 1
└─ PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_B[ | 1
└─ Unknown/no sensor: BOILER_B_BFW_ENTHALPY ¦ BOILER_B_CORRECTE | 1
└─ PI exists but NOT in hierarchy: BOILER_B_STEAM_DRUM_PRESSURE | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_CORRECTED_ | 1
└─ Unknown/no sensor: BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_CORRECT | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_B_INLET_TEMPERATU | 1
└─ Unknown/no sensor: BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_LMTD_ | 1
└─ Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_UA_ECONOMIZER | 1
└─ PI exists but NOT in hierarchy: BOILER_B_STEAM_DRUM_PRESSURE | 1
└─ Unknown/no sensor: BOILER_B_SH_DUTY ¦ BOILER_B_STATUS | 1
└─ Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_S | 1
└─ Unknown/no sensor: BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_ | 1
└─ PI exists but NOT in hierarchy: CBD_BLOW_DOWN_B[sensor:UN.UO | 1
└─ Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_FUEL_GAS_C | 1
└─ Unknown/no sensor: BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_B_C | 1
└─ Unknown/no sensor: BOILER_B_SH_SPECIFIC_DUTY ¦ BOILER_B_STAT | 1
└─ Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_STATUS ¦ B | 1
└─ Unknown/no sensor: BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_SH_DU | 1
└─ Unknown/no sensor: BOILER_B_ENERGY_GAINED ¦ BOILER_B_RADIATI | 1
└─ Unknown/no sensor: BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_S | 1
└─ Unknown/no sensor: BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | 1
└─ Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_CORRE | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_C | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_E | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_E | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_P | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_N | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_H | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_I | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_N | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_N | 1
└─ Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_I | 1
└─ Unknown/no sensor: BOILER_C_FG_MW | 1
└─ Unknown/no sensor: BOILER_C_FG_DENSITY | 1
└─ Unknown/no sensor: BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_PERCENTAGE ¦ BOI | 1
└─ Unknown/no sensor: BOILER_C_FG_NITROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_C_FG_IC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FG_NC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FG_NC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FG_IC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_ | 1
└─ Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1
└─ Unknown/no sensor: BOILER_C_CH4_CO2_COMBUSTION ¦ BOILER_C_ET | 1
└─ Unknown/no sensor: BOILER_C_CH4_N2_COMBUSTION ¦ BOILER_C_ETH | 1
└─ Unknown/no sensor: BOILER_C_CH4_H2O_COMBUSTION ¦ BOILER_C_ET | 1
└─ Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ PI exists but NOT in hierarchy: BOILER_C_FLUE_GAS_OXGYGEN[se | 1
└─ Unknown/no sensor: BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILE | 1
└─ Unknown/no sensor: BOILER_C_AIR_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_C_H2O_FORMED ¦ BOILER_C_TOTAL_MOIS | 1
└─ Unknown/no sensor: BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | 1
└─ Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_ | 1
└─ Unknown/no sensor: BOILER_C_CP_CH4_FUEL_TEMP ¦ BOILER_C_CP_E | 1
└─ Unknown/no sensor: BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOI | 1
└─ Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_SENS | 1
└─ Unknown/no sensor: BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1
└─ Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_H2O_PER_ | 1
└─ Unknown/no sensor: BOILER_C_STATUS | 1
└─ Unknown/no sensor: BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1
└─ Unknown/no sensor: BOILER_C_RADIATION_LOSSES ¦ BOILER_C_STAT | 1
└─ Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_INP | 1
└─ Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_ABS | 1
└─ Unknown/no sensor: BOILER_C_HP_STEAM_ENTHALPY ¦ BOILER_C_STA | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_C_INLET_TEMPERATU | 1
└─ PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_C[ | 1
└─ Unknown/no sensor: BOILER_C_BFW_ENTHALPY ¦ BOILER_C_CORRECTE | 1
└─ PI exists but NOT in hierarchy: BOILER_C_STEAM_DRUM_PRESSURE | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ Unknown/no sensor: BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_S | 1
└─ Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_BLOWDOWN_L | 1
└─ Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_CORRECTED_ | 1
└─ Unknown/no sensor: BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_CORRECT | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_C_INLET_TEMPERATU | 1
└─ Unknown/no sensor: BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_LMTD_ | 1
└─ Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_UA_ECONOMIZER | 1
└─ PI exists but NOT in hierarchy: BOILER_C_STEAM_DRUM_PRESSURE | 1
└─ Unknown/no sensor: BOILER_C_SH_DUTY ¦ BOILER_C_STATUS | 1
└─ Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_S | 1
└─ Unknown/no sensor: BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_ | 1
└─ PI exists but NOT in hierarchy: CBD_BLOW_DOWN_C[sensor:UN.UO | 1
└─ Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_FUEL_GAS_C | 1
└─ Unknown/no sensor: BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_C_C | 1
└─ Unknown/no sensor: BOILER_C_SH_SPECIFIC_DUTY ¦ BOILER_C_STAT | 1
└─ Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_STATUS ¦ B | 1
└─ Unknown/no sensor: BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_SH_DU | 1
└─ Unknown/no sensor: BOILER_C_ENERGY_GAINED ¦ BOILER_C_RADIATI | 1
└─ Unknown/no sensor: BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_S | 1
└─ Unknown/no sensor: BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | 1
└─ Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_CORRE | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_C | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_E | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_E | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_P | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_N | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_H | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_I | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_N | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_N | 1
└─ Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_I | 1
└─ Unknown/no sensor: BOILER_D_FG_MW | 1
└─ Unknown/no sensor: BOILER_D_FG_DENSITY | 1
└─ Unknown/no sensor: BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_PERCENTAGE ¦ BOI | 1
└─ Unknown/no sensor: BOILER_D_FG_NITROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_D_FG_IC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FG_NC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FG_NC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FG_IC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_ | 1
└─ Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1
└─ Unknown/no sensor: BOILER_D_CH4_CO2_COMBUSTION ¦ BOILER_D_ET | 1
└─ Unknown/no sensor: BOILER_D_CH4_N2_COMBUSTION ¦ BOILER_D_ETH | 1
└─ Unknown/no sensor: BOILER_D_CH4_H2O_COMBUSTION ¦ BOILER_D_ET | 1
└─ Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ PI exists but NOT in hierarchy: BOILER_D_FLUE_GAS_OXGYGEN[se | 1
└─ Unknown/no sensor: BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILE | 1
└─ Unknown/no sensor: BOILER_D_AIR_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_D_H2O_FORMED ¦ BOILER_D_TOTAL_MOIS | 1
└─ Unknown/no sensor: BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | 1
└─ Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_ | 1
└─ Unknown/no sensor: BOILER_D_CP_CH4_FUEL_TEMP ¦ BOILER_D_CP_E | 1
└─ Unknown/no sensor: BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOI | 1
└─ Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_SENS | 1
└─ Unknown/no sensor: BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1
└─ Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_H2O_PER_ | 1
└─ Unknown/no sensor: BOILER_D_STATUS | 1
└─ Unknown/no sensor: BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1
└─ Unknown/no sensor: BOILER_D_RADIATION_LOSSES ¦ BOILER_D_STAT | 1
└─ Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_INP | 1
└─ Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_ABS | 1
└─ Unknown/no sensor: BOILER_D_HP_STEAM_ENTHALPY ¦ BOILER_D_STA | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_D_INLET_TEMPERATU | 1
└─ PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_D[ | 1
└─ Unknown/no sensor: BOILER_D_BFW_ENTHALPY ¦ BOILER_D_CORRECTE | 1
└─ PI exists but NOT in hierarchy: BOILER_D_STEAM_DRUM_PRESSURE | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ Unknown/no sensor: BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_S | 1
└─ Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_BLOWDOWN_L | 1
└─ Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_CORRECTED_ | 1
└─ Unknown/no sensor: BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_CORRECT | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_D_INLET_TEMPERATU | 1
└─ Unknown/no sensor: BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_LMTD_ | 1
└─ Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_UA_ECONOMIZER | 1
└─ PI exists but NOT in hierarchy: BOILER_D_STEAM_DRUM_PRESSURE | 1
└─ Unknown/no sensor: BOILER_D_SH_DUTY ¦ BOILER_D_STATUS | 1
└─ Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_S | 1
└─ Unknown/no sensor: BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_ | 1
└─ PI exists but NOT in hierarchy: CBD_BLOW_DOWN_D[sensor:UN.UO | 1
└─ Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_FUEL_GAS_C | 1
└─ Unknown/no sensor: BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_D_C | 1
└─ Unknown/no sensor: BOILER_D_SH_SPECIFIC_DUTY ¦ BOILER_D_STAT | 1
└─ Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_STATUS ¦ B | 1
└─ Unknown/no sensor: BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_SH_DU | 1
└─ Unknown/no sensor: BOILER_D_ENERGY_GAINED ¦ BOILER_D_RADIATI | 1
└─ Unknown/no sensor: BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_S | 1
└─ Unknown/no sensor: BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | 1
└─ Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_CORRE | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_ | 1
└─ Unknown/no sensor: NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_C | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_E | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_E | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_P | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_N | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_H | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_I | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_N | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_N | 1
└─ Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_I | 1
└─ Unknown/no sensor: BOILER_E_FG_MW | 1
└─ Unknown/no sensor: BOILER_E_FG_DENSITY | 1
└─ Unknown/no sensor: BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOIL | 1
└─ Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_PERCENTAGE ¦ BOI | 1
└─ Unknown/no sensor: BOILER_E_FG_NITROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BO | 1
└─ Unknown/no sensor: BOILER_E_FG_IC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FG_NC4_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FG_NC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FG_IC5_MASS_PERCENTAGE ¦ BOILER_ | 1
└─ Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_ | 1
└─ Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1
└─ Unknown/no sensor: BOILER_E_CH4_CO2_COMBUSTION ¦ BOILER_E_ET | 1
└─ Unknown/no sensor: BOILER_E_CH4_N2_COMBUSTION ¦ BOILER_E_ETH | 1
└─ Unknown/no sensor: BOILER_E_CH4_H2O_COMBUSTION ¦ BOILER_E_ET | 1
└─ Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUS | 1
└─ PI exists but NOT in hierarchy: BOILER_E_FLUE_GAS_OXGYGEN_NE | 1
└─ Unknown/no sensor: BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILE | 1
└─ Unknown/no sensor: BOILER_E_AIR_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_E_H2O_FORMED ¦ BOILER_E_TOTAL_MOIS | 1
└─ Unknown/no sensor: BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | 1
└─ Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_ | 1
└─ Unknown/no sensor: BOILER_E_CP_CH4_FUEL_TEMP ¦ BOILER_E_CP_E | 1
└─ Unknown/no sensor: BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOI | 1
└─ Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR | 1
└─ Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG ¦ BOILER_E_SENS | 1
└─ Unknown/no sensor: BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1
└─ Unknown/no sensor: BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | 1
└─ Unknown/no sensor: BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1
└─ Unknown/no sensor: BOILER_E_RADIATION_LOSSES ¦ BOILER_E_TOTA | 1
└─ Unknown/no sensor: BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | 1
└─ Unknown/no sensor: BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FU | 1
└─ Unknown/no sensor: BOILER_E_HP_STEAM_ENTHALPY | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_E_INLET_TEMPERATU | 1
└─ PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_E[ | 1
└─ Unknown/no sensor: BOILER_E_BFW_ENTHALPY ¦ BOILER_E_CORRECTE | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ Unknown/no sensor: BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | 1
└─ Unknown/no sensor: BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_F | 1
└─ Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_BLOWDOWN_L | 1
└─ Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_CORRECTED_ | 1
└─ Unknown/no sensor: BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_CORRECT | 1
└─ PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[senso | 1
└─ PI exists but NOT in hierarchy: ECONOMIZER_E_INLET_TEMPERATU | 1
└─ Unknown/no sensor: BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_LMTD_ | 1
└─ Unknown/no sensor: BOILER_E_UA_ECONOMIZER | 1
└─ Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW | 1
└─ Unknown/no sensor: BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ B | 1
└─ Unknown/no sensor: BOILER_E_FUEL_GAS_CORRECTED_TPH ¦ BOILER_ | 1
└─ PI exists but NOT in hierarchy: CBD_BLOW_DOWN_E[sensor:UN.UO | 1
└─ Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_FUEL_GAS_C | 1
└─ Unknown/no sensor: BOILER_E_AIR_FUEL_MASS_RATIO ¦ BOILER_E_C | 1
└─ Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_TOTAL_STEA | 1
└─ Unknown/no sensor: BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_STACK | 1
└─ Unknown/no sensor: BOILER_E_ENERGY_GAINED ¦ BOILER_E_RADIATI | 1
└─ Unknown/no sensor: BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_S | 1
└─ Unknown/no sensor: BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | 1
└─ Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_CORRE | 1
└─ Unknown/no sensor: BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_G | 1
└─ Unknown/no sensor: BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_TO | 1
└─ Unknown/no sensor: BOILER_A_BOILER_INDIRECT_EFFICIENCY ¦ BOI | 1
└─ Unknown/no sensor: BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | 1
└─ Unknown/no sensor: BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_B_ | 1
└─ Unknown/no sensor: BOILER_A_BLOWDOWN_LOSS ¦ BOILER_B_BLOWDOW | 1
└─ Unknown/no sensor: BOILER_A_SUPERHEATED_STEAM_BFW_RATIO ¦ BO | 1
└─ Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_B_A | 1
└─ Unknown/no sensor: BOILER_A_CO2_EMISSIONS ¦ BOILER_B_CO2_EMI | 1
└─ PI exists but NOT in hierarchy: BOILER_A_FLUE_GAS_OXGYGEN[se | 1
└─ PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[se | 1
└─ PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMP | 1
└─ PI exists but NOT in hierarchy: BOILER_A_CONDUCTIVITY[sensor | 1
└─ Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_SPECIFIC_ENERGY | 1
└─ Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STAT | 1
└─ eval_error: name 'BOILER_A_FG_FLOW_RATE_actual' is not defin | 1
└─ eval_error: name 'TOTAL_STEAM_PRODUCTION_actual' is not defi | 1
└─ eval_error: name 'BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 1
└─ eval_error: name 'BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 1
└─ eval_error: name 'BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 1
└─ eval_error: name 'BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 1
└─ eval_error: name 'BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 1
└─ eval_error: name 'BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual' is | 1
└─ eval_error: name 'BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual' is | 1
└─ eval_error: name 'BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual' is | 1
└─ eval_error: name 'BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual' is | 1
└─ eval_error: name 'BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual' is | 1
└─ eval_error: name 'BOILER_A_FUEL_GAIN_LOSS_actual' is not def | 1
└─ Unknown/no sensor: STEAM_PRESS ¦ STEAM_TEMP | 1
└─ eval_error: name 'FLAG_QUALITY_RATE_PTA_actual' is not defin | 1
└─ eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_bench | 1
└─ PI exists but NOT in hierarchy: BOILER_E_FLUE_GAS_OXGYGEN_NE | 1
└─ Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILE | 1
└─ Unknown/no sensor: STEAM_MARGIN_TPH | 1
└─ Unknown/no sensor: NUMBER_OF_BOILERS_ONLINE ¦ STEAM_MARGIN_N | 1
└─ PI exists but NOT in hierarchy: BFW_CONDUCTIVITY[sensor:UN.U | 1
└─ eval_error: name 'FLAG_BFW_QUALITY_PTA_actual' is not define | 1
──────────────────────────────────────── | ──────────
Coverage % | 9.1%

## Computed
tag_name | description | uom | category | formula | value
BOILER_E_STEAM_DRUM_PRESSURE | BOILER E STEAM DRUM PRESSURE | nan | LBM_preprocessing_inferred_tags_main | if(HP_STEAM_PRESSURE_FROM_DS_E==MISSING_NUMERIC,0,HP_STEAM_PRESSURE_FROM_DS_E) | 1.884
LHV_H2_HYDROGEN | LHV H2 HYDROGEN | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 120.004 | 120.004
LHV_CH4_METHANE | LHV CH4 METHANE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 50.026 | 50.026
LHV_H2O_WATER | LHV H2O WATER | MJ/KG | LBM_preprocessing_inferred_tags_main | 0 | 0
LHV_N2_NITROGEN | LHV N2 NITROGEN | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 0 | 0
LHV_C2H4_ETHYLENE | LHV C2H4 ETHYLENE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 47.178 | 47.178
LHV_C2H6_ETHANE | LHV C2H6 ETHANE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 47.497 | 47.497
LHV_C3H8_PROPANE | LHV C3H8 PROPANE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 46.362 | 46.362
LHV_BUTANE | LHV BUTANE | MJ/KG | LBM_preprocessing_inferred_tags_main | 45.689 | 45.689
LHV_CO | LHV CO | MJ/KG | LBM_preprocessing_inferred_tags_main | 10.105 | 10.105
LHV_PENTANE | LHV PENTANE | MJ/KG | LBM_preprocessing_inferred_tags_main | 45.35 | 45.35
LHV_NC4 | LHV NC4 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.75 | 45.75
LHV_IC4 | LHV IC4 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.613 | 45.613
LHV_NC5 | LHV NC5 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.36 | 45.36
LHV_IC5 | LHV IC5 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.241 | 45.241
LHV_FG | LHV FG | MJ/KG | LBM_preprocessing_inferred_tags_main | 31316 | 31316
LHV_FG_E_DESIGN | LHV FG E | - | LBM_preprocessing_inferred_tags_main | 45108 | 45108
COMPONENT_HYDROGEN_MW | COMPONENT HYDROGEN MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 2.016 | 2.016
COMPONENT_NITROGEN_MW | COMPONENT NITROGEN MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 28.016 | 28.016
COMPONENT_CO_MW | COMPONENT CO MW | g/gmol | LBM_preprocessing_inferred_tags_main | 28.01 | 28.01
COMPONENT_METHANE_MW | COMPONENT METHANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 16.04 | 16.04
COMPONENT_ETHANE_MW | COMPONENT ETHANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 30.07 | 30.07
COMPONENT_PROPANE_MW | COMPONENT PROPANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 44.09 | 44.09
COMPONENT_ETHYLENE_MW | COMPONENT ETHYLENE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 28.051 | 28.051
COMPONENT_PENTANE_MW | COMPONENT PENTANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 72.15 | 72.15
COMPONENT_BUTANE_MW | COMPONENT BUTANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 58.12 | 58.12
BOILER_A_AIR_CP_REF_T | BOILER A AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | 6.96
BOILER_B_AIR_CP_REF_T | BOILER B AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | 6.96
BOILER_C_AIR_CP_REF_T | BOILER C AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | 6.96
BOILER_D_AIR_CP_REF_T | BOILER D AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | 6.96
BOILER_E_AIR_CP_REF_T | BOILER E AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | 6.96
RELATIVE_HUMIDITY_CLEAN | RELATIVE HUMIDITY | % | LBM_preprocessing_inferred_tags_main | if((abs(RELATIVE_HUMIDITY)<1 && abs(RELATIVE_HUMIDITY)>0),abs(RELATIVE_HUMIDITY),0.6) | 0.17
BOILER_A_BOILER_LOAD | BOILER A BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_OUTLET_STEAM_FLOW/150000*100 | 1.7975
BOILER_B_BOILER_LOAD | BOILER B BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_B_OUTLET_STEAM_FLOW/150000*100 | 1.8401
BOILER_C_BOILER_LOAD | BOILER C BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_C_OUTLET_STEAM_FLOW/150000*100 | 1.7993
BOILER_D_BOILER_LOAD | BOILER D BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_D_OUTLET_STEAM_FLOW/150000*100 | 1.8534
BOILER_E_BOILER_LOAD | BOILER E BOILER LOAD | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | DESUPERHEATER_E_OUTLET_STEAM_FLOW/150000*100 | 1.8692
BOILER_E_STATUS | BOILER E STATUS | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(BOILER_E_BOILER_LOAD>25&&DESUPERHEATER_E_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_E>40,1,0) | 0
BOILER_FG_ETHYLENE_CONCENTRATION | BOILER FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 0 | 0
BOILER_A_FG_FLOW_RATE | BOILER A FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_A_FUEL_GAS_FLOW/1000 | 0.17548
BOILER_A_VAPOUR_PRESSURE_OF_H2O | BOILER A VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_A_AIR_MOISTURE | BOILER A AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_A_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_A_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_A_CP_OF_AIR_AT_STACK_TEMP | BOILER A CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_A_STACK_TEMPERATURE+273.15 | 6.9676
BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER A CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6499
BOILER_A_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER A CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER A CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_A_CP_OF_H2O_AT_STACK_TEMP | BOILER A CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_B_VAPOUR_PRESSURE_OF_H2O | BOILER B VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_B_AIR_MOISTURE | BOILER B AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_B_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_B_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_B_CP_OF_AIR_AT_STACK_TEMP | BOILER B CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_B_STACK_TEMPERATURE+273.15 | 6.9675
BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER B CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6497
BOILER_B_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER B CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER B CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_B_CP_OF_H2O_AT_STACK_TEMP | BOILER B CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_C_FG_FLOW_RATE | BOILER C FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_C_FUEL_GAS_FLOW/1000 | 0.1755
BOILER_C_VAPOUR_PRESSURE_OF_H2O | BOILER C VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_C_AIR_MOISTURE | BOILER C AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_C_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_C_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_C_CP_OF_AIR_AT_STACK_TEMP | BOILER C CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_C_STACK_TEMPERATURE+273.15 | 6.9676
BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER C CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6502
BOILER_C_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER C CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2) | 8.3662
BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER C CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_C_CP_OF_H2O_AT_STACK_TEMP | BOILER C CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_D_FG_FLOW_RATE | BOILER D FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_D_FUEL_GAS_FLOW/1000 | 0.17549
BOILER_D_VAPOUR_PRESSURE_OF_H2O | BOILER D VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_D_AIR_MOISTURE | BOILER D AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_D_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_D_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_D_CP_OF_AIR_AT_STACK_TEMP | BOILER D CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_D_STACK_TEMPERATURE+273.15 | 6.9675
BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER D CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6481
BOILER_D_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER D CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2) | 8.3661
BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER D CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9586
BOILER_D_CP_OF_H2O_AT_STACK_TEMP | BOILER D CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.4644
BOILER_E_FG_FLOW_RATE | BOILER E FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_E_FUEL_GAS_FLOW/1.295/1000 | 0.17993
BOILER_E_VAPOUR_PRESSURE_OF_H2O | BOILER E VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
BOILER_E_AIR_MOISTURE | BOILER E AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_E_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_E_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | 0.000645
BOILER_E_CP_OF_AIR_AT_STACK_TEMP | BOILER E CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_E_STACK_TEMPERATURE+273.15 | 6.9677
BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER E CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 8.6572
BOILER_E_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER E CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2) | 8.3667
BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER E CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | 6.9587
BOILER_E_CP_OF_H2O_AT_STACK_TEMP | BOILER E CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2))/18.015 | 0.46443
BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER E HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,0*10^-6*28*5654*BOILER_E_BOILER_LOAD) | 0
BOILER_E_STEAM_DRUM_TEMP | BOILER E STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,4.02521999671835*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | 0
BOILER_E_SH_DUTY | BOILER E SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_E_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_E_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_E_STEAM_DRUM_TEMP*3.45877718874616+2082.10231045632))*0.239006/1000000) | 0
BOILER_E_SH_SPECIFIC_DUTY | BOILER E SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_SH_DUTY/DESUPERHEATER_E_OUTLET_STEAM_FLOW*1000) | 0
BOILER_E_SH_PERFORMANCE | BOILER E SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(BOILER_E_SH_SPECIFIC_DUTY)/0.110075721*100) | 0
VAPOUR_PRESSURE_OF_WATER | VAPOUR PRESSURE OF WATER | mmhg | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | 4.631
Calc_capacity | CALC CAPACITY | MT/ HR | LBM_preprocessing_inferred_tags_main,LBM_postprocessing_capacity_utilization_inferred,LBM_optimum_inferred_tags_main | (DESUPERHEATER_OUTLET_STEAM_FLOW+DESUPERHEATER_B_OUTLET_STEAM_FLOW+DESUPERHEATER_C_OUTLET_STEAM_FLOW+DESUPERHEATER_D_OUTLET_STEAM_FLOW+DESUPERHEATER_E_OUTLET_STEAM_FLOW) | 13739.292

## Not_Computed
tag_name | description | uom | category | formula | reason_if_not | missing_inputs
Timestamp | Timestamp | nan | fixed,LBM_,362_DM_ |  | No formula defined and no PI value
BOILER_A_STATUS | BOILER A STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_A_BOILER_LOAD>25&&DESUPERHEATER_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS>40,1,0) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] | HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV]
BOILER_B_STATUS | BOILER B STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_B_BOILER_LOAD>25&&DESUPERHEATER_B_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_B>40,1,0) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] | HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV]
BOILER_C_STATUS | BOILER C STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_C_BOILER_LOAD>25&&DESUPERHEATER_C_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_C>40,1,0) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] | HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV]
BOILER_D_STATUS | BOILER D STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_D_BOILER_LOAD>25&&DESUPERHEATER_D_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_D>40,1,0) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV] | HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV]
BOILERS_ONLINE | BOILERS ONLINE | - | LBM_preprocessing_inferred_tags_main | BOILER_A_STATUS+BOILER_B_STATUS+BOILER_C_STATUS+BOILER_D_STATUS+BOILER_E_STATUS | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
plant_status | plant status | nan | LBM_preprocessing_inferred_tags_main | if(BOILERS_ONLINE==0,0,1) | Unknown/no sensor: BOILERS_ONLINE | BOILERS_ONLINE
ARRAZI_PLANT_LOAD_1 | ARRAZI PLANT LOAD 1 | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_LOAD==MISSING_NUMERIC,0,ARRAZI_PLANT_LOAD) | PI exists but NOT in hierarchy: ARRAZI_PLANT_LOAD[sensor:AR.AR5.DCS.Process.REFLOAD5.CPV] | ARRAZI_PLANT_LOAD[sensor:AR.AR5.DCS.Process.REFLOAD5.CPV]
ARRAZI_PLANT_STATUS | ARRAZI PLANT STATUS | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_LOAD_1<70,0,1) | Unknown/no sensor: ARRAZI_PLANT_LOAD_1 | ARRAZI_PLANT_LOAD_1
BOILER_FG_N2_CONCENTRATION | BOILER FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_N2_CONCENTRATION_ARRAZI,10.236) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_CH4_CONCENTRATION | BOILER FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CH4_CONCENTRATION_ARRAZI,87.548) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_ETHANE_CONCENTRATION | BOILER FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_ETHANE_CONCENTRATION_ARRAZI,1.569) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_PROPANE_CONCENTRATION | BOILER FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_PROPANE_CONCENTRATION_ARRAZI,.343) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_NC4_CONCENTRATION | BOILER FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC4_CONCENTRATION_ARRAZI,.115) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_IC4_CONCENTRATION | BOILER FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC4_CONCENTRATION_ARRAZI,.097) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_CO2_CONCENTRATION | BOILER FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CO2_CONCENTRATION_ARRAZI,0) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_NC5_CONCENTRATION | BOILER FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC5_CONCENTRATION_ARRAZI,.001) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_IC5_CONCENTRATION | BOILER FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC5_CONCENTRATION_ARRAZI,.033) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_HYDROGEN_CONCENTRATION | BOILER FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,0,0) | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER A FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | NORMALIZED BOILER A FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_FG_CH4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER A FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER A FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL)*100 | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER_A_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER A FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_A_FG_CO2_CONCENTRATION | NORMALIZED BOILER A FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | NORMALIZED BOILER A FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | NORMALIZED BOILER A FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | NORMALIZED BOILER A FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | NORMALIZED BOILER A FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | NORMALIZED BOILER A FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_FG_N2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER A FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_A_FG_MW | BOILER A FG MW | G/MOL | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW+NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_A_F | Unknown/no sensor: NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION
BOILER_A_FG_CH4_MASS_PERCENTAGE | BOILER A FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION
BOILER_A_FG_ETHANE_MASS_PERCENTAGE | BOILER A FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION
BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE | BOILER A FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION
BOILER_A_FG_PROPANE_MASS_PERCENTAGE | BOILER A FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION
BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | BOILER A FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_N2_CONCENTRATION
BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE | BOILER A FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION
BOILER_A_FG_IC4_MASS_PERCENTAGE | BOILER A FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION
BOILER_A_FG_NC4_MASS_PERCENTAGE | BOILER A FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION
BOILER_A_FG_NC5_MASS_PERCENTAGE | BOILER A FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION
BOILER_A_FG_IC5_MASS_PERCENTAGE | BOILER A FG IC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION
BOILER_A_FG_DENSITY | BOILER A FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_MW/22.414 | Unknown/no sensor: BOILER_A_FG_MW | BOILER_A_FG_MW
BOILER_A_LHV_DESIGN | BOILER A LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_A_FG_DENSITY)/1000 | Unknown/no sensor: BOILER_A_FG_DENSITY | BOILER_A_FG_DENSITY
TOTAL_FUEL_COMPOSTION_MASS | TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_A_FG_CH4_MASS_PERCENTAGE+BOILER_A_FG_ETHANE_MASS_PERCENTAGE+BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_A_FG_PROPANE_MASS_PERCENTAGE+BOILER_A_FG_NC4_MASS_PERCENTAGE+BOILER_A_FG_IC4_MASS_PERCENTAGE+BOILER_A_FG_NC5_MASS_PERCENTAGE+BOILER_A_FG_IC5_MASS_PERCENTAGE+BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | Unknown/no sensor: BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_A_FG_IC4_MASS_PERCENTAGE | BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_A_FG_IC4_MASS_PERCENTAGE ¦ BOILER_A_FG_IC5_MASS_PERCENTAGE ¦ BOILER_A_FG_NC4_MASS_PERCENTAGE ¦ BOILER_A_FG_NC5_MASS_PERCENTAGE ¦ BOILER_A_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_A_FG_PROPANE_MASS_PERCENTAGE
BOILER_A_FG_CH4_MASS_FRACTION | BOILER A FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_CH4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER A FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_ETHANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER A FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER A FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_PROPANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_PROPANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NITROGEN_MASS_FRACTION | BOILER A FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_NITROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER A FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_IC4_MASS_FRACTION | BOILER A FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_IC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_IC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NC4_MASS_FRACTION | BOILER A FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_NC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_NC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NC5_MASS_FRACTION | BOILER A FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_NC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_NC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_IC5_MASS_FRACTION | BOILER A FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_IC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_A_FG_IC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_LHV | BOILER LHV | Kcal/Kg | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_A_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_A_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_A_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_A_FG_ETHYLENE_MASS_FRACTION*LHV_C2H4_ETHYLENE+BOILER_A_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_A_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_A_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_A_F | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION ¦ BOILER_A_FG_IC5_MASS_FRACTION ¦ BOILER_A_FG_NC4_MASS_FRACTION ¦ BOILER_A_FG_NC5_MASS_FRACTION ¦ BOILER_A_FG_NITROGEN_MASS_FRACTION ¦ BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER A AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*34.344 | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER A AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*17.265 | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*16.119 | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*14.807 | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER A AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*15.703 | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER A AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER A AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER A AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER A AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_H2_CO2_COMBUSTION | BOILER A H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*0 | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_CH4_CO2_COMBUSTION | BOILER A CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*2.744 | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_ETHANE_CO2_COMBUSTION | BOILER A ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*2.927 | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHYLENE_CO2_COMBUSTION | BOILER A ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*3.138 | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_PROPANE_CO2_COMBUSTION | BOILER A PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*2.994 | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_NC4_CO2_COMBUSTION | BOILER A NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_IC4_CO2_COMBUSTION | BOILER A IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_NC5_CO2_COMBUSTION | BOILER A NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_IC5_CO2_COMBUSTION | BOILER A IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_H2_N2_COMBUSTION | BOILER A H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*26.407 | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_CH4_N2_COMBUSTION | BOILER A CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*13.275 | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_ETHANE_N2_COMBUSTION | BOILER A ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*12.394 | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHYLENE_N2_COMBUSTION | BOILER A ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*11.385 | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_PROPANE_N2_COMBUSTION | BOILER A PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*12.074 | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_IC4_N2_COMBUSTION | BOILER A IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_NC4_N2_COMBUSTION | BOILER A NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_IC5_N2_COMBUSTION | BOILER A IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_NC5_N2_COMBUSTION | BOILER A NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_H2_H2O_COMBUSTION | BOILER A H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*8.937 | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_CH4_H2O_COMBUSTION | BOILER A CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*2.246 | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_ETHANE_H2O_COMBUSTION | BOILER A ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*1.798 | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHYLENE_H2O_COMBUSTION | BOILER A ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*1.285 | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_PROPANE_H2O_COMBUSTION | BOILER A PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*1.634 | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_IC4_H2O_COMBUSTION | BOILER A IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_NC4_H2O_COMBUSTION | BOILER A NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_IC5_H2O_COMBUSTION | BOILER A IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_NC5_H2O_COMBUSTION | BOILER A NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER A AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_A_AI | Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_A_CO2_FORMED | BOILER A CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_CH4_CO2_COMBUSTION+BOILER_A_ETHANE_CO2_COMBUSTION+BOILER_A_ETHYLENE_CO2_COMBUSTION+BOILER_A_PROPANE_CO2_COMBUSTION+BOILER_A_NC4_CO2_COMBUSTION+BOILER_A_IC4_CO2_COMBUSTION+BOILER_A_NC5_CO2_COMBUSTION+BOILER_A_IC5_CO2_COMBUSTION | Unknown/no sensor: BOILER_A_CH4_CO2_COMBUSTION ¦ BOILER_A_ETHANE_CO2_COMBUSTION ¦ BOILER_A_ETHYLENE_CO2_COMBUSTION ¦ BOILER_A_IC4_CO2_COMBUSTION ¦ BOILER_A_IC5_CO2_COMBUSTION | BOILER_A_CH4_CO2_COMBUSTION ¦ BOILER_A_ETHANE_CO2_COMBUSTION ¦ BOILER_A_ETHYLENE_CO2_COMBUSTION ¦ BOILER_A_IC4_CO2_COMBUSTION ¦ BOILER_A_IC5_CO2_COMBUSTION ¦ BOILER_A_NC4_CO2_COMBUSTION ¦ BOILER_A_NC5_CO2_COMBUSTION ¦ BOILER_A_PROPANE_CO2_COMBUSTION
BOILER_A_N2_FORMED | BOILER A N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_H2_N2_COMBUSTION+BOILER_A_CH4_N2_COMBUSTION+BOILER_A_ETHANE_N2_COMBUSTION+BOILER_A_ETHYLENE_N2_COMBUSTION+BOILER_A_PROPANE_N2_COMBUSTION+BOILER_A_IC4_N2_COMBUSTION+BOILER_A_NC4_N2_COMBUSTION+BOILER_A_IC5_N2_COMBUSTION+BOILER_A_NC5_N2_COMBUSTION | Unknown/no sensor: BOILER_A_CH4_N2_COMBUSTION ¦ BOILER_A_ETHANE_N2_COMBUSTION ¦ BOILER_A_ETHYLENE_N2_COMBUSTION ¦ BOILER_A_H2_N2_COMBUSTION ¦ BOILER_A_IC4_N2_COMBUSTION | BOILER_A_CH4_N2_COMBUSTION ¦ BOILER_A_ETHANE_N2_COMBUSTION ¦ BOILER_A_ETHYLENE_N2_COMBUSTION ¦ BOILER_A_H2_N2_COMBUSTION ¦ BOILER_A_IC4_N2_COMBUSTION ¦ BOILER_A_IC5_N2_COMBUSTION ¦ BOILER_A_NC4_N2_COMBUSTION ¦ BOILER_A_NC5_N2_COMBUSTION ¦ BOILER_A_PROPANE_N2_COMBUSTION
BOILER_A_H2O_FORMED | BOILER A H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_H2_H2O_COMBUSTION+BOILER_A_CH4_H2O_COMBUSTION+BOILER_A_ETHANE_H2O_COMBUSTION+BOILER_A_ETHYLENE_H2O_COMBUSTION+BOILER_A_PROPANE_H2O_COMBUSTION+BOILER_A_IC4_H2O_COMBUSTION+BOILER_A_NC4_H2O_COMBUSTION+BOILER_A_IC5_H2O_COMBUSTION+BOILER_A_NC5_H2O_COMBUSTION | Unknown/no sensor: BOILER_A_CH4_H2O_COMBUSTION ¦ BOILER_A_ETHANE_H2O_COMBUSTION ¦ BOILER_A_ETHYLENE_H2O_COMBUSTION ¦ BOILER_A_H2_H2O_COMBUSTION ¦ BOILER_A_IC4_H2O_COMBUSTION | BOILER_A_CH4_H2O_COMBUSTION ¦ BOILER_A_ETHANE_H2O_COMBUSTION ¦ BOILER_A_ETHYLENE_H2O_COMBUSTION ¦ BOILER_A_H2_H2O_COMBUSTION ¦ BOILER_A_IC4_H2O_COMBUSTION ¦ BOILER_A_IC5_H2O_COMBUSTION ¦ BOILER_A_NC4_H2O_COMBUSTION ¦ BOILER_A_NC5_H2O_COMBUSTION ¦ BOILER_A_PROPANE_H2O_COMBUSTION
BOILER_A_CORRECTED_COMBUSTION_AIR | BOILER A CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_A_AIR_MOISTURE) | Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_A_CORRECTED_COMBUTION_H2O_FORMED | BOILER A CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_H2O_FORMED+(BOILER_A_CORRECTED_COMBUSTION_AIR-BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_H2O_FORMED | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_H2O_FORMED
BOILER_A_EXCESS_AIR | BOILER A EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_A_FLUE_GAS_OXGYGEN)*((BOILER_A_N2_FORMED/28.01)+(BOILER_A_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_A_CO2_FORMED/44.01))/(20.95-BOILER_A_FLUE_GAS_OXGYGEN)) | PI exists but NOT in hierarchy: BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV]; Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_A_N2_FORMED | BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV] ¦ BOILER_A_CO2_FORMED ¦ BOILER_A_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_A_N2_FORMED
BOILER_A_AIR_FUEL_MASS_RATIO | BOILER A AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_EXCESS_AIR+BOILER_A_CORRECTED_COMBUSTION_AIR | Unknown/no sensor: BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_EXCESS_AIR | BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_EXCESS_AIR
BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER A TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_AIR_MOISTURE | Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO
BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER A TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_TOTAL_MOISTURE_WITH_AIR+BOILER_A_H2O_FORMED | Unknown/no sensor: BOILER_A_H2O_FORMED ¦ BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER_A_H2O_FORMED ¦ BOILER_A_TOTAL_MOISTURE_WITH_AIR
BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER A CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] | BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV]
BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER A AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_AIR_CP_REF_T+BOILER_A_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | Unknown/no sensor: BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER_A_CP_AT_COMBUSTION_TEMPERATURE
BOILER_A_CP_H2_FUEL_TEMP | BOILER A CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_CH4_FUEL_TEMP | BOILER A CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_ETHANE_FUEL_TEMP | BOILER A CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_PROPANE_FUEL_TEMP | BOILER A CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_ETHYLENE_FUEL_TEMP | BOILER A CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_NC4_FUEL_TEMP | BOILER A CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_IC4_FUEL_TEMP | BOILER A CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_NC5_FUEL_TEMP | BOILER A CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_IC5_FUEL_TEMP | BOILER A CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER A CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_A_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_A_FG_NC4_MASS_FRACTION/COMPONENT | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION ¦ BOILER_A_FG_IC5_MASS_FRACTION ¦ BOILER_A_FG_MW ¦ BOILER_A_FG_NC4_MASS_FRACTION ¦ BOILER_A_FG_NC5_MASS_FRACTION ¦ BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER A CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_A_CP_H2_FUEL_TEMP+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_A_CP_CH4_FUEL_TEMP+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_A_CP_ETHYLENE_FUEL_TEMP+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_A_CP_ETHANE_FUEL_TEMP+(BOILER_A_FG_P | Unknown/no sensor: BOILER_A_CP_CH4_FUEL_TEMP ¦ BOILER_A_CP_ETHANE_FUEL_TEMP ¦ BOILER_A_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_A_CP_H2_FUEL_TEMP ¦ BOILER_A_CP_IC4_FUEL_TEMP (+9 more) | BOILER_A_CP_CH4_FUEL_TEMP ¦ BOILER_A_CP_ETHANE_FUEL_TEMP ¦ BOILER_A_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_A_CP_H2_FUEL_TEMP ¦ BOILER_A_CP_IC4_FUEL_TEMP ¦ BOILER_A_CP_IC5_FUEL_TEMP ¦ BOILER_A_CP_NC4_FUEL_TEMP ¦ BOILER_A_CP_NC5_FUEL_TEMP ¦ BOILER_A_CP_PROPANE_FUEL_TEMP ¦ BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION ¦ BOILER_A_FG_IC5_MASS_FRACTION ¦ BOILER_A_FG_MW ¦ BOILER_A_FG_NC4_MASS_FRACTION ¦ BOILER_A_FG_NC5_MASS_FRACTION ¦ BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER A AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_A_FG_MW)/2 | Unknown/no sensor: BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_A_FG_MW | BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_A_FG_MW
BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_EXCESS_AIR*(1-BOILER_A_AIR_MOISTURE)+BOILER_A_N2_FORMED+BOILER_A_CO2_FORMED | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_N2_FORMED
BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | Unknown/no sensor: BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_FLUE_GAS_MW | BOILER A FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_A_CO2_FORMED/44.01+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.96) | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER A AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_A_CO2_FORMED/44.01+BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.85*BOILER_A_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_A_FLUE_GAS_MW)/BOILER_A_FLUE_GAS_MW | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_MW ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_MW ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED
BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER A SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]; Unknown/no sensor: BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] ¦ BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER A SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_A_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_A_AIR_FUEL_MASS_RATIO | PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV]; Unknown/no sensor: BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_A_AIR_FUEL_MASS_RATIO | BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] ¦ BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_A_AIR_FUEL_MASS_RATIO
BOILER_A_MIXED_LHV_PER_KG | BOILER A MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER A TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_A_MIXED_LHV_PER_KG) | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER A HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_A_STACK_TEMPERATURE-15.6)))) | Unknown/no sensor: BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS | BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER A HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,9*(BOILER_A_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_A_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_A_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_STATUS | BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER A HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_A_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER A HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,0*10^-6*28*5654*BOILER_A_BOILER_LOAD) | Unknown/no sensor: BOILER_A_STATUS | BOILER_A_STATUS
BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER A TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | Unknown/no sensor: BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_A_STATUS | BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_A_STATUS
BOILER_A_RADIATION_LOSSES | BOILER A RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_MIXED_LHV_PER_KG*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOAD^2-0.0899*BOILER_A_BOILER_LOAD+3.2426)/100) | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER A TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_A_RADIATION_LOSSES) | Unknown/no sensor: BOILER_A_RADIATION_LOSSES ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_RADIATION_LOSSES ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER A TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_A_BOILER_INDIRECT_EFFICIENCY | BOILER A BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_A_HP_STEAM_ENTHALPY | BOILER A HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS)+2.66244961166282*DESUPERHEATER_OUTLET_TEMPERATURE)*0.239+2) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] ¦ BOILER_A_STATUS
BOILER_A_TOTAL_STEAM_ENERGY | BOILER A TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_HP_STEAM_ENTHALPY/1000000) | Unknown/no sensor: BOILER_A_HP_STEAM_ENTHALPY ¦ BOILER_A_STATUS | BOILER_A_HP_STEAM_ENTHALPY ¦ BOILER_A_STATUS
BOILER_A_BFW_ENTHALPY | BOILER A BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_A_INLET_TEMPERATURE) | PI exists but NOT in hierarchy: ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ BOILER_A_STATUS
BOILER_A_CORRECTED_BFW_FLOW | BOILER A CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-DESUPERHEATER_OUTLET_STEAM_FLOW-BOILER_A_CBD_BD))/1000) | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_A[sensor:UN.UO.71FI1102.PV] ¦ BFW_FLOW_TO_ECOMONIZER_A[sensor:UN.UO.71FI1103.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV]; Unknown/no sensor: BOILER_A_STATUS | BFW_FLOW_TO_DESUPERHEATER_A[sensor:UN.UO.71FI1102.PV] ¦ BFW_FLOW_TO_ECOMONIZER_A[sensor:UN.UO.71FI1103.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ BOILER_A_STATUS
BOILER_A_BFW_ENERGY | BOILER A BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*BOILER_A_BFW_ENTHALPY/1000) | Unknown/no sensor: BOILER_A_BFW_ENTHALPY ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS | BOILER_A_BFW_ENTHALPY ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS
BOILER_A_FUEL_GAS_ENERGY_INPUT | BOILER A FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FG_FLOW_RATE*1000*BOILER_A_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_STEAM_DRUM_TEMP | BOILER A STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,4.02521999671835*log(STEAM_DRUM_A_PRESSURE*98.065)^3-4.64392873298701*log(STEAM_DRUM_A_PRESSURE*98.065)^2+11.2370106828649*log(STEAM_DRUM_A_PRESSURE*98.065)+83.4806425229703) | PI exists but NOT in hierarchy: STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV]; Unknown/no sensor: BOILER_A_STATUS | STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ BOILER_A_STATUS
BOILER_A_BLOWDOWN_LOSS | BOILER A BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,((BOILER_A_CBD_BD/1000)*((STEAM_DRUM_A_PRESSURE*2.11087739028321+SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV]; Unknown/no sensor: BOILER_A_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV] ¦ BOILER_A_STATUS
BOILER_A_TOTAL_FLUE_GAS_GENERATED | BOILER A TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW/1000*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS
BOILER_A_STACK_LOSS | BOILER A STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_FLOW/(1000*1000)) | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_CORRECTED_FUEL_FLOW | BOILER A CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW-((BOILER_A_FUEL_GAS_ENERGY_INPUT-(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY+BOILER_A_BLOWDOWN_LOSS+BOILER_A_STACK_LOSS+BOILER_A_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_A_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOAD^2-0.0899*BOILER_A_BOILER_LOAD+3.2426)/100+(BOILE | Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_MIXED_LHV_PER_KG | BOILER_A_BFW_ENERGY ¦ BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STACK_LOSS ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_FUEL_CONSUMPTION | BOILER A FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER A SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)) | Unknown/no sensor: BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER A SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)*4.184) | Unknown/no sensor: BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS
BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER A CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_THERMAL_EFFICIENCY | BOILER A THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY)/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER A EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_BLOWDOWN_LOSS/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS | BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS
BOILER_A_ECONOMIZER_DUTY | BOILER A ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*((STEAM_DRUM_A_PRESSURE*0.0336523715096497+ECONIMIZER_A_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_A_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV]; Unknown/no sensor: BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS
BOILER_A_LMTD_ECONOMIZER | BOILER A LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,((673-ECONIMIZER_A_OUTLET_TEMPERATURE)-(BOILER_A_STACK_TEMPERATURE-ECONOMIZER_A_INLET_TEMPERATURE))/ln((673-ECONIMIZER_A_OUTLET_TEMPERATURE)/(-ECONOMIZER_A_INLET_TEMPERATURE+BOILER_A_STACK_TEMPERATURE))) | PI exists but NOT in hierarchy: ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ BOILER_A_STATUS
BOILER_A_UA_ECONOMIZER | BOILER A UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY/BOILER_A_LMTD_ECONOMIZER) | Unknown/no sensor: BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_LMTD_ECONOMIZER ¦ BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_LMTD_ECONOMIZER ¦ BOILER_A_STATUS
BOILER_A_FOULING_INDEX | BOILER A FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,1/BOILER_A_UA_ECONOMIZER) | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_UA_ECONOMIZER | BOILER_A_STATUS ¦ BOILER_A_UA_ECONOMIZER
BOILER_A_SH_DUTY | BOILER A SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*((STEAM_DRUM_A_PRESSURE*-2.64315212289699+DESUPERHEATER_TEMPERATURE*3.58096116723573+1939.73413132244)-(STEAM_DRUM_A_PRESSURE*-4.27591051303366+SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | PI exists but NOT in hierarchy: DESUPERHEATER_TEMPERATURE[sensor:UN.UO.71TI1106.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV]; Unknown/no sensor: BOILER_A_STATUS | DESUPERHEATER_TEMPERATURE[sensor:UN.UO.71TI1106.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV] ¦ BOILER_A_STATUS
BOILER_A_SH_SPECIFIC_DUTY | BOILER A SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_SH_DUTY/DESUPERHEATER_OUTLET_STEAM_FLOW*1000) | Unknown/no sensor: BOILER_A_SH_DUTY ¦ BOILER_A_STATUS | BOILER_A_SH_DUTY ¦ BOILER_A_STATUS
BOILER_A_FUEL_GAS_CORRECTED_TPH | BOILER A FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW/1000) | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS
BOILER_A_TOTAL_FLUE_GAS_CORRECTED | BOILER A TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_CORRECTED_TPH*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS
BOILER_A_STACK_LOSS_CORRECTED | BOILER A STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_CORRECTED_TPH/1000) | Unknown/no sensor: BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_SUPERHEATED_STEAM_BFW_RATIO | BOILER A SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(DESUPERHEATER_OUTLET_STEAM_FLOW+BOILER_A_CBD_BD)/(BOILER_A_CORRECTED_BFW_FLOW*1000)) | PI exists but NOT in hierarchy: BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV]; Unknown/no sensor: BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS | BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS
BOILER_A_CO2_EMISSIONS | BOILER A CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CO2_FORMED*BOILER_A_FUEL_GAS_CORRECTED_TPH) | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS | BOILER_A_CO2_FORMED ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS
BOILER_A_CALCULATED_AIRFLOW_NM3H | BOILER A CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS | BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS
BOILER_A_SH_PERFORMANCE | BOILER A SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(BOILER_A_SH_SPECIFIC_DUTY)/0.128049016*100) | Unknown/no sensor: BOILER_A_SH_SPECIFIC_DUTY ¦ BOILER_A_STATUS | BOILER_A_SH_SPECIFIC_DUTY ¦ BOILER_A_STATUS
BOILER_A_ENERGY_GAINED | BOILER A ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY) | Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_CONVECTION_DUTY | BOILER A CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY+BOILER_A_SH_DUTY+BOILER_A_STACK_LOSS_CORRECTED) | Unknown/no sensor: BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_SH_DUTY ¦ BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_SH_DUTY ¦ BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_A_STATUS
BOILER_A_RADIATION_DUTY | BOILER A RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_ENERGY_GAINED-BOILER_A_CONVECTION_DUTY) | Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS
BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER A PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS
BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER A PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_A_ENERGY_GAINED ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS | BOILER_A_ENERGY_GAINED ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS
BOILER_A_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER A RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | Unknown/no sensor: BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_A_STATUS | BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_A_STATUS
BOILER_A_RADIATION_SECTION_EFFICIENCY | BOILER A RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS
BOILER_A_CONVECTION_SECTION_EFFICIENCY | BOILER A CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS
BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER B FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | NORMALIZED BOILER B FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER B FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER B FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL)*100 | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER_B_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER B FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_CO2_CONCENTRATION | NORMALIZED BOILER B FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | NORMALIZED BOILER B FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | NORMALIZED BOILER B FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | NORMALIZED BOILER B FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | NORMALIZED BOILER B FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | NORMALIZED BOILER B FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER B FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_B_FG_MW | BOILER B FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_B_FG_NC5_C | Unknown/no sensor: NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION
BOILER_B_FG_CH4_MASS_PERCENTAGE | BOILER B FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION
BOILER_B_FG_ETHANE_MASS_PERCENTAGE | BOILER B FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION
BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE | BOILER B FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION
BOILER_B_FG_PROPANE_MASS_PERCENTAGE | BOILER B FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION
BOILER_B_FG_NITROGEN_MASS_PERCENTAGE | BOILER B FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_N2_CONCENTRATION
BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE | BOILER B FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION
BOILER_B_FG_IC4_MASS_PERCENTAGE | BOILER B FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION
BOILER_B_FG_NC4_MASS_PERCENTAGE | BOILER B FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION
BOILER_B_FG_NC5_MASS_PERCENTAGE | BOILER B FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION
BOILER_B_FG_IC5_MASS_PERCENTAGE | BOILER B FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION
BOILER_B_FG_DENSITY | BOILER B FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_MW/22.414 | Unknown/no sensor: BOILER_B_FG_MW | BOILER_B_FG_MW
BOILER_B_LHV_DESIGN | BOILER B LHV DESIGN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_B_FG_DENSITY)/1000 | Unknown/no sensor: BOILER_B_FG_DENSITY | BOILER_B_FG_DENSITY
BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER B TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_PERCENTAGE+BOILER_B_FG_ETHANE_MASS_PERCENTAGE+BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_B_FG_PROPANE_MASS_PERCENTAGE+BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_B_FG_NITROGEN_MASS_PERCENTAGE+BOILER_B_FG_IC4_MASS_PERCENTAGE+BOILER_B_FG_NC4_MASS_PERCENTAGE+BOILER_B_FG_NC5_MASS_PERCENTAGE+BOILER_B_FG_IC5_MASS_PERCENTAGE | Unknown/no sensor: BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_FG_IC4_MASS_PERCENTAGE | BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_FG_IC4_MASS_PERCENTAGE ¦ BOILER_B_FG_IC5_MASS_PERCENTAGE ¦ BOILER_B_FG_NC4_MASS_PERCENTAGE ¦ BOILER_B_FG_NC5_MASS_PERCENTAGE ¦ BOILER_B_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_B_FG_PROPANE_MASS_PERCENTAGE
BOILER_B_FG_CH4_MASS_FRACTION | BOILER B FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER B FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER B FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER B FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NITROGEN_MASS_FRACTION | BOILER B FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER B FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_IC4_MASS_FRACTION | BOILER B FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_IC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NC4_MASS_FRACTION | BOILER B FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_NC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NC5_MASS_FRACTION | BOILER B FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_NC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_IC5_MASS_FRACTION | BOILER B FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_B_FG_IC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_LHV | BOILER B LHV | Kcal/Kg | LBM_preprocessing_inferred_tags_main | (BOILER_B_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_B_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_B_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_B_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_B_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_B_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_B_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_B_FG_NC5_MASS_FRAC | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION ¦ BOILER_B_FG_NC4_MASS_FRACTION ¦ BOILER_B_FG_NC5_MASS_FRACTION ¦ BOILER_B_FG_NITROGEN_MASS_FRACTION ¦ BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_FG_FLOW_RATE | BOILER B FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_B_FUEL_GAS_FLOW/1000 | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]
BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER B AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*34.344 | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER B AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*17.265 | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*16.119 | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*14.807 | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER B AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*15.703 | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER B AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER B AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER B AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER B AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_H2_CO2_COMBUSTION | BOILER B H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*0 | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_CH4_CO2_COMBUSTION | BOILER B CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*2.744 | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_ETHANE_CO2_COMBUSTION | BOILER B ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*2.927 | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHYLENE_CO2_COMBUSTION | BOILER B ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*3.138 | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_PROPANE_CO2_COMBUSTION | BOILER B PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*2.994 | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_NC4_CO2_COMBUSTION | BOILER B NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_IC4_CO2_COMBUSTION | BOILER B IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_NC5_CO2_COMBUSTION | BOILER B NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_IC5_CO2_COMBUSTION | BOILER B IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_H2_N2_COMBUSTION | BOILER B H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*26.407 | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_CH4_N2_COMBUSTION | BOILER B CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*13.275 | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_ETHANE_N2_COMBUSTION | BOILER B ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*12.394 | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHYLENE_N2_COMBUSTION | BOILER B ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*11.385 | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_PROPANE_N2_COMBUSTION | BOILER B PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*12.074 | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_IC4_N2_COMBUSTION | BOILER B IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_NC4_N2_COMBUSTION | BOILER B NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_IC5_N2_COMBUSTION | BOILER B IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_NC5_N2_COMBUSTION | BOILER B NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_H2_H2O_COMBUSTION | BOILER B H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*8.937 | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_CH4_H2O_COMBUSTION | BOILER B CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*2.246 | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_ETHANE_H2O_COMBUSTION | BOILER B ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*1.798 | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHYLENE_H2O_COMBUSTION | BOILER B ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*1.285 | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_PROPANE_H2O_COMBUSTION | BOILER B PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*1.634 | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_IC4_H2O_COMBUSTION | BOILER B IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_NC4_H2O_COMBUSTION | BOILER B NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_IC5_H2O_COMBUSTION | BOILER B IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_NC5_H2O_COMBUSTION | BOILER B NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER B AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_B_AI | Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_B_CO2_FORMED | BOILER B CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_CH4_CO2_COMBUSTION+BOILER_B_ETHANE_CO2_COMBUSTION+BOILER_B_ETHYLENE_CO2_COMBUSTION+BOILER_B_PROPANE_CO2_COMBUSTION+BOILER_B_NC4_CO2_COMBUSTION+BOILER_B_IC4_CO2_COMBUSTION+BOILER_B_NC5_CO2_COMBUSTION+BOILER_B_IC5_CO2_COMBUSTION | Unknown/no sensor: BOILER_B_CH4_CO2_COMBUSTION ¦ BOILER_B_ETHANE_CO2_COMBUSTION ¦ BOILER_B_ETHYLENE_CO2_COMBUSTION ¦ BOILER_B_IC4_CO2_COMBUSTION ¦ BOILER_B_IC5_CO2_COMBUSTION | BOILER_B_CH4_CO2_COMBUSTION ¦ BOILER_B_ETHANE_CO2_COMBUSTION ¦ BOILER_B_ETHYLENE_CO2_COMBUSTION ¦ BOILER_B_IC4_CO2_COMBUSTION ¦ BOILER_B_IC5_CO2_COMBUSTION ¦ BOILER_B_NC4_CO2_COMBUSTION ¦ BOILER_B_NC5_CO2_COMBUSTION ¦ BOILER_B_PROPANE_CO2_COMBUSTION
BOILER_B_N2_FORMED | BOILER B N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_H2_N2_COMBUSTION+BOILER_B_CH4_N2_COMBUSTION+BOILER_B_ETHANE_N2_COMBUSTION+BOILER_B_ETHYLENE_N2_COMBUSTION+BOILER_B_PROPANE_N2_COMBUSTION+BOILER_B_IC4_N2_COMBUSTION+BOILER_B_NC4_N2_COMBUSTION+BOILER_B_IC5_N2_COMBUSTION+BOILER_B_NC5_N2_COMBUSTION | Unknown/no sensor: BOILER_B_CH4_N2_COMBUSTION ¦ BOILER_B_ETHANE_N2_COMBUSTION ¦ BOILER_B_ETHYLENE_N2_COMBUSTION ¦ BOILER_B_H2_N2_COMBUSTION ¦ BOILER_B_IC4_N2_COMBUSTION | BOILER_B_CH4_N2_COMBUSTION ¦ BOILER_B_ETHANE_N2_COMBUSTION ¦ BOILER_B_ETHYLENE_N2_COMBUSTION ¦ BOILER_B_H2_N2_COMBUSTION ¦ BOILER_B_IC4_N2_COMBUSTION ¦ BOILER_B_IC5_N2_COMBUSTION ¦ BOILER_B_NC4_N2_COMBUSTION ¦ BOILER_B_NC5_N2_COMBUSTION ¦ BOILER_B_PROPANE_N2_COMBUSTION
BOILER_B_H2O_FORMED | BOILER B H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_H2_H2O_COMBUSTION+BOILER_B_CH4_H2O_COMBUSTION+BOILER_B_ETHANE_H2O_COMBUSTION+BOILER_B_ETHYLENE_H2O_COMBUSTION+BOILER_B_PROPANE_H2O_COMBUSTION+BOILER_B_IC4_H2O_COMBUSTION+BOILER_B_NC4_H2O_COMBUSTION+BOILER_B_IC5_H2O_COMBUSTION+BOILER_B_NC5_H2O_COMBUSTION | Unknown/no sensor: BOILER_B_CH4_H2O_COMBUSTION ¦ BOILER_B_ETHANE_H2O_COMBUSTION ¦ BOILER_B_ETHYLENE_H2O_COMBUSTION ¦ BOILER_B_H2_H2O_COMBUSTION ¦ BOILER_B_IC4_H2O_COMBUSTION | BOILER_B_CH4_H2O_COMBUSTION ¦ BOILER_B_ETHANE_H2O_COMBUSTION ¦ BOILER_B_ETHYLENE_H2O_COMBUSTION ¦ BOILER_B_H2_H2O_COMBUSTION ¦ BOILER_B_IC4_H2O_COMBUSTION ¦ BOILER_B_IC5_H2O_COMBUSTION ¦ BOILER_B_NC4_H2O_COMBUSTION ¦ BOILER_B_NC5_H2O_COMBUSTION ¦ BOILER_B_PROPANE_H2O_COMBUSTION
BOILER_B_CORRECTED_COMBUSTION_AIR | BOILER B CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_B_AIR_MOISTURE) | Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_B_CORRECTED_COMBUTION_H2O_FORMED | BOILER B CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_H2O_FORMED+(BOILER_B_CORRECTED_COMBUSTION_AIR-BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_H2O_FORMED | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_H2O_FORMED
BOILER_B_EXCESS_AIR | BOILER B EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_B_FLUE_GAS_OXGYGEN)*((BOILER_B_N2_FORMED/28.01)+(BOILER_B_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_B_CO2_FORMED/44.01))/(20.95-BOILER_B_FLUE_GAS_OXGYGEN)) | PI exists but NOT in hierarchy: BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV]; Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_B_N2_FORMED | BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV] ¦ BOILER_B_CO2_FORMED ¦ BOILER_B_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_B_N2_FORMED
BOILER_B_AIR_FUEL_MASS_RATIO | BOILER B AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_EXCESS_AIR+BOILER_B_CORRECTED_COMBUSTION_AIR | Unknown/no sensor: BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_EXCESS_AIR | BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_EXCESS_AIR
BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER B TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_AIR_MOISTURE | Unknown/no sensor: BOILER_B_AIR_FUEL_MASS_RATIO | BOILER_B_AIR_FUEL_MASS_RATIO
BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER B TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_TOTAL_MOISTURE_WITH_AIR+BOILER_B_H2O_FORMED | Unknown/no sensor: BOILER_B_H2O_FORMED ¦ BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER_B_H2O_FORMED ¦ BOILER_B_TOTAL_MOISTURE_WITH_AIR
BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER B CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | PI exists but NOT in hierarchy: BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] | BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV]
BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER B AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_AIR_CP_REF_T+BOILER_B_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | Unknown/no sensor: BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER_B_CP_AT_COMBUSTION_TEMPERATURE
BOILER_B_CP_H2_FUEL_TEMP | BOILER B CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_CH4_FUEL_TEMP | BOILER B CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_ETHANE_FUEL_TEMP | BOILER B CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_PROPANE_FUEL_TEMP | BOILER B CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_ETHYLENE_FUEL_TEMP | BOILER B CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_NC4_FUEL_TEMP | BOILER B CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_IC4_FUEL_TEMP | BOILER B CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_NC5_FUEL_TEMP | BOILER B CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_IC5_FUEL_TEMP | BOILER B CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER B CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_B_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_B_FG_NC4_MASS_FRACTION/COMPONENT | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION ¦ BOILER_B_FG_MW ¦ BOILER_B_FG_NC4_MASS_FRACTION ¦ BOILER_B_FG_NC5_MASS_FRACTION ¦ BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER B CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_B_CP_H2_FUEL_TEMP+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_B_CP_CH4_FUEL_TEMP+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_B_CP_ETHYLENE_FUEL_TEMP+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_B_CP_ETHANE_FUEL_TEMP+(BOILER_B_FG_P | Unknown/no sensor: BOILER_B_CP_CH4_FUEL_TEMP ¦ BOILER_B_CP_ETHANE_FUEL_TEMP ¦ BOILER_B_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_B_CP_H2_FUEL_TEMP ¦ BOILER_B_CP_IC4_FUEL_TEMP (+9 more) | BOILER_B_CP_CH4_FUEL_TEMP ¦ BOILER_B_CP_ETHANE_FUEL_TEMP ¦ BOILER_B_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_B_CP_H2_FUEL_TEMP ¦ BOILER_B_CP_IC4_FUEL_TEMP ¦ BOILER_B_CP_IC5_FUEL_TEMP ¦ BOILER_B_CP_NC4_FUEL_TEMP ¦ BOILER_B_CP_NC5_FUEL_TEMP ¦ BOILER_B_CP_PROPANE_FUEL_TEMP ¦ BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION ¦ BOILER_B_FG_MW ¦ BOILER_B_FG_NC4_MASS_FRACTION ¦ BOILER_B_FG_NC5_MASS_FRACTION ¦ BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER B AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_B_FG_MW)/2 | Unknown/no sensor: BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_B_FG_MW | BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_B_FG_MW
BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_B_EXCESS_AIR*(1-BOILER_B_AIR_MOISTURE)+BOILER_B_N2_FORMED+BOILER_B_CO2_FORMED | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_N2_FORMED
BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | Unknown/no sensor: BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_FLUE_GAS_MW | BOILER B FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_B_CO2_FORMED/44.01+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.96) | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER B AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_B_CO2_FORMED/44.01+BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.85*BOILER_B_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_B_FLUE_GAS_MW)/BOILER_B_FLUE_GAS_MW | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_MW ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_MW ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED
BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER B SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]; Unknown/no sensor: BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] ¦ BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER B SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_B_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_B_AIR_FUEL_MASS_RATIO | PI exists but NOT in hierarchy: BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV]; Unknown/no sensor: BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_B_AIR_FUEL_MASS_RATIO | BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] ¦ BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_B_AIR_FUEL_MASS_RATIO
BOILER_B_MIXED_LHV_PER_KG | BOILER B MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER B TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_B_MIXED_LHV_PER_KG) | Unknown/no sensor: BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER B HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_B_STACK_TEMPERATURE-15.6)))) | Unknown/no sensor: BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS | BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER B HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,9*(BOILER_B_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_B_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_B_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_STATUS | BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER B HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_B_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_STATUS ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER B HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,0*10^-6*28*5654*BOILER_B_BOILER_LOAD) | Unknown/no sensor: BOILER_B_STATUS | BOILER_B_STATUS
BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER B TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | Unknown/no sensor: BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_B_STATUS | BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_B_STATUS
BOILER_B_RADIATION_LOSSES | BOILER B RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_MIXED_LHV_PER_KG*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOAD^2-0.0899*BOILER_B_BOILER_LOAD+3.2426)/100) | Unknown/no sensor: BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER B TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_B_RADIATION_LOSSES) | Unknown/no sensor: BOILER_B_RADIATION_LOSSES ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_RADIATION_LOSSES ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER B TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_B_BOILER_INDIRECT_EFFICIENCY | BOILER B BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_B_HP_STEAM_ENTHALPY | BOILER B HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_B)+2.66244961166282*DESUPERHEATER_B_OUTLET_TEMPERATURE)*0.239+2) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] ¦ BOILER_A_STATUS
BOILER_B_TOTAL_STEAM_ENERGY | BOILER B TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_HP_STEAM_ENTHALPY/1000000) | Unknown/no sensor: BOILER_B_HP_STEAM_ENTHALPY ¦ BOILER_B_STATUS | BOILER_B_HP_STEAM_ENTHALPY ¦ BOILER_B_STATUS
BOILER_B_BFW_ENTHALPY | BOILER B BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_B_INLET_TEMPERATURE) | PI exists but NOT in hierarchy: ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ BOILER_A_STATUS
BOILER_B_CORRECTED_BFW_FLOW | BOILER B CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-DESUPERHEATER_B_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_B))/1000) | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_B[sensor:UN.UO.71FI1202.PV] ¦ BFW_FLOW_TO_ECONOMIZER_B[sensor:UN.UO.71FI1203.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV]; Unknown/no sensor: BOILER_B_STATUS | BFW_FLOW_TO_DESUPERHEATER_B[sensor:UN.UO.71FI1202.PV] ¦ BFW_FLOW_TO_ECONOMIZER_B[sensor:UN.UO.71FI1203.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV] ¦ BOILER_B_STATUS
BOILER_B_BFW_ENERGY | BOILER B BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*BOILER_B_BFW_ENTHALPY/1000) | Unknown/no sensor: BOILER_B_BFW_ENTHALPY ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS | BOILER_B_BFW_ENTHALPY ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS
BOILER_B_FUEL_GAS_ENERGY_INPUT | BOILER B FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FG_FLOW_RATE*1000*BOILER_B_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_STEAM_DRUM_TEMP | BOILER B STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,4.02521999671835*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | PI exists but NOT in hierarchy: BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV]; Unknown/no sensor: BOILER_B_STATUS | BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_STATUS
BOILER_B_BLOWDOWN_LOSS | BOILER B BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,((CBD_BLOW_DOWN_B/1000)*((BOILER_B_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV]; Unknown/no sensor: BOILER_B_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV] ¦ BOILER_B_STATUS
BOILER_B_TOTAL_FLUE_GAS_GENERATED | BOILER B TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW/1000*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]; Unknown/no sensor: BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS
BOILER_B_STACK_LOSS | BOILER B STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_FLOW/(1000*1000)) | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]; Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_CORRECTED_FUEL_FLOW | BOILER B CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW-((BOILER_B_FUEL_GAS_ENERGY_INPUT-(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY+BOILER_B_BLOWDOWN_LOSS+BOILER_B_STACK_LOSS+BOILER_B_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_B_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOAD^2-0.0899*BOILER_B_BOILER_LOAD+3.2426)/100+(BOILE | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]; Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_MIXED_LHV_PER_KG | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] ¦ BOILER_B_BFW_ENERGY ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STACK_LOSS ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_FUEL_CONSUMPTION | BOILER B FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER B SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)) | Unknown/no sensor: BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER B SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)*4.184) | Unknown/no sensor: BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS
BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER B CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_THERMAL_EFFICIENCY | BOILER B THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY)/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER B EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_BLOWDOWN_LOSS/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS | BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS
BOILER_B_ECONOMIZER_DUTY | BOILER B ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_B_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_B_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV]; Unknown/no sensor: BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV] ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS
BOILER_B_LMTD_ECONOMIZER | BOILER B LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,((673-ECONOMIZER_B_OUTLET_TEMPERATURE)-(BOILER_B_STACK_TEMPERATURE-ECONOMIZER_B_INLET_TEMPERATURE))/ln((673-ECONOMIZER_B_OUTLET_TEMPERATURE)/(-ECONOMIZER_B_INLET_TEMPERATURE+BOILER_B_STACK_TEMPERATURE))) | PI exists but NOT in hierarchy: ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV]; Unknown/no sensor: BOILER_B_STATUS | ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV] ¦ BOILER_B_STATUS
BOILER_B_UA_ECONOMIZER | BOILER B UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY/BOILER_B_LMTD_ECONOMIZER) | Unknown/no sensor: BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_LMTD_ECONOMIZER ¦ BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_LMTD_ECONOMIZER ¦ BOILER_B_STATUS
BOILER_B_FOULING_INDEX | BOILER B FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,1/BOILER_B_UA_ECONOMIZER) | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_UA_ECONOMIZER | BOILER_B_STATUS ¦ BOILER_B_UA_ECONOMIZER
BOILER_B_SH_DUTY | BOILER B SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_B_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_B_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | PI exists but NOT in hierarchy: BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV]; Unknown/no sensor: BOILER_B_STATUS | BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV] ¦ BOILER_B_STATUS
BOILER_B_SH_SPECIFIC_DUTY | BOILER B SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_SH_DUTY/DESUPERHEATER_B_OUTLET_STEAM_FLOW*1000) | Unknown/no sensor: BOILER_B_SH_DUTY ¦ BOILER_B_STATUS | BOILER_B_SH_DUTY ¦ BOILER_B_STATUS
BOILER_B_FUEL_GAS_CORRECTED_TPH | BOILER B FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW/1000) | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS
BOILER_B_TOTAL_FLUE_GAS_CORRECTED | BOILER B TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_CORRECTED_TPH*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS
BOILER_B_STACK_LOSS_CORRECTED | BOILER B STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_CORRECTED_TPH/1000) | Unknown/no sensor: BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_SUPERHEATED_STEAM_BFW_RATIO | BOILER B SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(DESUPERHEATER_B_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_B)/(BOILER_B_CORRECTED_BFW_FLOW*1000)) | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV]; Unknown/no sensor: BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS | CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV] ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS
BOILER_B_CO2_EMISSIONS | BOILER B CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CO2_FORMED*BOILER_B_FUEL_GAS_CORRECTED_TPH) | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS | BOILER_B_CO2_FORMED ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS
BOILER_B_CALCULATED_AIRFLOW_NM3H | BOILER B CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | Unknown/no sensor: BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS | BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS
BOILER_B_SH_PERFORMANCE | BOILER B SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(BOILER_B_SH_SPECIFIC_DUTY)/0.110075721*100) | Unknown/no sensor: BOILER_B_SH_SPECIFIC_DUTY ¦ BOILER_B_STATUS | BOILER_B_SH_SPECIFIC_DUTY ¦ BOILER_B_STATUS
BOILER_B_ENERGY_GAINED | BOILER B ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY) | Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_CONVECTION_DUTY | BOILER B CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY+BOILER_B_SH_DUTY+BOILER_B_STACK_LOSS_CORRECTED) | Unknown/no sensor: BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_SH_DUTY ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_SH_DUTY ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_B_STATUS
BOILER_B_RADIATION_DUTY | BOILER B RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_ENERGY_GAINED-BOILER_B_CONVECTION_DUTY) | Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS
BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER B PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS
BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER B PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_B_ENERGY_GAINED ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS | BOILER_B_ENERGY_GAINED ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS
BOILER_B_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER B RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | Unknown/no sensor: BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_B_STATUS | BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_B_STATUS
BOILER_B_RADIATION_SECTION_EFFICIENCY | BOILER B RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS
BOILER_B_CONVECTION_SECTION_EFFICIENCY | BOILER B CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS
BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER C FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | NORMALIZED BOILER C FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER C FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER C FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL)*100 | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER_C_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER C FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_CO2_CONCENTRATION | NORMALIZED BOILER C FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | NORMALIZED BOILER C FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | NORMALIZED BOILER C FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | NORMALIZED BOILER C FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | NORMALIZED BOILER C FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | NORMALIZED BOILER C FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER C FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_C_FG_MW | BOILER C FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_C_FG_NC5_C | Unknown/no sensor: NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION
BOILER_C_FG_CH4_MASS_PERCENTAGE | BOILER C FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION
BOILER_C_FG_ETHANE_MASS_PERCENTAGE | BOILER C FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION
BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE | BOILER C FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION
BOILER_C_FG_PROPANE_MASS_PERCENTAGE | BOILER C FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION
BOILER_C_FG_NITROGEN_MASS_PERCENTAGE | BOILER C FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_N2_CONCENTRATION
BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE | BOILER C FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION
BOILER_C_FG_IC4_MASS_PERCENTAGE | BOILER C FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION
BOILER_C_FG_NC4_MASS_PERCENTAGE | BOILER C FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION
BOILER_C_FG_NC5_MASS_PERCENTAGE | BOILER C FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION
BOILER_C_FG_IC5_MASS_PERCENTAGE | BOILER C FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION
BOILER_C_FG_DENSITY | BOILER C FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_MW/22.414 | Unknown/no sensor: BOILER_C_FG_MW | BOILER_C_FG_MW
BOILER_C_LHV_DESIGEN | BOILER C LHV DESIGEN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_C_FG_DENSITY)/1000 | Unknown/no sensor: BOILER_C_FG_DENSITY | BOILER_C_FG_DENSITY
BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER C TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_PERCENTAGE+BOILER_C_FG_ETHANE_MASS_PERCENTAGE+BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_C_FG_PROPANE_MASS_PERCENTAGE+BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_C_FG_NITROGEN_MASS_PERCENTAGE+BOILER_C_FG_IC4_MASS_PERCENTAGE+BOILER_C_FG_NC4_MASS_PERCENTAGE+BOILER_C_FG_NC5_MASS_PERCENTAGE+BOILER_C_FG_IC5_MASS_PERCENTAGE | Unknown/no sensor: BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_FG_IC4_MASS_PERCENTAGE | BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_FG_IC4_MASS_PERCENTAGE ¦ BOILER_C_FG_IC5_MASS_PERCENTAGE ¦ BOILER_C_FG_NC4_MASS_PERCENTAGE ¦ BOILER_C_FG_NC5_MASS_PERCENTAGE ¦ BOILER_C_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_C_FG_PROPANE_MASS_PERCENTAGE
BOILER_C_FG_CH4_MASS_FRACTION | BOILER C FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER C FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER C FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER C FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NITROGEN_MASS_FRACTION | BOILER C FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER C FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_IC4_MASS_FRACTION | BOILER C FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_IC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NC4_MASS_FRACTION | BOILER C FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_NC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NC5_MASS_FRACTION | BOILER C FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_NC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_IC5_MASS_FRACTION | BOILER C FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_C_FG_IC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_LHV | BOILER C LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (BOILER_C_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_C_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_C_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_C_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_C_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_C_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_C_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_C_FG_NC5_MASS_FRAC | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION ¦ BOILER_C_FG_NC4_MASS_FRACTION ¦ BOILER_C_FG_NC5_MASS_FRACTION ¦ BOILER_C_FG_NITROGEN_MASS_FRACTION ¦ BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER C AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*34.344 | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER C AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*17.265 | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*16.119 | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*14.807 | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER C AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*15.703 | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER C AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER C AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER C AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER C AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_H2_CO2_COMBUSTION | BOILER C H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*0 | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_CH4_CO2_COMBUSTION | BOILER C CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*2.744 | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_ETHANE_CO2_COMBUSTION | BOILER C ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*2.927 | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHYLENE_CO2_COMBUSTION | BOILER C ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*3.138 | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_PROPANE_CO2_COMBUSTION | BOILER C PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*2.994 | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_NC4_CO2_COMBUSTION | BOILER C NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_IC4_CO2_COMBUSTION | BOILER C IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_NC5_CO2_COMBUSTION | BOILER C NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_IC5_CO2_COMBUSTION | BOILER C IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_H2_N2_COMBUSTION | BOILER C H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*26.407 | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_CH4_N2_COMBUSTION | BOILER C CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*13.275 | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_ETHANE_N2_COMBUSTION | BOILER C ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*12.394 | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHYLENE_N2_COMBUSTION | BOILER C ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*11.385 | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_PROPANE_N2_COMBUSTION | BOILER C PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*12.074 | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_IC4_N2_COMBUSTION | BOILER C IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_NC4_N2_COMBUSTION | BOILER C NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_IC5_N2_COMBUSTION | BOILER C IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_NC5_N2_COMBUSTION | BOILER C NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_H2_H2O_COMBUSTION | BOILER C H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*8.937 | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_CH4_H2O_COMBUSTION | BOILER C CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*2.246 | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_ETHANE_H2O_COMBUSTION | BOILER C ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*1.798 | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHYLENE_H2O_COMBUSTION | BOILER C ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*1.285 | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_PROPANE_H2O_COMBUSTION | BOILER C PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*1.634 | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_IC4_H2O_COMBUSTION | BOILER C IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_NC4_H2O_COMBUSTION | BOILER C NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_IC5_H2O_COMBUSTION | BOILER C IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_NC5_H2O_COMBUSTION | BOILER C NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER C AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_C_AI | Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_C_CO2_FORMED | BOILER C CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_CH4_CO2_COMBUSTION+BOILER_C_ETHANE_CO2_COMBUSTION+BOILER_C_ETHYLENE_CO2_COMBUSTION+BOILER_C_PROPANE_CO2_COMBUSTION+BOILER_C_NC4_CO2_COMBUSTION+BOILER_C_IC4_CO2_COMBUSTION+BOILER_C_NC5_CO2_COMBUSTION+BOILER_C_IC5_CO2_COMBUSTION | Unknown/no sensor: BOILER_C_CH4_CO2_COMBUSTION ¦ BOILER_C_ETHANE_CO2_COMBUSTION ¦ BOILER_C_ETHYLENE_CO2_COMBUSTION ¦ BOILER_C_IC4_CO2_COMBUSTION ¦ BOILER_C_IC5_CO2_COMBUSTION | BOILER_C_CH4_CO2_COMBUSTION ¦ BOILER_C_ETHANE_CO2_COMBUSTION ¦ BOILER_C_ETHYLENE_CO2_COMBUSTION ¦ BOILER_C_IC4_CO2_COMBUSTION ¦ BOILER_C_IC5_CO2_COMBUSTION ¦ BOILER_C_NC4_CO2_COMBUSTION ¦ BOILER_C_NC5_CO2_COMBUSTION ¦ BOILER_C_PROPANE_CO2_COMBUSTION
BOILER_C_N2_FORMED | BOILER C N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_H2_N2_COMBUSTION+BOILER_C_CH4_N2_COMBUSTION+BOILER_C_ETHANE_N2_COMBUSTION+BOILER_C_ETHYLENE_N2_COMBUSTION+BOILER_C_PROPANE_N2_COMBUSTION+BOILER_C_IC4_N2_COMBUSTION+BOILER_C_NC4_N2_COMBUSTION+BOILER_C_IC5_N2_COMBUSTION+BOILER_C_NC5_N2_COMBUSTION | Unknown/no sensor: BOILER_C_CH4_N2_COMBUSTION ¦ BOILER_C_ETHANE_N2_COMBUSTION ¦ BOILER_C_ETHYLENE_N2_COMBUSTION ¦ BOILER_C_H2_N2_COMBUSTION ¦ BOILER_C_IC4_N2_COMBUSTION | BOILER_C_CH4_N2_COMBUSTION ¦ BOILER_C_ETHANE_N2_COMBUSTION ¦ BOILER_C_ETHYLENE_N2_COMBUSTION ¦ BOILER_C_H2_N2_COMBUSTION ¦ BOILER_C_IC4_N2_COMBUSTION ¦ BOILER_C_IC5_N2_COMBUSTION ¦ BOILER_C_NC4_N2_COMBUSTION ¦ BOILER_C_NC5_N2_COMBUSTION ¦ BOILER_C_PROPANE_N2_COMBUSTION
BOILER_C_H2O_FORMED | BOILER C H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_H2_H2O_COMBUSTION+BOILER_C_CH4_H2O_COMBUSTION+BOILER_C_ETHANE_H2O_COMBUSTION+BOILER_C_ETHYLENE_H2O_COMBUSTION+BOILER_C_PROPANE_H2O_COMBUSTION+BOILER_C_IC4_H2O_COMBUSTION+BOILER_C_NC4_H2O_COMBUSTION+BOILER_C_IC5_H2O_COMBUSTION+BOILER_C_NC5_H2O_COMBUSTION | Unknown/no sensor: BOILER_C_CH4_H2O_COMBUSTION ¦ BOILER_C_ETHANE_H2O_COMBUSTION ¦ BOILER_C_ETHYLENE_H2O_COMBUSTION ¦ BOILER_C_H2_H2O_COMBUSTION ¦ BOILER_C_IC4_H2O_COMBUSTION | BOILER_C_CH4_H2O_COMBUSTION ¦ BOILER_C_ETHANE_H2O_COMBUSTION ¦ BOILER_C_ETHYLENE_H2O_COMBUSTION ¦ BOILER_C_H2_H2O_COMBUSTION ¦ BOILER_C_IC4_H2O_COMBUSTION ¦ BOILER_C_IC5_H2O_COMBUSTION ¦ BOILER_C_NC4_H2O_COMBUSTION ¦ BOILER_C_NC5_H2O_COMBUSTION ¦ BOILER_C_PROPANE_H2O_COMBUSTION
BOILER_C_CORRECTED_COMBUSTION_AIR | BOILER C CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_C_AIR_MOISTURE) | Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_C_CORRECTED_COMBUTION_H2O_FORMED | BOILER C CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_H2O_FORMED+(BOILER_C_CORRECTED_COMBUSTION_AIR-BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_H2O_FORMED | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_H2O_FORMED
BOILER_C_EXCESS_AIR | BOILER C EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_C_FLUE_GAS_OXGYGEN)*((BOILER_C_N2_FORMED/28.01)+(BOILER_C_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_C_CO2_FORMED/44.01))/(20.95-BOILER_C_FLUE_GAS_OXGYGEN)) | PI exists but NOT in hierarchy: BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV]; Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_C_N2_FORMED | BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV] ¦ BOILER_C_CO2_FORMED ¦ BOILER_C_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_C_N2_FORMED
BOILER_C_AIR_FUEL_MASS_RATIO | BOILER C AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_EXCESS_AIR+BOILER_C_CORRECTED_COMBUSTION_AIR | Unknown/no sensor: BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_EXCESS_AIR | BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_EXCESS_AIR
BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER C TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_AIR_MOISTURE | Unknown/no sensor: BOILER_C_AIR_FUEL_MASS_RATIO | BOILER_C_AIR_FUEL_MASS_RATIO
BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER C TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_TOTAL_MOISTURE_WITH_AIR+BOILER_C_H2O_FORMED | Unknown/no sensor: BOILER_C_H2O_FORMED ¦ BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER_C_H2O_FORMED ¦ BOILER_C_TOTAL_MOISTURE_WITH_AIR
BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER C CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | PI exists but NOT in hierarchy: BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] | BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV]
BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER C AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_AIR_CP_REF_T+BOILER_C_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | Unknown/no sensor: BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER_C_CP_AT_COMBUSTION_TEMPERATURE
BOILER_C_CP_H2_FUEL_TEMP | BOILER C CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_CH4_FUEL_TEMP | BOILER C CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_ETHANE_FUEL_TEMP | BOILER C CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_PROPANE_FUEL_TEMP | BOILER C CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_ETHYLENE_FUEL_TEMP | BOILER C CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_NC4_FUEL_TEMP | BOILER C CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_IC4_FUEL_TEMP | BOILER C CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_NC5_FUEL_TEMP | BOILER C CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_IC5_FUEL_TEMP | BOILER C CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER C CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_C_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_C_FG_NC4_MASS_FRACTION/COMPONENT | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION ¦ BOILER_C_FG_MW ¦ BOILER_C_FG_NC4_MASS_FRACTION ¦ BOILER_C_FG_NC5_MASS_FRACTION ¦ BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER C CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_C_CP_H2_FUEL_TEMP+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_C_CP_CH4_FUEL_TEMP+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_C_CP_ETHYLENE_FUEL_TEMP+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_C_CP_ETHANE_FUEL_TEMP+(BOILER_C_FG_P | Unknown/no sensor: BOILER_C_CP_CH4_FUEL_TEMP ¦ BOILER_C_CP_ETHANE_FUEL_TEMP ¦ BOILER_C_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_C_CP_H2_FUEL_TEMP ¦ BOILER_C_CP_IC4_FUEL_TEMP (+9 more) | BOILER_C_CP_CH4_FUEL_TEMP ¦ BOILER_C_CP_ETHANE_FUEL_TEMP ¦ BOILER_C_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_C_CP_H2_FUEL_TEMP ¦ BOILER_C_CP_IC4_FUEL_TEMP ¦ BOILER_C_CP_IC5_FUEL_TEMP ¦ BOILER_C_CP_NC4_FUEL_TEMP ¦ BOILER_C_CP_NC5_FUEL_TEMP ¦ BOILER_C_CP_PROPANE_FUEL_TEMP ¦ BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION ¦ BOILER_C_FG_MW ¦ BOILER_C_FG_NC4_MASS_FRACTION ¦ BOILER_C_FG_NC5_MASS_FRACTION ¦ BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER C AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_C_FG_MW)/2 | Unknown/no sensor: BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_C_FG_MW | BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_C_FG_MW
BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_C_EXCESS_AIR*(1-BOILER_C_AIR_MOISTURE)+BOILER_C_N2_FORMED+BOILER_C_CO2_FORMED | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_N2_FORMED
BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | Unknown/no sensor: BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_FLUE_GAS_MW | BOILER C FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_C_CO2_FORMED/44.01+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.96) | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER C AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_C_CO2_FORMED/44.01+BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.85*BOILER_C_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_C_FLUE_GAS_MW)/BOILER_C_FLUE_GAS_MW | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_MW ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_MW ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED
BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER C SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]; Unknown/no sensor: BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] ¦ BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER C SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_C_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_C_AIR_FUEL_MASS_RATIO | PI exists but NOT in hierarchy: BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV]; Unknown/no sensor: BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_C_AIR_FUEL_MASS_RATIO | BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] ¦ BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_C_AIR_FUEL_MASS_RATIO
BOILER_C_MIXED_LHV_PER_KG | BOILER C MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER C TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_C_MIXED_LHV_PER_KG) | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER C HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_C_STACK_TEMPERATURE-15.6)))) | Unknown/no sensor: BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS | BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER C HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,9*(BOILER_C_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_C_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_C_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_STATUS | BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER C HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_C_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER C HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,0*10^-6*28*5654*BOILER_C_BOILER_LOAD) | Unknown/no sensor: BOILER_C_STATUS | BOILER_C_STATUS
BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER C TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | Unknown/no sensor: BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_C_STATUS | BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_C_STATUS
BOILER_C_RADIATION_LOSSES | BOILER C RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_MIXED_LHV_PER_KG*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOAD^2-0.0899*BOILER_C_BOILER_LOAD+3.2426)/100) | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER C TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_C_RADIATION_LOSSES) | Unknown/no sensor: BOILER_C_RADIATION_LOSSES ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_RADIATION_LOSSES ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER C TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_C_BOILER_INDIRECT_EFFICIENCY | BOILER C BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_C_HP_STEAM_ENTHALPY | BOILER C HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_C)+2.66244961166282*DESUPERHEATER_C_OUTLET_TEMPERATURE)*0.239+2) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] ¦ BOILER_A_STATUS
BOILER_C_TOTAL_STEAM_ENERGY | BOILER C TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_HP_STEAM_ENTHALPY/1000000) | Unknown/no sensor: BOILER_C_HP_STEAM_ENTHALPY ¦ BOILER_C_STATUS | BOILER_C_HP_STEAM_ENTHALPY ¦ BOILER_C_STATUS
BOILER_C_BFW_ENTHALPY | BOILER C BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_C_INLET_TEMPERATURE) | PI exists but NOT in hierarchy: ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ BOILER_A_STATUS
BOILER_C_CORRECTED_BFW_FLOW | BOILER C CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-DESUPERHEATER_C_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_C))/1000) | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_C[sensor:UN.UO.71FI1302.PV] ¦ BFW_FLOW_TO_ECONOMIZER_C[sensor:UN.UO.71FI1303.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV]; Unknown/no sensor: BOILER_C_STATUS | BFW_FLOW_TO_DESUPERHEATER_C[sensor:UN.UO.71FI1302.PV] ¦ BFW_FLOW_TO_ECONOMIZER_C[sensor:UN.UO.71FI1303.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV] ¦ BOILER_C_STATUS
BOILER_C_BFW_ENERGY | BOILER C BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*BOILER_C_BFW_ENTHALPY/1000) | Unknown/no sensor: BOILER_C_BFW_ENTHALPY ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS | BOILER_C_BFW_ENTHALPY ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS
BOILER_C_FUEL_GAS_ENERGY_INPUT | BOILER C FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FG_FLOW_RATE*1000*BOILER_C_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_STEAM_DRUM_TEMP | BOILER C STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,4.02521999671835*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | PI exists but NOT in hierarchy: BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV]; Unknown/no sensor: BOILER_C_STATUS | BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_STATUS
BOILER_C_BLOWDOWN_LOSS | BOILER C BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,((CBD_BLOW_DOWN_C/1000)*((BOILER_C_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV]; Unknown/no sensor: BOILER_C_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV] ¦ BOILER_C_STATUS
BOILER_C_TOTAL_FLUE_GAS_GENERATED | BOILER C TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW/1000*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS
BOILER_C_STACK_LOSS | BOILER C STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_FLOW/(1000*1000)) | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_CORRECTED_FUEL_FLOW | BOILER C CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW-((BOILER_C_FUEL_GAS_ENERGY_INPUT-(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY+BOILER_C_BLOWDOWN_LOSS+BOILER_C_STACK_LOSS+BOILER_C_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_C_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOAD^2-0.0899*BOILER_C_BOILER_LOAD+3.2426)/100+(BOILE | Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_MIXED_LHV_PER_KG | BOILER_C_BFW_ENERGY ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STACK_LOSS ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_FUEL_CONSUMPTION | BOILER C FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER C SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)) | Unknown/no sensor: BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER C SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)*4.184) | Unknown/no sensor: BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS
BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER C CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_THERMAL_EFFICIENCY | BOILER C THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY)/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER C EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_BLOWDOWN_LOSS/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS | BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS
BOILER_C_ECONOMIZER_DUTY | BOILER C ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_C_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_C_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV]; Unknown/no sensor: BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV] ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS
BOILER_C_LMTD_ECONOMIZER | BOILER C LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,((673-ECONOMIZER_C_OUTLET_TEMPERATURE)-(BOILER_C_STACK_TEMPERATURE-ECONOMIZER_C_INLET_TEMPERATURE))/ln((673-ECONOMIZER_C_OUTLET_TEMPERATURE)/(-ECONOMIZER_C_INLET_TEMPERATURE+BOILER_C_STACK_TEMPERATURE))) | PI exists but NOT in hierarchy: ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV]; Unknown/no sensor: BOILER_C_STATUS | ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV] ¦ BOILER_C_STATUS
BOILER_C_UA_ECONOMIZER | BOILER C UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY/BOILER_C_LMTD_ECONOMIZER) | Unknown/no sensor: BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_LMTD_ECONOMIZER ¦ BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_LMTD_ECONOMIZER ¦ BOILER_C_STATUS
BOILER_C_FOULING_INDEX | BOILER C FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,1/BOILER_C_UA_ECONOMIZER) | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_UA_ECONOMIZER | BOILER_C_STATUS ¦ BOILER_C_UA_ECONOMIZER
BOILER_C_SH_DUTY | BOILER C SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_C_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_C_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | PI exists but NOT in hierarchy: BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV]; Unknown/no sensor: BOILER_C_STATUS | BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV] ¦ BOILER_C_STATUS
BOILER_C_SH_SPECIFIC_DUTY | BOILER C SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_SH_DUTY/DESUPERHEATER_C_OUTLET_STEAM_FLOW*1000) | Unknown/no sensor: BOILER_C_SH_DUTY ¦ BOILER_C_STATUS | BOILER_C_SH_DUTY ¦ BOILER_C_STATUS
BOILER_C_FUEL_GAS_CORRECTED_TPH | BOILER C FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW/1000) | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS
BOILER_C_TOTAL_FLUE_GAS_CORRECTED | BOILER C TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_CORRECTED_TPH*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS
BOILER_C_STACK_LOSS_CORRECTED | BOILER C STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_CORRECTED_TPH/1000) | Unknown/no sensor: BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_SUPERHEATED_STEAM_BFW_RATIO | BOILER C SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(DESUPERHEATER_C_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_C)/(BOILER_C_CORRECTED_BFW_FLOW*1000)) | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV]; Unknown/no sensor: BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS | CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV] ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS
BOILER_C_CO2_EMISSIONS | BOILER C CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CO2_FORMED*BOILER_C_FUEL_GAS_CORRECTED_TPH) | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS | BOILER_C_CO2_FORMED ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS
BOILER_C_CALCULATED_AIRFLOW_NM3H | BOILER C CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | Unknown/no sensor: BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS | BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS
BOILER_C_SH_PERFORMANCE | BOILER C SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(BOILER_C_SH_SPECIFIC_DUTY)/0.110075721*100) | Unknown/no sensor: BOILER_C_SH_SPECIFIC_DUTY ¦ BOILER_C_STATUS | BOILER_C_SH_SPECIFIC_DUTY ¦ BOILER_C_STATUS
BOILER_C_ENERGY_GAINED | BOILER C ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY) | Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_CONVECTION_DUTY | BOILER C CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY+BOILER_C_SH_DUTY+BOILER_C_STACK_LOSS_CORRECTED) | Unknown/no sensor: BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_SH_DUTY ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_SH_DUTY ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_C_STATUS
BOILER_C_RADIATION_DUTY | BOILER C RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_ENERGY_GAINED-BOILER_C_CONVECTION_DUTY) | Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS
BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER C PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS
BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER C PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_C_ENERGY_GAINED ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS | BOILER_C_ENERGY_GAINED ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS
BOILER_C_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER C RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | Unknown/no sensor: BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_C_STATUS | BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_C_STATUS
BOILER_C_RADIATION_SECTION_EFFICIENCY | BOILER C RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS
BOILER_C_CONVECTION_SECTION_EFFICIENCY | BOILER C CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS
BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER D FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | NORMALIZED BOILER D FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER D FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER D FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL)*100 | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER_D_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER D FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_CO2_CONCENTRATION | NORMALIZED BOILER D FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | NORMALIZED BOILER D FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | NORMALIZED BOILER D FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | NORMALIZED BOILER D FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | NORMALIZED BOILER D FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | NORMALIZED BOILER D FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER D FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_D_FG_MW | BOILER D FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_D_FG_NC5_C | Unknown/no sensor: NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION
BOILER_D_FG_CH4_MASS_PERCENTAGE | BOILER D FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION
BOILER_D_FG_ETHANE_MASS_PERCENTAGE | BOILER D FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION
BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE | BOILER D FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION
BOILER_D_FG_PROPANE_MASS_PERCENTAGE | BOILER D FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION
BOILER_D_FG_NITROGEN_MASS_PERCENTAGE | BOILER D FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_N2_CONCENTRATION
BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE | BOILER D FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION
BOILER_D_FG_IC4_MASS_PERCENTAGE | BOILER D FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION
BOILER_D_FG_NC4_MASS_PERCENTAGE | BOILER D FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION
BOILER_D_FG_NC5_MASS_PERCENTAGE | BOILER D FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION
BOILER_D_FG_IC5_MASS_PERCENTAGE | BOILER D FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION
BOILER_D_FG_DENSITY | BOILER D FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_MW/22.414 | Unknown/no sensor: BOILER_D_FG_MW | BOILER_D_FG_MW
BOILER_D_LHV_DESIGEN | BOILER D LHV DESIGEN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_D_FG_DENSITY)/1000 | Unknown/no sensor: BOILER_D_FG_DENSITY | BOILER_D_FG_DENSITY
BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER D TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_PERCENTAGE+BOILER_D_FG_ETHANE_MASS_PERCENTAGE+BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_D_FG_PROPANE_MASS_PERCENTAGE+BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_D_FG_NITROGEN_MASS_PERCENTAGE+BOILER_D_FG_IC4_MASS_PERCENTAGE+BOILER_D_FG_NC4_MASS_PERCENTAGE+BOILER_D_FG_NC5_MASS_PERCENTAGE+BOILER_D_FG_IC5_MASS_PERCENTAGE | Unknown/no sensor: BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_FG_IC4_MASS_PERCENTAGE | BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_FG_IC4_MASS_PERCENTAGE ¦ BOILER_D_FG_IC5_MASS_PERCENTAGE ¦ BOILER_D_FG_NC4_MASS_PERCENTAGE ¦ BOILER_D_FG_NC5_MASS_PERCENTAGE ¦ BOILER_D_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_D_FG_PROPANE_MASS_PERCENTAGE
BOILER_D_FG_CH4_MASS_FRACTION | BOILER D FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER D FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER D FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER D FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NITROGEN_MASS_FRACTION | BOILER D FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER D FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_IC4_MASS_FRACTION | BOILER D FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_IC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NC4_MASS_FRACTION | BOILER D FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_NC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NC5_MASS_FRACTION | BOILER D FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_NC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_IC5_MASS_FRACTION | BOILER D FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_D_FG_IC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_LHV | BOILER D LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (BOILER_D_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_D_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_D_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_D_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_D_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_D_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_D_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_D_FG_NC5_MASS_FRAC | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION ¦ BOILER_D_FG_NC4_MASS_FRACTION ¦ BOILER_D_FG_NC5_MASS_FRACTION ¦ BOILER_D_FG_NITROGEN_MASS_FRACTION ¦ BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER D AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*34.344 | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER D AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*17.265 | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*14.807 | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER D AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*15.703 | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER D AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER D AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER D AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER D AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_H2_CO2_COMBUSTION | BOILER D H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*0 | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_CH4_CO2_COMBUSTION | BOILER D CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*2.744 | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_ETHANE_CO2_COMBUSTION | BOILER D ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*2.927 | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHYLENE_CO2_COMBUSTION | BOILER D ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*3.138 | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_PROPANE_CO2_COMBUSTION | BOILER D PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*2.994 | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_NC4_CO2_COMBUSTION | BOILER D NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_IC4_CO2_COMBUSTION | BOILER D IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_NC5_CO2_COMBUSTION | BOILER D NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_IC5_CO2_COMBUSTION | BOILER D IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_H2_N2_COMBUSTION | BOILER D H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*26.407 | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_CH4_N2_COMBUSTION | BOILER D CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*13.275 | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_ETHANE_N2_COMBUSTION | BOILER D ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*12.394 | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHYLENE_N2_COMBUSTION | BOILER D ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*11.385 | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_PROPANE_N2_COMBUSTION | BOILER D PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*12.074 | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_IC4_N2_COMBUSTION | BOILER D IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_NC4_N2_COMBUSTION | BOILER D NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_IC5_N2_COMBUSTION | BOILER D IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_NC5_N2_COMBUSTION | BOILER D NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_H2_H2O_COMBUSTION | BOILER D H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*8.937 | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_CH4_H2O_COMBUSTION | BOILER D CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*2.246 | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_ETHANE_H2O_COMBUSTION | BOILER D ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*1.798 | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHYLENE_H2O_COMBUSTION | BOILER D ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*1.285 | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_PROPANE_H2O_COMBUSTION | BOILER D PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*1.634 | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_IC4_H2O_COMBUSTION | BOILER D IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_NC4_H2O_COMBUSTION | BOILER D NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_IC5_H2O_COMBUSTION | BOILER D IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_NC5_H2O_COMBUSTION | BOILER D NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER D AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_D_AI | Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_D_CO2_FORMED | BOILER D CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_CH4_CO2_COMBUSTION+BOILER_D_ETHANE_CO2_COMBUSTION+BOILER_D_ETHYLENE_CO2_COMBUSTION+BOILER_D_PROPANE_CO2_COMBUSTION+BOILER_D_NC4_CO2_COMBUSTION+BOILER_D_IC4_CO2_COMBUSTION+BOILER_D_NC5_CO2_COMBUSTION+BOILER_D_IC5_CO2_COMBUSTION | Unknown/no sensor: BOILER_D_CH4_CO2_COMBUSTION ¦ BOILER_D_ETHANE_CO2_COMBUSTION ¦ BOILER_D_ETHYLENE_CO2_COMBUSTION ¦ BOILER_D_IC4_CO2_COMBUSTION ¦ BOILER_D_IC5_CO2_COMBUSTION | BOILER_D_CH4_CO2_COMBUSTION ¦ BOILER_D_ETHANE_CO2_COMBUSTION ¦ BOILER_D_ETHYLENE_CO2_COMBUSTION ¦ BOILER_D_IC4_CO2_COMBUSTION ¦ BOILER_D_IC5_CO2_COMBUSTION ¦ BOILER_D_NC4_CO2_COMBUSTION ¦ BOILER_D_NC5_CO2_COMBUSTION ¦ BOILER_D_PROPANE_CO2_COMBUSTION
BOILER_D_N2_FORMED | BOILER D N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_H2_N2_COMBUSTION+BOILER_D_CH4_N2_COMBUSTION+BOILER_D_ETHANE_N2_COMBUSTION+BOILER_D_ETHYLENE_N2_COMBUSTION+BOILER_D_PROPANE_N2_COMBUSTION+BOILER_D_IC4_N2_COMBUSTION+BOILER_D_NC4_N2_COMBUSTION+BOILER_D_IC5_N2_COMBUSTION+BOILER_D_NC5_N2_COMBUSTION | Unknown/no sensor: BOILER_D_CH4_N2_COMBUSTION ¦ BOILER_D_ETHANE_N2_COMBUSTION ¦ BOILER_D_ETHYLENE_N2_COMBUSTION ¦ BOILER_D_H2_N2_COMBUSTION ¦ BOILER_D_IC4_N2_COMBUSTION | BOILER_D_CH4_N2_COMBUSTION ¦ BOILER_D_ETHANE_N2_COMBUSTION ¦ BOILER_D_ETHYLENE_N2_COMBUSTION ¦ BOILER_D_H2_N2_COMBUSTION ¦ BOILER_D_IC4_N2_COMBUSTION ¦ BOILER_D_IC5_N2_COMBUSTION ¦ BOILER_D_NC4_N2_COMBUSTION ¦ BOILER_D_NC5_N2_COMBUSTION ¦ BOILER_D_PROPANE_N2_COMBUSTION
BOILER_D_H2O_FORMED | BOILER D H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_H2_H2O_COMBUSTION+BOILER_D_CH4_H2O_COMBUSTION+BOILER_D_ETHANE_H2O_COMBUSTION+BOILER_D_ETHYLENE_H2O_COMBUSTION+BOILER_D_PROPANE_H2O_COMBUSTION+BOILER_D_IC4_H2O_COMBUSTION+BOILER_D_NC4_H2O_COMBUSTION+BOILER_D_IC5_H2O_COMBUSTION+BOILER_D_NC5_H2O_COMBUSTION | Unknown/no sensor: BOILER_D_CH4_H2O_COMBUSTION ¦ BOILER_D_ETHANE_H2O_COMBUSTION ¦ BOILER_D_ETHYLENE_H2O_COMBUSTION ¦ BOILER_D_H2_H2O_COMBUSTION ¦ BOILER_D_IC4_H2O_COMBUSTION | BOILER_D_CH4_H2O_COMBUSTION ¦ BOILER_D_ETHANE_H2O_COMBUSTION ¦ BOILER_D_ETHYLENE_H2O_COMBUSTION ¦ BOILER_D_H2_H2O_COMBUSTION ¦ BOILER_D_IC4_H2O_COMBUSTION ¦ BOILER_D_IC5_H2O_COMBUSTION ¦ BOILER_D_NC4_H2O_COMBUSTION ¦ BOILER_D_NC5_H2O_COMBUSTION ¦ BOILER_D_PROPANE_H2O_COMBUSTION
BOILER_D_CORRECTED_COMBUSTION_AIR | BOILER D CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_D_AIR_MOISTURE) | Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_D_CORRECTED_COMBUTION_H2O_FORMED | BOILER D CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_H2O_FORMED+(BOILER_D_CORRECTED_COMBUSTION_AIR-BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_H2O_FORMED | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_H2O_FORMED
BOILER_D_EXCESS_AIR | BOILER D EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_D_FLUE_GAS_OXGYGEN)*((BOILER_D_N2_FORMED/28.01)+(BOILER_D_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_D_CO2_FORMED/44.01))/(20.95-BOILER_D_FLUE_GAS_OXGYGEN)) | PI exists but NOT in hierarchy: BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV]; Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_D_N2_FORMED | BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV] ¦ BOILER_D_CO2_FORMED ¦ BOILER_D_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_D_N2_FORMED
BOILER_D_AIR_FUEL_MASS_RATIO | BOILER D AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_EXCESS_AIR+BOILER_D_CORRECTED_COMBUSTION_AIR | Unknown/no sensor: BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_EXCESS_AIR | BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_EXCESS_AIR
BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER D TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_AIR_MOISTURE | Unknown/no sensor: BOILER_D_AIR_FUEL_MASS_RATIO | BOILER_D_AIR_FUEL_MASS_RATIO
BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER D TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_TOTAL_MOISTURE_WITH_AIR+BOILER_D_H2O_FORMED | Unknown/no sensor: BOILER_D_H2O_FORMED ¦ BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER_D_H2O_FORMED ¦ BOILER_D_TOTAL_MOISTURE_WITH_AIR
BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER D CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | PI exists but NOT in hierarchy: BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] | BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV]
BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER D AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_AIR_CP_REF_T+BOILER_D_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | Unknown/no sensor: BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER_D_CP_AT_COMBUSTION_TEMPERATURE
BOILER_D_CP_H2_FUEL_TEMP | BOILER D CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_CH4_FUEL_TEMP | BOILER D CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_ETHANE_FUEL_TEMP | BOILER D CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_PROPANE_FUEL_TEMP | BOILER D CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_ETHYLENE_FUEL_TEMP | BOILER D CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_NC4_FUEL_TEMP | BOILER D CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_IC4_FUEL_TEMP | BOILER D CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_NC5_FUEL_TEMP | BOILER D CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_IC5_FUEL_TEMP | BOILER D CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER D CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_D_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_D_FG_NC4_MASS_FRACTION/COMPONENT | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION ¦ BOILER_D_FG_MW ¦ BOILER_D_FG_NC4_MASS_FRACTION ¦ BOILER_D_FG_NC5_MASS_FRACTION ¦ BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER D CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_D_CP_H2_FUEL_TEMP+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_D_CP_CH4_FUEL_TEMP+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_D_CP_ETHYLENE_FUEL_TEMP+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_D_CP_ETHANE_FUEL_TEMP+(BOILER_D_FG_P | Unknown/no sensor: BOILER_D_CP_CH4_FUEL_TEMP ¦ BOILER_D_CP_ETHANE_FUEL_TEMP ¦ BOILER_D_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_D_CP_H2_FUEL_TEMP ¦ BOILER_D_CP_IC4_FUEL_TEMP (+9 more) | BOILER_D_CP_CH4_FUEL_TEMP ¦ BOILER_D_CP_ETHANE_FUEL_TEMP ¦ BOILER_D_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_D_CP_H2_FUEL_TEMP ¦ BOILER_D_CP_IC4_FUEL_TEMP ¦ BOILER_D_CP_IC5_FUEL_TEMP ¦ BOILER_D_CP_NC4_FUEL_TEMP ¦ BOILER_D_CP_NC5_FUEL_TEMP ¦ BOILER_D_CP_PROPANE_FUEL_TEMP ¦ BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION ¦ BOILER_D_FG_MW ¦ BOILER_D_FG_NC4_MASS_FRACTION ¦ BOILER_D_FG_NC5_MASS_FRACTION ¦ BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER D AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_D_FG_MW)/2 | Unknown/no sensor: BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_D_FG_MW | BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_D_FG_MW
BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_D_EXCESS_AIR*(1-BOILER_D_AIR_MOISTURE)+BOILER_D_N2_FORMED+BOILER_D_CO2_FORMED | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_N2_FORMED
BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | Unknown/no sensor: BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_FLUE_GAS_MW | BOILER D FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_D_CO2_FORMED/44.01+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.96) | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER D AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_D_CO2_FORMED/44.01+BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.85*BOILER_D_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_D_FLUE_GAS_MW)/BOILER_D_FLUE_GAS_MW | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_MW ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_MW ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED
BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER D SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]; Unknown/no sensor: BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] ¦ BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER D SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_D_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_D_AIR_FUEL_MASS_RATIO | PI exists but NOT in hierarchy: BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV]; Unknown/no sensor: BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_D_AIR_FUEL_MASS_RATIO | BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] ¦ BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_D_AIR_FUEL_MASS_RATIO
BOILER_D_MIXED_LHV_PER_KG | BOILER D MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER D TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_D_MIXED_LHV_PER_KG) | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER D HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_D_STACK_TEMPERATURE-15.6)))) | Unknown/no sensor: BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS | BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER D HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,9*(BOILER_D_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_D_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_D_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_STATUS | BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER D HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_D_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER D HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,0*10^-6*28*5654*BOILER_D_BOILER_LOAD) | Unknown/no sensor: BOILER_D_STATUS | BOILER_D_STATUS
BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER D TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | Unknown/no sensor: BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_D_STATUS | BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_D_STATUS
BOILER_D_RADIATION_LOSSES | BOILER D RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_MIXED_LHV_PER_KG*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOAD^2-0.0899*BOILER_D_BOILER_LOAD+3.2426)/100) | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER D TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_D_RADIATION_LOSSES) | Unknown/no sensor: BOILER_D_RADIATION_LOSSES ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_RADIATION_LOSSES ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER D TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_D_BOILER_INDIRECT_EFFICIENCY | BOILER D BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_D_HP_STEAM_ENTHALPY | BOILER D HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_D)+2.66244961166282*DESUPERHEATER_D_OUTLET_TEMPERATURE)*0.239+2) | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV] ¦ BOILER_A_STATUS
BOILER_D_TOTAL_STEAM_ENERGY | BOILER D TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_HP_STEAM_ENTHALPY/1000000) | Unknown/no sensor: BOILER_D_HP_STEAM_ENTHALPY ¦ BOILER_D_STATUS | BOILER_D_HP_STEAM_ENTHALPY ¦ BOILER_D_STATUS
BOILER_D_BFW_ENTHALPY | BOILER D BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_D_INLET_TEMPERATURE) | PI exists but NOT in hierarchy: ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ BOILER_A_STATUS
BOILER_D_CORRECTED_BFW_FLOW | BOILER D CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-DESUPERHEATER_D_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_D))/1000) | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_D[sensor:UN.UO.71FI1402.PV] ¦ BFW_FLOW_TO_ECONOMIZER_D[sensor:UN.UO.71FI1403.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV]; Unknown/no sensor: BOILER_D_STATUS | BFW_FLOW_TO_DESUPERHEATER_D[sensor:UN.UO.71FI1402.PV] ¦ BFW_FLOW_TO_ECONOMIZER_D[sensor:UN.UO.71FI1403.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV] ¦ BOILER_D_STATUS
BOILER_D_BFW_ENERGY | BOILER D BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*BOILER_D_BFW_ENTHALPY/1000) | Unknown/no sensor: BOILER_D_BFW_ENTHALPY ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS | BOILER_D_BFW_ENTHALPY ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS
BOILER_D_FUEL_GAS_ENERGY_INPUT | BOILER D FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FG_FLOW_RATE*1000*BOILER_D_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_STEAM_DRUM_TEMP | BOILER D STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,4.02521999671835*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | PI exists but NOT in hierarchy: BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV]; Unknown/no sensor: BOILER_D_STATUS | BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_STATUS
BOILER_D_BLOWDOWN_LOSS | BOILER D BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,((CBD_BLOW_DOWN_D/1000)*((BOILER_D_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV]; Unknown/no sensor: BOILER_D_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV] ¦ BOILER_D_STATUS
BOILER_D_TOTAL_FLUE_GAS_GENERATED | BOILER D TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW/1000*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS
BOILER_D_STACK_LOSS | BOILER D STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_FLOW/(1000*1000)) | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_CORRECTED_FUEL_FLOW | BOILER D CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW-((BOILER_D_FUEL_GAS_ENERGY_INPUT-(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY+BOILER_D_BLOWDOWN_LOSS+BOILER_D_STACK_LOSS+BOILER_D_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_D_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOAD^2-0.0899*BOILER_D_BOILER_LOAD+3.2426)/100+(BOILE | Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_MIXED_LHV_PER_KG | BOILER_D_BFW_ENERGY ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STACK_LOSS ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_FUEL_CONSUMPTION | BOILER D FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER D SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)) | Unknown/no sensor: BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER D SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)*4.184) | Unknown/no sensor: BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS
BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER D CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_THERMAL_EFFICIENCY | BOILER D THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY)/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER D EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_BLOWDOWN_LOSS/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS | BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS
BOILER_D_ECONOMIZER_DUTY | BOILER D ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_D_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_D_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV]; Unknown/no sensor: BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV] ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS
BOILER_D_LMTD_ECONOMIZER | BOILER D LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,((673-ECONOMIZER_D_OUTLET_TEMPERATURE)-(BOILER_D_STACK_TEMPERATURE-ECONOMIZER_D_INLET_TEMPERATURE))/ln((673-ECONOMIZER_D_OUTLET_TEMPERATURE)/(-ECONOMIZER_D_INLET_TEMPERATURE+BOILER_D_STACK_TEMPERATURE))) | PI exists but NOT in hierarchy: ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV]; Unknown/no sensor: BOILER_D_STATUS | ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV] ¦ BOILER_D_STATUS
BOILER_D_UA_ECONOMIZER | BOILER D UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY/BOILER_D_LMTD_ECONOMIZER) | Unknown/no sensor: BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_LMTD_ECONOMIZER ¦ BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_LMTD_ECONOMIZER ¦ BOILER_D_STATUS
BOILER_D_FOULING_INDEX | BOILER D FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,1/BOILER_D_UA_ECONOMIZER) | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_UA_ECONOMIZER | BOILER_D_STATUS ¦ BOILER_D_UA_ECONOMIZER
BOILER_D_SH_DUTY | BOILER D SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_D_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_D_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | PI exists but NOT in hierarchy: BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV]; Unknown/no sensor: BOILER_D_STATUS | BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV] ¦ BOILER_D_STATUS
BOILER_D_SH_SPECIFIC_DUTY | BOILER D SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_SH_DUTY/DESUPERHEATER_D_OUTLET_STEAM_FLOW*1000) | Unknown/no sensor: BOILER_D_SH_DUTY ¦ BOILER_D_STATUS | BOILER_D_SH_DUTY ¦ BOILER_D_STATUS
BOILER_D_FUEL_GAS_CORRECTED_TPH | BOILER D FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW/1000) | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS
BOILER_D_TOTAL_FLUE_GAS_CORRECTED | BOILER D TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_CORRECTED_TPH*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS
BOILER_D_STACK_LOSS_CORRECTED | BOILER D STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_CORRECTED_TPH/1000) | Unknown/no sensor: BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_SUPERHEATED_STEAM_BFW_RATIO | BOILER D SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(DESUPERHEATER_D_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_D)/(BOILER_D_CORRECTED_BFW_FLOW*1000)) | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV]; Unknown/no sensor: BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS | CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV] ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS
BOILER_D_CO2_EMISSIONS | BOILER D CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CO2_FORMED*BOILER_D_FUEL_GAS_CORRECTED_TPH) | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS | BOILER_D_CO2_FORMED ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS
BOILER_D_CALCULATED_AIRFLOW_NM3H | BOILER D CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | Unknown/no sensor: BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS | BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS
BOILER_D_SH_PERFORMANCE | BOILER D SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(BOILER_D_SH_SPECIFIC_DUTY)/0.110075721*100) | Unknown/no sensor: BOILER_D_SH_SPECIFIC_DUTY ¦ BOILER_D_STATUS | BOILER_D_SH_SPECIFIC_DUTY ¦ BOILER_D_STATUS
BOILER_D_ENERGY_GAINED | BOILER D ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY) | Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_CONVECTION_DUTY | BOILER D CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY+BOILER_D_SH_DUTY+BOILER_D_STACK_LOSS_CORRECTED) | Unknown/no sensor: BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_SH_DUTY ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_SH_DUTY ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_D_STATUS
BOILER_D_RADIATION_DUTY | BOILER D RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_ENERGY_GAINED-BOILER_D_CONVECTION_DUTY) | Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS
BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER D PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS
BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER D PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_D_ENERGY_GAINED ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS | BOILER_D_ENERGY_GAINED ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS
BOILER_D_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER D RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | Unknown/no sensor: BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_D_STATUS | BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_D_STATUS
BOILER_D_RADIATION_SECTION_EFFICIENCY | BOILER D RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS
BOILER_D_CONVECTION_SECTION_EFFICIENCY | BOILER D CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS
BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER E FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | NORMALIZED BOILER E FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER E FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER E FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL)*100 | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER_E_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER E FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_CO2_CONCENTRATION | NORMALIZED BOILER E FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | NORMALIZED BOILER E FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | NORMALIZED BOILER E FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | NORMALIZED BOILER E FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | NORMALIZED BOILER E FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | NORMALIZED BOILER E FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER E FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_E_FG_MW | BOILER E FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_E_FG_NC5_C | Unknown/no sensor: NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION
BOILER_E_FG_CH4_MASS_PERCENTAGE | BOILER E FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION
BOILER_E_FG_ETHANE_MASS_PERCENTAGE | BOILER E FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION
BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE | BOILER E FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION
BOILER_E_FG_PROPANE_MASS_PERCENTAGE | BOILER E FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION
BOILER_E_FG_NITROGEN_MASS_PERCENTAGE | BOILER E FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_N2_CONCENTRATION
BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE | BOILER E FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION
BOILER_E_FG_IC4_MASS_PERCENTAGE | BOILER E FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION
BOILER_E_FG_NC4_MASS_PERCENTAGE | BOILER E FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION
BOILER_E_FG_NC5_MASS_PERCENTAGE | BOILER E FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION
BOILER_E_FG_IC5_MASS_PERCENTAGE | BOILER E FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION
BOILER_E_FG_DENSITY | BOILER E FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_MW/22.414 | Unknown/no sensor: BOILER_E_FG_MW | BOILER_E_FG_MW
BOILER_E_LHV_DESIGN | BOILER E LHV DESIGN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_E_FG_DENSITY)/1000 | Unknown/no sensor: BOILER_E_FG_DENSITY | BOILER_E_FG_DENSITY
BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER E TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_PERCENTAGE+BOILER_E_FG_ETHANE_MASS_PERCENTAGE+BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_E_FG_PROPANE_MASS_PERCENTAGE+BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_E_FG_NITROGEN_MASS_PERCENTAGE+BOILER_E_FG_IC4_MASS_PERCENTAGE+BOILER_E_FG_NC4_MASS_PERCENTAGE+BOILER_E_FG_NC5_MASS_PERCENTAGE+BOILER_E_FG_IC5_MASS_PERCENTAGE | Unknown/no sensor: BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_FG_IC4_MASS_PERCENTAGE | BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_FG_IC4_MASS_PERCENTAGE ¦ BOILER_E_FG_IC5_MASS_PERCENTAGE ¦ BOILER_E_FG_NC4_MASS_PERCENTAGE ¦ BOILER_E_FG_NC5_MASS_PERCENTAGE ¦ BOILER_E_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_E_FG_PROPANE_MASS_PERCENTAGE
BOILER_E_FG_CH4_MASS_FRACTION | BOILER E FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER E FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER E FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER E FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NITROGEN_MASS_FRACTION | BOILER E FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER E FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_IC4_MASS_FRACTION | BOILER E FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_IC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NC4_MASS_FRACTION | BOILER E FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_NC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NC5_MASS_FRACTION | BOILER E FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_NC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_IC5_MASS_FRACTION | BOILER E FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | Unknown/no sensor: BOILER_E_FG_IC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_LHV | BOILER E LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (BOILER_E_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_E_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_E_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_E_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_E_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_E_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_E_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_E_FG_NC5_MASS_FRAC | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION ¦ BOILER_E_FG_NC4_MASS_FRACTION ¦ BOILER_E_FG_NC5_MASS_FRACTION ¦ BOILER_E_FG_NITROGEN_MASS_FRACTION ¦ BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER E AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*34.344 | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER E AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*17.265 | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*14.807 | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER E AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*15.703 | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER E AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER E AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*15.487 | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER E AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER E AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*15.353 | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_H2_CO2_COMBUSTION | BOILER E H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*0 | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_CH4_CO2_COMBUSTION | BOILER E CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*2.744 | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_ETHANE_CO2_COMBUSTION | BOILER E ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_FRACTION*2.927 | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHYLENE_CO2_COMBUSTION | BOILER E ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*3.138 | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_PROPANE_CO2_COMBUSTION | BOILER E PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*2.994 | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_NC4_CO2_COMBUSTION | BOILER E NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_IC4_CO2_COMBUSTION | BOILER E IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*3.029 | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_NC5_CO2_COMBUSTION | BOILER E NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_IC5_CO2_COMBUSTION | BOILER E IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*3.05 | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_H2_N2_COMBUSTION | BOILER E H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*26.407 | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_CH4_N2_COMBUSTION | BOILER E CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*13.275 | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_ETHANE_N2_COMBUSTION | BOILER E ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_FRACTION*12.394 | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHYLENE_N2_COMBUSTION | BOILER E ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*11.385 | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_PROPANE_N2_COMBUSTION | BOILER E PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*12.074 | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_IC4_N2_COMBUSTION | BOILER E IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_NC4_N2_COMBUSTION | BOILER E NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*11.908 | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_IC5_N2_COMBUSTION | BOILER E IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_NC5_N2_COMBUSTION | BOILER E NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*11.805 | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_H2_H2O_COMBUSTION | BOILER E H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*8.937 | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_CH4_H2O_COMBUSTION | BOILER E CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*2.246 | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_ETHANE_H2O_COMBUSTION | BOILER E ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_FRACTION*1.798 | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHYLENE_H2O_COMBUSTION | BOILER E ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*1.285 | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_PROPANE_H2O_COMBUSTION | BOILER E PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*1.634 | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_IC4_H2O_COMBUSTION | BOILER E IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_NC4_H2O_COMBUSTION | BOILER E NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*1.55 | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_IC5_H2O_COMBUSTION | BOILER E IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_NC5_H2O_COMBUSTION | BOILER E NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*1.498 | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER E AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_E_AI | Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_E_CO2_FORMED | BOILER E CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_CH4_CO2_COMBUSTION+BOILER_E_ETHANE_CO2_COMBUSTION+BOILER_E_ETHYLENE_CO2_COMBUSTION+BOILER_E_PROPANE_CO2_COMBUSTION+BOILER_E_NC4_CO2_COMBUSTION+BOILER_E_IC4_CO2_COMBUSTION+BOILER_E_NC5_CO2_COMBUSTION+BOILER_E_IC5_CO2_COMBUSTION | Unknown/no sensor: BOILER_E_CH4_CO2_COMBUSTION ¦ BOILER_E_ETHANE_CO2_COMBUSTION ¦ BOILER_E_ETHYLENE_CO2_COMBUSTION ¦ BOILER_E_IC4_CO2_COMBUSTION ¦ BOILER_E_IC5_CO2_COMBUSTION | BOILER_E_CH4_CO2_COMBUSTION ¦ BOILER_E_ETHANE_CO2_COMBUSTION ¦ BOILER_E_ETHYLENE_CO2_COMBUSTION ¦ BOILER_E_IC4_CO2_COMBUSTION ¦ BOILER_E_IC5_CO2_COMBUSTION ¦ BOILER_E_NC4_CO2_COMBUSTION ¦ BOILER_E_NC5_CO2_COMBUSTION ¦ BOILER_E_PROPANE_CO2_COMBUSTION
BOILER_E_N2_FORMED | BOILER E N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_H2_N2_COMBUSTION+BOILER_E_CH4_N2_COMBUSTION+BOILER_E_ETHANE_N2_COMBUSTION+BOILER_E_ETHYLENE_N2_COMBUSTION+BOILER_E_PROPANE_N2_COMBUSTION+BOILER_E_IC4_N2_COMBUSTION+BOILER_E_NC4_N2_COMBUSTION+BOILER_E_IC5_N2_COMBUSTION+BOILER_E_NC5_N2_COMBUSTION | Unknown/no sensor: BOILER_E_CH4_N2_COMBUSTION ¦ BOILER_E_ETHANE_N2_COMBUSTION ¦ BOILER_E_ETHYLENE_N2_COMBUSTION ¦ BOILER_E_H2_N2_COMBUSTION ¦ BOILER_E_IC4_N2_COMBUSTION | BOILER_E_CH4_N2_COMBUSTION ¦ BOILER_E_ETHANE_N2_COMBUSTION ¦ BOILER_E_ETHYLENE_N2_COMBUSTION ¦ BOILER_E_H2_N2_COMBUSTION ¦ BOILER_E_IC4_N2_COMBUSTION ¦ BOILER_E_IC5_N2_COMBUSTION ¦ BOILER_E_NC4_N2_COMBUSTION ¦ BOILER_E_NC5_N2_COMBUSTION ¦ BOILER_E_PROPANE_N2_COMBUSTION
BOILER_E_H2O_FORMED | BOILER E H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_H2_H2O_COMBUSTION+BOILER_E_CH4_H2O_COMBUSTION+BOILER_E_ETHANE_H2O_COMBUSTION+BOILER_E_ETHYLENE_H2O_COMBUSTION+BOILER_E_PROPANE_H2O_COMBUSTION+BOILER_E_IC4_H2O_COMBUSTION+BOILER_E_NC4_H2O_COMBUSTION+BOILER_E_IC5_H2O_COMBUSTION+BOILER_E_NC5_H2O_COMBUSTION | Unknown/no sensor: BOILER_E_CH4_H2O_COMBUSTION ¦ BOILER_E_ETHANE_H2O_COMBUSTION ¦ BOILER_E_ETHYLENE_H2O_COMBUSTION ¦ BOILER_E_H2_H2O_COMBUSTION ¦ BOILER_E_IC4_H2O_COMBUSTION | BOILER_E_CH4_H2O_COMBUSTION ¦ BOILER_E_ETHANE_H2O_COMBUSTION ¦ BOILER_E_ETHYLENE_H2O_COMBUSTION ¦ BOILER_E_H2_H2O_COMBUSTION ¦ BOILER_E_IC4_H2O_COMBUSTION ¦ BOILER_E_IC5_H2O_COMBUSTION ¦ BOILER_E_NC4_H2O_COMBUSTION ¦ BOILER_E_NC5_H2O_COMBUSTION ¦ BOILER_E_PROPANE_H2O_COMBUSTION
BOILER_E_CORRECTED_COMBUSTION_AIR | BOILER E CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_E_AIR_MOISTURE) | Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_E_CORRECTED_COMBUTION_H2O_FORMED | BOILER E CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_H2O_FORMED+(BOILER_E_CORRECTED_COMBUSTION_AIR-BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_H2O_FORMED | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_H2O_FORMED
BOILER_E_EXCESS_AIR | BOILER E EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_E_FLUE_GAS_OXGYGEN_NEW)*((BOILER_E_N2_FORMED/28.01)+(BOILER_E_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_E_CO2_FORMED/44.01))/(20.95-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | PI exists but NOT in hierarchy: BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV]; Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_E_N2_FORMED | BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILER_E_CO2_FORMED ¦ BOILER_E_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_E_N2_FORMED
BOILER_E_AIR_FUEL_MASS_RATIO | BOILER E AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_EXCESS_AIR+BOILER_E_CORRECTED_COMBUSTION_AIR | Unknown/no sensor: BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_EXCESS_AIR | BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_EXCESS_AIR
BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER E TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_AIR_MOISTURE | Unknown/no sensor: BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_E_AIR_FUEL_MASS_RATIO
BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER E TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_TOTAL_MOISTURE_WITH_AIR+BOILER_E_H2O_FORMED | Unknown/no sensor: BOILER_E_H2O_FORMED ¦ BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER_E_H2O_FORMED ¦ BOILER_E_TOTAL_MOISTURE_WITH_AIR
BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER E CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)-9.647459*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2+16.63537*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^3+(0.000117/((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)+57.86644*((BOILER_E_COMBUSTION_AIR | PI exists but NOT in hierarchy: BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV] | BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV]
BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER E AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_AIR_CP_REF_T+BOILER_E_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | Unknown/no sensor: BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER_E_CP_AT_COMBUSTION_TEMPERATURE
BOILER_E_CP_H2_FUEL_TEMP | BOILER E CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_CH4_FUEL_TEMP | BOILER E CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_ETHANE_FUEL_TEMP | BOILER E CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_PROPANE_FUEL_TEMP | BOILER E CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_ETHYLENE_FUEL_TEMP | BOILER E CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_NC4_FUEL_TEMP | BOILER E CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_IC4_FUEL_TEMP | BOILER E CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_NC5_FUEL_TEMP | BOILER E CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_IC5_FUEL_TEMP | BOILER E CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER E CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_E_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_E_FG_NC4_MASS_FRACTION/COMPONENT | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION ¦ BOILER_E_FG_MW ¦ BOILER_E_FG_NC4_MASS_FRACTION ¦ BOILER_E_FG_NC5_MASS_FRACTION ¦ BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER E CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_E_CP_H2_FUEL_TEMP+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_E_CP_CH4_FUEL_TEMP+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_E_CP_ETHYLENE_FUEL_TEMP+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_E_CP_ETHANE_FUEL_TEMP+(BOILER_E_FG_P | Unknown/no sensor: BOILER_E_CP_CH4_FUEL_TEMP ¦ BOILER_E_CP_ETHANE_FUEL_TEMP ¦ BOILER_E_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_E_CP_H2_FUEL_TEMP ¦ BOILER_E_CP_IC4_FUEL_TEMP (+9 more) | BOILER_E_CP_CH4_FUEL_TEMP ¦ BOILER_E_CP_ETHANE_FUEL_TEMP ¦ BOILER_E_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_E_CP_H2_FUEL_TEMP ¦ BOILER_E_CP_IC4_FUEL_TEMP ¦ BOILER_E_CP_IC5_FUEL_TEMP ¦ BOILER_E_CP_NC4_FUEL_TEMP ¦ BOILER_E_CP_NC5_FUEL_TEMP ¦ BOILER_E_CP_PROPANE_FUEL_TEMP ¦ BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION ¦ BOILER_E_FG_MW ¦ BOILER_E_FG_NC4_MASS_FRACTION ¦ BOILER_E_FG_NC5_MASS_FRACTION ¦ BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER E AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_E_FG_MW)/2 | Unknown/no sensor: BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_E_FG_MW | BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_E_FG_MW
BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_E_EXCESS_AIR*(1-BOILER_E_AIR_MOISTURE)+BOILER_E_N2_FORMED+BOILER_E_CO2_FORMED | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_N2_FORMED
BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | Unknown/no sensor: BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_FLUE_GAS_MW | BOILER E FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_E_CO2_FORMED/44.01+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.96) | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER E AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_E_CO2_FORMED/44.01+BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.85*BOILER_E_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_E_FLUE_GAS_MW)/BOILER_E_FLUE_GAS_MW | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_MW ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_MW ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED
BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER E SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]; Unknown/no sensor: BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] ¦ BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER E SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_E_COMBUSTION_AIR_TEMP-15.6)*BOILER_E_AIR_FUEL_MASS_RATIO | PI exists but NOT in hierarchy: BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV]; Unknown/no sensor: BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV] ¦ BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_E_AIR_FUEL_MASS_RATIO
BOILER_E_MIXED_LHV_PER_KG | BOILER E MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_LHV) | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER E TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_E_MIXED_LHV_PER_KG) | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG ¦ BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER_E_MIXED_LHV_PER_KG ¦ BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL
BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER E HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_E_STACK_TEMPERATURE-15.6)))) | Unknown/no sensor: BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO
BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER E HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,9*(BOILER_E_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_E_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_E_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER E HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_E_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | Unknown/no sensor: BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER E TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | Unknown/no sensor: BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3
BOILER_E_RADIATION_LOSSES | BOILER E RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_MIXED_LHV_PER_KG*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOILER_LOAD^2-0.0899*BOILER_E_BOILER_LOAD+3.2426)/100) | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER E TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_E_RADIATION_LOSSES) | Unknown/no sensor: BOILER_E_RADIATION_LOSSES ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_RADIATION_LOSSES ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER E TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | Unknown/no sensor: BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_E_BOILER_INDIRECT_EFFICIENCY | BOILER E BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | Unknown/no sensor: BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_E_HP_STEAM_ENTHALPY | BOILER E HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_E)+2.66244961166282*DESUPERHEATER_E_OUTLET_TEMPERATURE)*0.239+2) | Unknown/no sensor: BOILER_A_STATUS | BOILER_A_STATUS
BOILER_E_TOTAL_STEAM_ENERGY | BOILER E TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_HP_STEAM_ENTHALPY/1000000) | Unknown/no sensor: BOILER_E_HP_STEAM_ENTHALPY | BOILER_E_HP_STEAM_ENTHALPY
BOILER_E_BFW_ENTHALPY | BOILER E BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_E_INLET_TEMPERATURE) | PI exists but NOT in hierarchy: ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ BOILER_A_STATUS
BOILER_E_CORRECTED_BFW_FLOW | BOILER E CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-DESUPERHEATER_E_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_E))/1000) | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_E[sensor:UN.UO.71FC1502.PV] ¦ BFW_FLOW_TO_ECONOMIZER_E[sensor:UN.UO.71FC1503.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV] | BFW_FLOW_TO_DESUPERHEATER_E[sensor:UN.UO.71FC1502.PV] ¦ BFW_FLOW_TO_ECONOMIZER_E[sensor:UN.UO.71FC1503.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV]
BOILER_E_BFW_ENERGY | BOILER E BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*BOILER_E_BFW_ENTHALPY/1000) | Unknown/no sensor: BOILER_E_BFW_ENTHALPY ¦ BOILER_E_CORRECTED_BFW_FLOW | BOILER_E_BFW_ENTHALPY ¦ BOILER_E_CORRECTED_BFW_FLOW
BOILER_E_FUEL_GAS_ENERGY_INPUT | BOILER E FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FG_FLOW_RATE*1000*BOILER_E_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
BOILER_E_BLOWDOWN_LOSS | BOILER E BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,((CBD_BLOW_DOWN_E/1000)*((BOILER_E_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_E_STEAM_DRUM_TEMP*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_E_STEAM_DRUM_TEMP*4.22416911685416-3.01717714574329)*0.2390006))/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV] | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV]
BOILER_E_TOTAL_FLUE_GAS_GENERATED | BOILER E TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295/1000*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO
BOILER_E_STACK_LOSS | BOILER E STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_FLOW/1.295/(1000*1000)) | Unknown/no sensor: BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_CORRECTED_FUEL_FLOW | BOILER E CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295-((BOILER_E_FUEL_GAS_ENERGY_INPUT-(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY+BOILER_E_BLOWDOWN_LOSS+BOILER_E_STACK_LOSS+BOILER_E_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_E_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOILER_LOAD^2-0.0899*BOILER_E_BOILER_LOAD+3.2426)/100+ | Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_E_MIXED_LHV_PER_KG | BOILER_E_BFW_ENERGY ¦ BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_E_MIXED_LHV_PER_KG ¦ BOILER_E_STACK_LOSS ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_FUEL_CONSUMPTION | BOILER E FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER E SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)) | Unknown/no sensor: BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER E SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)*4.184) | Unknown/no sensor: BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION
BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER E CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG
BOILER_E_THERMAL_EFFICIENCY | BOILER E THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY)/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER E EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_BLOWDOWN_LOSS/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
BOILER_E_ECONOMIZER_DUTY | BOILER E ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_E_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_E_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV]; Unknown/no sensor: BOILER_E_CORRECTED_BFW_FLOW | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV] ¦ BOILER_E_CORRECTED_BFW_FLOW
BOILER_E_LMTD_ECONOMIZER | BOILER E LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,((673-ECONOMIZER_E_OUTLET_TEMPERATURE)-(BOILER_E_STACK_TEMPERATURE-ECONOMIZER_E_INLET_TEMPERATURE))/ln((673-ECONOMIZER_E_OUTLET_TEMPERATURE)/(-ECONOMIZER_E_INLET_TEMPERATURE+BOILER_E_STACK_TEMPERATURE))) | PI exists but NOT in hierarchy: ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV] | ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV]
BOILER_E_UA_ECONOMIZER | BOILER E UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY/BOILER_E_LMTD_ECONOMIZER) | Unknown/no sensor: BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_LMTD_ECONOMIZER | BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_LMTD_ECONOMIZER
BOILER_E_FOULING_INDEX | BOILER E FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,1/BOILER_E_UA_ECONOMIZER) | Unknown/no sensor: BOILER_E_UA_ECONOMIZER | BOILER_E_UA_ECONOMIZER
BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER E FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW/1000) | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_CORRECTED_FUEL_FLOW
BOILER_E_TOTAL_FLUE_GAS_CORRECTED | BOILER E TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_CORRECTED_TPH*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | Unknown/no sensor: BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH
BOILER_E_STACK_LOSS_CORRECTED | BOILER E STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_CORRECTED_TPH/1000) | Unknown/no sensor: BOILER_E_FUEL_GAS_CORRECTED_TPH ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_FUEL_GAS_CORRECTED_TPH ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER E SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(DESUPERHEATER_E_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_E)/(BOILER_E_CORRECTED_BFW_FLOW*1000)) | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV]; Unknown/no sensor: BOILER_E_CORRECTED_BFW_FLOW | CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV] ¦ BOILER_E_CORRECTED_BFW_FLOW
BOILER_E_CO2_EMISSIONS | BOILER E CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CO2_FORMED*BOILER_E_FUEL_GAS_CORRECTED_TPH) | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_CO2_FORMED ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH
BOILER_E_CALCULATED_AIRFLOW_NM3H | BOILER E CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | Unknown/no sensor: BOILER_E_AIR_FUEL_MASS_RATIO ¦ BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_AIR_FUEL_MASS_RATIO ¦ BOILER_E_CORRECTED_FUEL_FLOW
BOILER_E_ENERGY_GAINED | BOILER E ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY) | Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_CONVECTION_DUTY | BOILER E CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY+BOILER_E_SH_DUTY+BOILER_E_STACK_LOSS_CORRECTED) | Unknown/no sensor: BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_STACK_LOSS_CORRECTED | BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_STACK_LOSS_CORRECTED
BOILER_E_RADIATION_DUTY | BOILER E RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_ENERGY_GAINED-BOILER_E_CONVECTION_DUTY) | Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED
BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER E PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED
BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER E PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_ENERGY_GAINED*100) | Unknown/no sensor: BOILER_E_ENERGY_GAINED ¦ BOILER_E_RADIATION_DUTY | BOILER_E_ENERGY_GAINED ¦ BOILER_E_RADIATION_DUTY
BOILER_E_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER E RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | Unknown/no sensor: BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION
BOILER_E_RADIATION_SECTION_EFFICIENCY | BOILER E RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_RADIATION_DUTY | BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_RADIATION_DUTY
BOILER_E_CONVECTION_SECTION_EFFICIENCY | BOILER E CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_CONVECTION_DUTY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION | OVER ALL SPECIFIC ENERGY CONSUMPTION | GJ/T | LBM_preprocessing_inferred_tags_main | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_D_TOTAL_STEAM_ENERGY*BOILER_D_STATUS+B | Unknown/no sensor: BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS (+4 more) | BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_E_TOTAL_STEAM_ENERGY
TOTAL_STEAM_PRODUCTION | TOTAL STEAM PRODUCTION | T/h | LBM_preprocessing_inferred_tags_main | (DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_STATUS)/1000 | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
TOTAL_STEAM_ENERGY | TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_TOTAL_STEAM_ENERGY+BOILER_B_TOTAL_STEAM_ENERGY+BOILER_C_TOTAL_STEAM_ENERGY+BOILER_D_TOTAL_STEAM_ENERGY+BOILER_E_TOTAL_STEAM_ENERGY | Unknown/no sensor: BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY | BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_OVERALL_EFFICIENCY | BOILER OVERALL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | (BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_BOILER_INDIRECT_EFFICIENCY*BOILER_A_STATUS+BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_BOILER_INDIRECT_EFFICIENCY*BOILER_B_STATUS+BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_BOILER_INDIRECT_EFFICIENCY*BOILER_C_STATUS+BOILER_D_TOTAL_STEAM_ENERGY*BOILER_D_BOILER_INDIRECT_EFFICIENCY*BOILER_D_STATUS+BOILER_E_TOTAL_STEAM_ENERGY*B | Unknown/no sensor: BOILER_A_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_B_STATUS (+5 more) | BOILER_A_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_E_TOTAL_STEAM_ENERGY ¦ TOTAL_STEAM_ENERGY
TOTAL_FUEL_CONSUMPTION_GCAL_H | TOTAL FUEL CONSUMPTION GCAL H | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
TOTAL_STACK_LOSS_GCAL_H | TOTAL STACK LOSS GCAL/H | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_STACK_LOSS_CORRECTED+BOILER_B_STACK_LOSS_CORRECTED+BOILER_C_STACK_LOSS_CORRECTED+BOILER_D_STACK_LOSS_CORRECTED+BOILER_E_STACK_LOSS_CORRECTED | Unknown/no sensor: BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_E_STACK_LOSS_CORRECTED | BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_E_STACK_LOSS_CORRECTED
TOTAL_BLOWDOWN_LOSS | TOTAL BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_BLOWDOWN_LOSS+BOILER_B_BLOWDOWN_LOSS+BOILER_C_BLOWDOWN_LOSS+BOILER_D_BLOWDOWN_LOSS+BOILER_E_BLOWDOWN_LOSS | Unknown/no sensor: BOILER_A_BLOWDOWN_LOSS ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_E_BLOWDOWN_LOSS | BOILER_A_BLOWDOWN_LOSS ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_E_BLOWDOWN_LOSS
TOTAL_FUEL_FLOW | TOTAL FUEL FLOW | Ton/h | LBM_preprocessing_inferred_tags_main | (BOILER_A_FUEL_GAS_FLOW+BOILER_B_FUEL_GAS_FLOW+BOILER_C_FUEL_GAS_FLOW+BOILER_D_FUEL_GAS_FLOW+BOILER_E_FUEL_GAS_FLOW/1.295)/1000 | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]
OVERALL_SUPERHEATED_STEAM_BFW_RATIO | OVERALL SUPERHEATED STEAM BFW RATIO | [-] | LBM_preprocessing_inferred_tags_main | (BOILER_A_SUPERHEATED_STEAM_BFW_RATIO+BOILER_B_SUPERHEATED_STEAM_BFW_RATIO+BOILER_C_SUPERHEATED_STEAM_BFW_RATIO+BOILER_D_SUPERHEATED_STEAM_BFW_RATIO+BOILER_E_SUPERHEATED_STEAM_BFW_RATIO)/5 | Unknown/no sensor: BOILER_A_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_B_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_C_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_D_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER_A_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_B_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_C_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_D_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_E_SUPERHEATED_STEAM_BFW_RATIO
TOTAL_FUEL_TO_AIR_RATIO | TOTAL FUEL TO AIR RATIO | Kg/ Kg Fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_FUEL_MASS_RATIO+BOILER_B_AIR_FUEL_MASS_RATIO+BOILER_C_AIR_FUEL_MASS_RATIO+BOILER_D_AIR_FUEL_MASS_RATIO+BOILER_E_AIR_FUEL_MASS_RATIO | Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_E_AIR_FUEL_MASS_RATIO
TOTAL_CO2_EMISSIONS | TOTAL CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | BOILER_A_CO2_EMISSIONS+BOILER_B_CO2_EMISSIONS+BOILER_C_CO2_EMISSIONS+BOILER_D_CO2_EMISSIONS+BOILER_E_CO2_EMISSIONS | Unknown/no sensor: BOILER_A_CO2_EMISSIONS ¦ BOILER_B_CO2_EMISSIONS ¦ BOILER_C_CO2_EMISSIONS ¦ BOILER_D_CO2_EMISSIONS ¦ BOILER_E_CO2_EMISSIONS | BOILER_A_CO2_EMISSIONS ¦ BOILER_B_CO2_EMISSIONS ¦ BOILER_C_CO2_EMISSIONS ¦ BOILER_D_CO2_EMISSIONS ¦ BOILER_E_CO2_EMISSIONS
BOILER_A_STEAM_TO_FIRE_DUTY_RATIO | BOILER A STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW/(BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG)*1000) | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_B_STEAM_TO_FIRE_DUTY_RATIO | BOILER B STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW/(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG)*1000) | Unknown/no sensor: BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_C_STEAM_TO_FIRE_DUTY_RATIO | BOILER C STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW/(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG)*1000) | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_D_STEAM_TO_FIRE_DUTY_RATIO | BOILER D STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW/(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG)*1000) | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_E_STEAM_TO_FIRE_DUTY_RATIO | BOILER E STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW/(BOILER_E_FG_FLOW_RATE*BOILER_E_MIXED_LHV_PER_KG)*1000) | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
EXCESS_O2 | EXCESS O2 | % | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FLUE_GAS_OXGYGEN*BOILER_A_STATUS)+(BOILER_B_FLUE_GAS_OXGYGEN*BOILER_B_STATUS)+(BOILER_C_FLUE_GAS_OXGYGEN*BOILER_C_STATUS)+(BOILER_D_FLUE_GAS_OXGYGEN*BOILER_D_STATUS)+(BOILER_E_FLUE_GAS_OXGYGEN_NEW*BOILER_E_STATUS))/BOILERS_ONLINE | PI exists but NOT in hierarchy: BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV] ¦ BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV] ¦ BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV] ¦ BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV] ¦ BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV] ¦ BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV] ¦ BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV] ¦ BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV] ¦ BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
STACK_TEMP | STACK TEMP | DEG C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_STACK_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_STACK_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_STACK_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_STACK_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_STACK_TEMPERATURE*BOILER_E_STATUS))/BOILERS_ONLINE | Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
STEAM_TEMP | STEAM TEMP | DEG C | LBM_preprocessing_inferred_tags_main | (DESUPERHEATER_OUTLET_TEMPERATURE*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_TEMPERATURE*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_TEMPERATURE*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_TEMPERATURE*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_TEMPERATURE*BOILER_E_STATUS)/BOILERS_ONLINE | Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
STEAM_PRESS | STEAM PRESS | BARG | LBM_preprocessing_inferred_tags_main | ((HP_STEAM_PRESSURE_FROM_DS*BOILER_A_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_B*BOILER_B_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_C*BOILER_C_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_D*BOILER_D_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_E*BOILER_E_STATUS))/BOILERS_ONLINE | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
COMBUSTION_AIR_TEMP | COMBUSTION AIR TEMP | DEG C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_COMBUSTION_AIR_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_COMBUSTION_AIR_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_COMBUSTION_AIR_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_COMBUSTION_AIR_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_COMBUSTION_AIR_TEMP*BOILER_E_STATUS))/BOILERS_ONLINE | PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] ¦ BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] ¦ BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] ¦ BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] ¦ BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] ¦ BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] ¦ BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] ¦ BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] ¦ BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
BLOWDOWN_CONDUCTIVITY | BLOWDOWN CONDUCTIVITY | US/ CM | LBM_preprocessing_inferred_tags_main | ((BOILER_A_CONDUCTIVITY*BOILER_A_STATUS)+(BOILER_B_CONDUCTIVITY*BOILER_B_STATUS)+(BOILER_C_CONDUCTIVITY*BOILER_C_STATUS)+(BOILER_D_CONDUCTIVITY*BOILER_D_STATUS)+(BOILER_E_CONDUCTIVITY*BOILER_E_STATUS))/BOILERS_ONLINE | PI exists but NOT in hierarchy: BOILER_A_CONDUCTIVITY[sensor:UN.UO.71AC1101.PV] ¦ BOILER_B_CONDUCTIVITY[sensor:UN.UO.71AC1201.PV] ¦ BOILER_C_CONDUCTIVITY[sensor:UN.UO.71AC1301.PV] ¦ BOILER_D_CONDUCTIVITY[sensor:UN.UO.71AC1401.PV] ¦ BOILER_E_CONDUCTIVITY[sensor:UN.UO.71AC1501A.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_CONDUCTIVITY[sensor:UN.UO.71AC1101.PV] ¦ BOILER_B_CONDUCTIVITY[sensor:UN.UO.71AC1201.PV] ¦ BOILER_C_CONDUCTIVITY[sensor:UN.UO.71AC1301.PV] ¦ BOILER_D_CONDUCTIVITY[sensor:UN.UO.71AC1401.PV] ¦ BOILER_E_CONDUCTIVITY[sensor:UN.UO.71AC1501A.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
SPECIFIC_ENERGY_AVG | SPECIFIC ENERGY AVG | KG/ KCAL | LBM_preprocessing_inferred_tags_main | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_D_STATUS+BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_E_STATUS)/BOILERS_ONLINE | Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS | BOILERS_ONLINE ¦ BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS ¦ BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_C_STATUS ¦ BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_D_STATUS ¦ BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ
FIRE_DUTY | FIRE DUTY | MMBTU/ DAY | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG*1000)*BOILER_A_STATUS+(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG*1000)*BOILER_B_STATUS+(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG*1000)*BOILER_C_STATUS+(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG*1000)*BOILER_D_STATUS+(BOILER_E_FG_FLOW_RATE*BOILER_E_MIXED_LHV_PER_KG*1000)*BOILER_E_S | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS ¦ BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS ¦ BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS ¦ BOILER_E_MIXED_LHV_PER_KG
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA | OVER ALL SPECIFIC ENERGY CONSUMPTION DELTA | nan | TRG_compute_inferred_pre_pta | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark<0,0,(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark)) | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
ENERGY_NUMBER | ENERGY NUMBER | MMBTU/ HR | TRG_compute_inferred_pre_pta | ((BOILER_A_FG_FLOW_RATE_actual*BOILER_A_MIXED_LHV_PER_KG_actual*1000)*BOILER_A_STATUS_actual+(BOILER_B_FG_FLOW_RATE_actual*BOILER_B_MIXED_LHV_PER_KG_actual*1000)*BOILER_B_STATUS_actual+(BOILER_C_FG_FLOW_RATE_actual*BOILER_C_MIXED_LHV_PER_KG_actual*1000)*BOILER_C_STATUS_actual+(BOILER_D_FG_FLOW_RATE_actual*BOILER_D_MIXED_LHV_PER_KG_actual*1000)*BOIL | eval_error: name 'BOILER_A_FG_FLOW_RATE_actual' is not defined
ENVIRONMENT_NUMBER | ENVIRONMENT NUMBER | MT/ HR | TRG_compute_inferred_pre_pta | ([ENERGY_NUMBER_actual]/0.0468/1000)*2.75 | eval_error: name 'ENERGY_NUMBER_actual' is not defined
opportunity_production | OPPORTUNITY PRODUCTION | MT/ DAY | TRG_compute_inferred_pre_pta | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual])*24/([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark])*0 | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
EQUIVALENT_FUEL | EQUIVALENT FUEL | MT/ HR | TRG_compute_inferred_pre_pta | [OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual]/0.0468/1000 | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
opportunity_environment | OPPORTUNITY ENVIRONMENT | MT/ DAY | TRG_compute_inferred_pre_pta | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[EQUIVALENT_FUEL_actual]*2.75*24) | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
opportunity_energy | OPPORTUNITY ENERGY | MMBTU/ DAY | TRG_compute_inferred_pre_pta | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
index_process | INDEX PROCESS | % | TRG_compute_inferred_pre_pta | (TOTAL_STEAM_PRODUCTION_actual/(TOTAL_STEAM_PRODUCTION_actual+opportunity_production_actual/24))*100*0+100 | eval_error: name 'TOTAL_STEAM_PRODUCTION_actual' is not defined
index_energy | INDEX ENERGY | % | TRG_compute_inferred_pre_pta | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 | eval_error: name 'ENERGY_NUMBER_actual' is not defined
index_environment | INDEX ENVIRONMENT | % | TRG_compute_inferred_pre_pta | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 | eval_error: name 'ENERGY_NUMBER_actual' is not defined
BOILER_A_ACTUAL_SP_ENERGY_DELTA | BOILER A ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | eval_error: name 'BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_B_ACTUAL_SP_ENERGY_DELTA | BOILER B ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | eval_error: name 'BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_C_ACTUAL_SP_ENERGY_DELTA | BOILER C ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | eval_error: name 'BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_D_ACTUAL_SP_ENERGY_DELTA | BOILER D ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | eval_error: name 'BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_E_ACTUAL_SP_ENERGY_DELTA | BOILER E ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | eval_error: name 'BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_A_FUEL_GAIN_LOSS | BOILER A FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | eval_error: name 'BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_B_FUEL_GAIN_LOSS | BOILER B FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_B_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | eval_error: name 'BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_C_FUEL_GAIN_LOSS | BOILER C FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_C_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | eval_error: name 'BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_D_FUEL_GAIN_LOSS | BOILER D FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_D_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | eval_error: name 'BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_E_FUEL_GAIN_LOSS | BOILER E FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_E_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | eval_error: name 'BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
TOTAL_FUEL_GAIN_LOSS | TOTAL FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | BOILER_A_FUEL_GAIN_LOSS_actual+BOILER_B_FUEL_GAIN_LOSS_actual+BOILER_C_FUEL_GAIN_LOSS_actual+BOILER_D_FUEL_GAIN_LOSS_actual+BOILER_E_FUEL_GAIN_LOSS_actual | eval_error: name 'BOILER_A_FUEL_GAIN_LOSS_actual' is not defined
FLAG_QUALITY_RATE | FLAG QUALITY RATE | % | LBM_preprocessing_inferred_tags_main | if(([STEAM_TEMP]>390&&[STEAM_PRESS]>40),1,0) | Unknown/no sensor: STEAM_PRESS ¦ STEAM_TEMP | STEAM_PRESS ¦ STEAM_TEMP
FLAG_QUALITY_RATE_PTA | FLAG QUALITY RATE PTA | % | TRG_compute_pta |  | No formula defined and no PI value
QUALITY_RATE | QUALITY RATE | % | TRG_compute_inferred_post_pta | FLAG_QUALITY_RATE_PTA_actual*100/24 | eval_error: name 'FLAG_QUALITY_RATE_PTA_actual' is not defined
Capacity_Utilization | CAPACITY UTILIZATION | % | LBM_ |  | No formula defined and no PI value
CAPACITY_UTILIZATION_1 | CAPACITY UTILIZATION 1 | % | LBM_preprocessing_inferred_tags_main | [TOTAL_STEAM_PRODUCTION]/750000*100 | Unknown/no sensor: TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
OVERALL_ENERGY_CONSUMPTION_DAY | OVERALL ENERGY CONSUMPTION DAY | GJ/ DAY | TRG_compute_inferred_pre_pta | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24 | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_benchmark | OVERALL ENERGY CONSUMPTION DAY BENCHMARK | GJ/ DAY | TRG_compute_inferred_pre_pta | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24 | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_DELTA | OVERALL ENERGY CONSUMPTION DAY DELTA | GJ/ DAY | TRG_compute_inferred_pre_pta | abs(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24)*TOTAL_STEAM_PRODUCTION_MT_DAY_actual | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
EQUIVALENT_FUEL_DAY | EQUIVALENT FUEL DAY | MT/ DAY | TRG_compute_inferred_pre_pta | [EQUIVALENT_FUEL_actual]*24 | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
TOTAL_ENERGY_GAP | TOTAL ENERGY GAP | MT/ DAY | TRG_compute_inferred_pre_pta | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
TOTAL_CO2_GAP | TOTAL CO2 GAP | MMBTU/ DAY | TRG_compute_inferred_pre_pta | [EQUIVALENT_FUEL_actual]*2.75*24 | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
Boiler_E_Nox_Emission | Boiler E Nox Emission | ng/J | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(BOILER_E_STATUS==0,0,BOILER_E_NOX*46/24.45*1000000*2.07/10000000*20.9/(20.9-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | PI exists but NOT in hierarchy: BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILER_E_NOX[sensor:UN.UO.71AI1505A1.PV] | BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILER_E_NOX[sensor:UN.UO.71AI1505A1.PV]
Boiler_E_Nox_Emission_Forecast | Boiler E Nox Emission Forecast | ng/J | 362_DM_ |  | No formula defined and no PI value
Boiler_E_Nox_Emission_Max_Forecast | Boiler E Nox Emission Max Forecast | ng/J | 362_DM_ |  | No formula defined and no PI value
Boiler_E_Nox_Emission_Timestamp_Max_Forecast | Boiler E Nox Emission Timestamp Max Forecast | nan | 362_DM_ |  | No formula defined and no PI value
TOTAL_STEAM_PRODUCTION_MT_DAY | TOTAL STEAM PRODUCTION IN MT PER DAY | MT/ DAY | LBM_preprocessing_inferred_tags_main | [TOTAL_STEAM_PRODUCTION]*24 | Unknown/no sensor: TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
Boiler_E_Nox_Emission_Actual_Value | Boiler E Nox Emission Actual Value | nan | 362_DM_ |  | No formula defined and no PI value
STEAM_MARGIN_TPH | Steam margin available in running boilers in TPH | TPH | LBM_preprocessing_inferred_tags_main | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS])*150-[TOTAL_STEAM_PRODUCTION] | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS ¦ TOTAL_STEAM_PRODUCTION | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS ¦ TOTAL_STEAM_PRODUCTION
STEAM_MARGIN_NUMBER | Available steam margin divided by 150 | nan | LBM_preprocessing_inferred_tags_main | [STEAM_MARGIN_TPH]/150 | Unknown/no sensor: STEAM_MARGIN_TPH | STEAM_MARGIN_TPH
NUMBER_OF_BOILERS_ONLINE | Number of boilers running | nan | LBM_preprocessing_inferred_tags_main | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS]) | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
NUMBER_OF_BOILERS_OPTIMUM | Optimum number of boilers that can be run considering steam margin. | nan | LBM_preprocessing_inferred_tags_main | if([STEAM_MARGIN_NUMBER]>2.0,([NUMBER_OF_BOILERS_ONLINE]-1),[NUMBER_OF_BOILERS_ONLINE]) | Unknown/no sensor: NUMBER_OF_BOILERS_ONLINE ¦ STEAM_MARGIN_NUMBER | NUMBER_OF_BOILERS_ONLINE ¦ STEAM_MARGIN_NUMBER
FLAG_BFW_QUALITY | FLAG BFW QUALITY | % | LBM_preprocessing_inferred_tags_main | if([BFW_OXYGEN]>7ll[BFW_SILICA]>20ll[BFW_SODIUM]>20[BFW_PH]>9.6ll[BFW_PH]<9.2ll[BFW_CONDUCTIVITY]>10,0,1) | PI exists but NOT in hierarchy: BFW_CONDUCTIVITY[sensor:UN.UO.71AI1005B.PV] ¦ BFW_OXYGEN[sensor:UN.UO.71AI1001.PV] ¦ BFW_PH[sensor:UN.UO.71AI1005A.PV] ¦ BFW_SILICA[sensor:UN.UO.71AI1002.PV] ¦ BFW_SODIUM[sensor:UN.UO.71AI1004.PV] | BFW_CONDUCTIVITY[sensor:UN.UO.71AI1005B.PV] ¦ BFW_OXYGEN[sensor:UN.UO.71AI1001.PV] ¦ BFW_PH[sensor:UN.UO.71AI1005A.PV] ¦ BFW_SILICA[sensor:UN.UO.71AI1002.PV] ¦ BFW_SODIUM[sensor:UN.UO.71AI1004.PV]
FLAG_BFW_QUALITY_PTA | FLAG BFW QUALITY PTA | % | TRG_compute_pta |  | No formula defined and no PI value
BFW_QUALITY_RATE | BFW QUALITY RATE | % | TRG_compute_inferred_post_pta | FLAG_BFW_QUALITY_PTA_actual*100/24 | eval_error: name 'FLAG_BFW_QUALITY_PTA_actual' is not defined

## Blocking_PI
blocking_tag_detail | blocks_n_calcs | tag_name | sensor_note
¦ | 1290 | ¦ | no sensor in PEEO
BOILER_A_STATUS | 71 | BOILER_A_STATUS | no sensor in PEEO
BOILER_B_STATUS | 61 | BOILER_B_STATUS | no sensor in PEEO
BOILER_C_STATUS | 61 | BOILER_C_STATUS | no sensor in PEEO
BOILER_D_STATUS | 61 | BOILER_D_STATUS | no sensor in PEEO
BOILER_A_FG_MW | 14 | BOILER_A_FG_MW | no sensor in PEEO
BOILER_B_FG_MW | 14 | BOILER_B_FG_MW | no sensor in PEEO
BOILER_C_FG_MW | 14 | BOILER_C_FG_MW | no sensor in PEEO
BOILER_D_FG_MW | 14 | BOILER_D_FG_MW | no sensor in PEEO
BOILER_E_FG_MW | 14 | BOILER_E_FG_MW | no sensor in PEEO
BOILER_A_FUEL_COMPOSITION_TOTAL | 11 | BOILER_A_FUEL_COMPOSITION_TOTAL | no sensor in PEEO
BOILER_B_FUEL_COMPOSITION_TOTAL | 11 | BOILER_B_FUEL_COMPOSITION_TOTAL | no sensor in PEEO
BOILER_C_FUEL_COMPOSITION_TOTAL | 11 | BOILER_C_FUEL_COMPOSITION_TOTAL | no sensor in PEEO
BOILER_D_FUEL_COMPOSITION_TOTAL | 11 | BOILER_D_FUEL_COMPOSITION_TOTAL | no sensor in PEEO
BOILER_E_FUEL_COMPOSITION_TOTAL | 11 | BOILER_E_FUEL_COMPOSITION_TOTAL | no sensor in PEEO
ARRAZI_PLANT_STATUS | 10 | ARRAZI_PLANT_STATUS | no sensor in PEEO
BOILER_FG_CH4_CONCENTRATION | 10 | BOILER_FG_CH4_CONCENTRATION | no sensor in PEEO
BOILER_FG_ETHANE_CONCENTRATION | 10 | BOILER_FG_ETHANE_CONCENTRATION | no sensor in PEEO
BOILER_FG_HYDROGEN_CONCENTRATION | 10 | BOILER_FG_HYDROGEN_CONCENTRATION | no sensor in PEEO
BOILER_FG_IC4_CONCENTRATION | 10 | BOILER_FG_IC4_CONCENTRATION | no sensor in PEEO
BOILER_FG_IC5_CONCENTRATION | 10 | BOILER_FG_IC5_CONCENTRATION | no sensor in PEEO
BOILER_FG_N2_CONCENTRATION | 10 | BOILER_FG_N2_CONCENTRATION | no sensor in PEEO
BOILER_FG_NC4_CONCENTRATION | 10 | BOILER_FG_NC4_CONCENTRATION | no sensor in PEEO
BOILER_FG_NC5_CONCENTRATION | 10 | BOILER_FG_NC5_CONCENTRATION | no sensor in PEEO
BOILER_FG_PROPANE_CONCENTRATION | 10 | BOILER_FG_PROPANE_CONCENTRATION | no sensor in PEEO
TOTAL_FUEL_COMPOSTION_MASS | 10 | TOTAL_FUEL_COMPOSTION_MASS | no sensor in PEEO
BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | 10 | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE | sensor:UN.UO.71TI1113.PV
BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] | 10 | BFW_PRESSURE_TO_BOILER | sensor:UN.UO.71PI1021A.PV
BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | 10 | BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | no sensor in PEEO
BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | 10 | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE | sensor:UN.UO.71TI1213.PV
BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | 10 | BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | no sensor in PEEO
BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | 10 | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE | sensor:UN.UO.71TI1313.PV
BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | 10 | BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | no sensor in PEEO
BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | 10 | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE | sensor:UN.UO.71TI1413.PV
BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | 10 | BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | no sensor in PEEO
BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | 10 | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE | sensor:UN.UO.71TI1513.PV
BOILERS_ONLINE | 8 | BOILERS_ONLINE | no sensor in PEEO
BOILER_A_FG_HYDROGEN_MASS_FRACTION | 8 | BOILER_A_FG_HYDROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_A_MIXED_LHV_PER_KG | 8 | BOILER_A_MIXED_LHV_PER_KG | no sensor in PEEO
BOILER_B_FG_HYDROGEN_MASS_FRACTION | 8 | BOILER_B_FG_HYDROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_B_MIXED_LHV_PER_KG | 8 | BOILER_B_MIXED_LHV_PER_KG | no sensor in PEEO
BOILER_C_FG_HYDROGEN_MASS_FRACTION | 8 | BOILER_C_FG_HYDROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_C_MIXED_LHV_PER_KG | 8 | BOILER_C_MIXED_LHV_PER_KG | no sensor in PEEO
BOILER_D_FG_ETHANE_MASS_FRACTION | 8 | BOILER_D_FG_ETHANE_MASS_FRACTION | no sensor in PEEO
BOILER_D_FG_HYDROGEN_MASS_FRACTION | 8 | BOILER_D_FG_HYDROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_D_MIXED_LHV_PER_KG | 8 | BOILER_D_MIXED_LHV_PER_KG | no sensor in PEEO
BOILER_E_FG_HYDROGEN_MASS_FRACTION | 8 | BOILER_E_FG_HYDROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_E_MIXED_LHV_PER_KG | 8 | BOILER_E_MIXED_LHV_PER_KG | no sensor in PEEO
BOILER_A_FG_CH4_MASS_FRACTION | 7 | BOILER_A_FG_CH4_MASS_FRACTION | no sensor in PEEO
BOILER_A_FG_ETHANE_MASS_FRACTION | 7 | BOILER_A_FG_ETHANE_MASS_FRACTION | no sensor in PEEO
BOILER_A_FG_ETHYLENE_MASS_FRACTION | 7 | BOILER_A_FG_ETHYLENE_MASS_FRACTION | no sensor in PEEO
BOILER_A_FG_IC4_MASS_FRACTION | 7 | BOILER_A_FG_IC4_MASS_FRACTION | no sensor in PEEO
BOILER_A_FG_IC5_MASS_FRACTION | 7 | BOILER_A_FG_IC5_MASS_FRACTION | no sensor in PEEO
BOILER_A_FG_NC4_MASS_FRACTION | 7 | BOILER_A_FG_NC4_MASS_FRACTION | no sensor in PEEO
BOILER_A_FG_NC5_MASS_FRACTION | 7 | BOILER_A_FG_NC5_MASS_FRACTION | no sensor in PEEO
BOILER_A_FG_PROPANE_MASS_FRACTION | 7 | BOILER_A_FG_PROPANE_MASS_FRACTION | no sensor in PEEO
BOILER_B_FG_CH4_MASS_FRACTION | 7 | BOILER_B_FG_CH4_MASS_FRACTION | no sensor in PEEO
BOILER_B_FG_ETHANE_MASS_FRACTION | 7 | BOILER_B_FG_ETHANE_MASS_FRACTION | no sensor in PEEO
BOILER_B_FG_IC4_MASS_FRACTION | 7 | BOILER_B_FG_IC4_MASS_FRACTION | no sensor in PEEO
BOILER_B_FG_IC5_MASS_FRACTION | 7 | BOILER_B_FG_IC5_MASS_FRACTION | no sensor in PEEO
BOILER_B_FG_NC4_MASS_FRACTION | 7 | BOILER_B_FG_NC4_MASS_FRACTION | no sensor in PEEO
BOILER_B_FG_NC5_MASS_FRACTION | 7 | BOILER_B_FG_NC5_MASS_FRACTION | no sensor in PEEO
BOILER_B_FG_PROPANE_MASS_FRACTION | 7 | BOILER_B_FG_PROPANE_MASS_FRACTION | no sensor in PEEO
BOILER_C_FG_CH4_MASS_FRACTION | 7 | BOILER_C_FG_CH4_MASS_FRACTION | no sensor in PEEO
BOILER_C_FG_ETHANE_MASS_FRACTION | 7 | BOILER_C_FG_ETHANE_MASS_FRACTION | no sensor in PEEO
BOILER_C_FG_IC4_MASS_FRACTION | 7 | BOILER_C_FG_IC4_MASS_FRACTION | no sensor in PEEO
BOILER_C_FG_IC5_MASS_FRACTION | 7 | BOILER_C_FG_IC5_MASS_FRACTION | no sensor in PEEO
BOILER_C_FG_NC4_MASS_FRACTION | 7 | BOILER_C_FG_NC4_MASS_FRACTION | no sensor in PEEO
BOILER_C_FG_NC5_MASS_FRACTION | 7 | BOILER_C_FG_NC5_MASS_FRACTION | no sensor in PEEO
BOILER_C_FG_PROPANE_MASS_FRACTION | 7 | BOILER_C_FG_PROPANE_MASS_FRACTION | no sensor in PEEO
BOILER_D_FG_CH4_MASS_FRACTION | 7 | BOILER_D_FG_CH4_MASS_FRACTION | no sensor in PEEO
BOILER_D_FG_IC4_MASS_FRACTION | 7 | BOILER_D_FG_IC4_MASS_FRACTION | no sensor in PEEO
BOILER_D_FG_IC5_MASS_FRACTION | 7 | BOILER_D_FG_IC5_MASS_FRACTION | no sensor in PEEO
BOILER_D_FG_NC4_MASS_FRACTION | 7 | BOILER_D_FG_NC4_MASS_FRACTION | no sensor in PEEO
BOILER_D_FG_NC5_MASS_FRACTION | 7 | BOILER_D_FG_NC5_MASS_FRACTION | no sensor in PEEO
BOILER_D_FG_PROPANE_MASS_FRACTION | 7 | BOILER_D_FG_PROPANE_MASS_FRACTION | no sensor in PEEO
BOILER_E_FG_CH4_MASS_FRACTION | 7 | BOILER_E_FG_CH4_MASS_FRACTION | no sensor in PEEO
BOILER_E_FG_IC4_MASS_FRACTION | 7 | BOILER_E_FG_IC4_MASS_FRACTION | no sensor in PEEO
BOILER_E_FG_IC5_MASS_FRACTION | 7 | BOILER_E_FG_IC5_MASS_FRACTION | no sensor in PEEO
BOILER_E_FG_NC4_MASS_FRACTION | 7 | BOILER_E_FG_NC4_MASS_FRACTION | no sensor in PEEO
BOILER_E_FG_NC5_MASS_FRACTION | 7 | BOILER_E_FG_NC5_MASS_FRACTION | no sensor in PEEO
BOILER_E_FG_PROPANE_MASS_FRACTION | 7 | BOILER_E_FG_PROPANE_MASS_FRACTION | no sensor in PEEO
BOILER_A_TOTAL_STEAM_ENERGY | 6 | BOILER_A_TOTAL_STEAM_ENERGY | no sensor in PEEO
BOILER_B_FG_ETHYLENE_MASS_FRACTION | 6 | BOILER_B_FG_ETHYLENE_MASS_FRACTION | no sensor in PEEO
BOILER_B_TOTAL_STEAM_ENERGY | 6 | BOILER_B_TOTAL_STEAM_ENERGY | no sensor in PEEO
BOILER_C_FG_ETHYLENE_MASS_FRACTION | 6 | BOILER_C_FG_ETHYLENE_MASS_FRACTION | no sensor in PEEO
BOILER_C_TOTAL_STEAM_ENERGY | 6 | BOILER_C_TOTAL_STEAM_ENERGY | no sensor in PEEO
BOILER_D_FG_ETHYLENE_MASS_FRACTION | 6 | BOILER_D_FG_ETHYLENE_MASS_FRACTION | no sensor in PEEO
BOILER_D_TOTAL_STEAM_ENERGY | 6 | BOILER_D_TOTAL_STEAM_ENERGY | no sensor in PEEO
BOILER_E_FG_ETHANE_MASS_FRACTION | 6 | BOILER_E_FG_ETHANE_MASS_FRACTION | no sensor in PEEO
BOILER_E_FG_ETHYLENE_MASS_FRACTION | 6 | BOILER_E_FG_ETHYLENE_MASS_FRACTION | no sensor in PEEO
BOILER_E_TOTAL_STEAM_ENERGY | 6 | BOILER_E_TOTAL_STEAM_ENERGY | no sensor in PEEO
BOILER_FG_CO2_CONCENTRATION | 5 | BOILER_FG_CO2_CONCENTRATION | no sensor in PEEO
BOILER_A_CO2_FORMED | 5 | BOILER_A_CO2_FORMED | no sensor in PEEO
BOILER_LHV | 5 | BOILER_LHV | no sensor in PEEO
BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | 5 | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] | 5 | BOILER_B_FUEL_GAS_FLOW | sensor:UN.UO.71FC1204.PV
BOILER_B_CO2_FORMED | 5 | BOILER_B_CO2_FORMED | no sensor in PEEO
BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | 5 | BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_C_CO2_FORMED | 5 | BOILER_C_CO2_FORMED | no sensor in PEEO
BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | 5 | BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_D_CO2_FORMED | 5 | BOILER_D_CO2_FORMED | no sensor in PEEO
BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | 5 | BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_E_CO2_FORMED | 5 | BOILER_E_CO2_FORMED | no sensor in PEEO
BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | 5 | BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_A_N2_FORMED | 4 | BOILER_A_N2_FORMED | no sensor in PEEO
BOILER_A_EXCESS_AIR | 4 | BOILER_A_EXCESS_AIR | no sensor in PEEO
BOILER_A_AIR_FUEL_MASS_RATIO | 4 | BOILER_A_AIR_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO | 4 | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] | 4 | STEAM_DRUM_A_PRESSURE | sensor:UN.UO.71PC1103.PV
BOILER_A_CORRECTED_FUEL_FLOW | 4 | BOILER_A_CORRECTED_FUEL_FLOW | no sensor in PEEO
BOILER_B_N2_FORMED | 4 | BOILER_B_N2_FORMED | no sensor in PEEO
BOILER_B_EXCESS_AIR | 4 | BOILER_B_EXCESS_AIR | no sensor in PEEO
BOILER_B_AIR_FUEL_MASS_RATIO | 4 | BOILER_B_AIR_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO | 4 | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] | 4 | BOILER_B_STEAM_DRUM_PRESSURE | sensor:UN.UO.71PC1203.PV
BOILER_B_CORRECTED_FUEL_FLOW | 4 | BOILER_B_CORRECTED_FUEL_FLOW | no sensor in PEEO
BOILER_C_N2_FORMED | 4 | BOILER_C_N2_FORMED | no sensor in PEEO
BOILER_C_EXCESS_AIR | 4 | BOILER_C_EXCESS_AIR | no sensor in PEEO
BOILER_C_AIR_FUEL_MASS_RATIO | 4 | BOILER_C_AIR_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO | 4 | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] | 4 | BOILER_C_STEAM_DRUM_PRESSURE | sensor:UN.UO.71PC1303.PV
BOILER_C_CORRECTED_FUEL_FLOW | 4 | BOILER_C_CORRECTED_FUEL_FLOW | no sensor in PEEO
BOILER_D_N2_FORMED | 4 | BOILER_D_N2_FORMED | no sensor in PEEO
BOILER_D_EXCESS_AIR | 4 | BOILER_D_EXCESS_AIR | no sensor in PEEO
BOILER_D_AIR_FUEL_MASS_RATIO | 4 | BOILER_D_AIR_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO | 4 | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] | 4 | BOILER_D_STEAM_DRUM_PRESSURE | sensor:UN.UO.71PC1403.PV
BOILER_D_CORRECTED_FUEL_FLOW | 4 | BOILER_D_CORRECTED_FUEL_FLOW | no sensor in PEEO
BOILER_E_N2_FORMED | 4 | BOILER_E_N2_FORMED | no sensor in PEEO
BOILER_E_EXCESS_AIR | 4 | BOILER_E_EXCESS_AIR | no sensor in PEEO
BOILER_E_AIR_FUEL_MASS_RATIO | 4 | BOILER_E_AIR_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | 4 | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_E_CORRECTED_FUEL_FLOW | 4 | BOILER_E_CORRECTED_FUEL_FLOW | no sensor in PEEO
HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] | 3 | HP_STEAM_PRESSURE_FROM_DS | sensor:UN.UO.71PI1113.PV
HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] | 3 | HP_STEAM_PRESSURE_FROM_DS_B | sensor:UN.UO.71PI1213.PV
HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] | 3 | HP_STEAM_PRESSURE_FROM_DS_C | sensor:UN.UO.71PI1313.PV
HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV] | 3 | HP_STEAM_PRESSURE_FROM_DS_D | sensor:UN.UO.71PI1413.PV
BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] | 3 | BOILER_A_COMBUSTION_AIR_TEMPERATURE | sensor:UN.UO.71TI1114B.PV
BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | 3 | BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 3 | BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | no sensor in PEEO
ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] | 3 | ECONOMIZER_A_INLET_TEMPERATURE | sensor:UN.UO.71TI1110.PV
BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] | 3 | BOILER_A_CBD_BD | sensor:UN.UO.71FC1100.PV
BOILER_A_CORRECTED_BFW_FLOW | 3 | BOILER_A_CORRECTED_BFW_FLOW | no sensor in PEEO
BOILER_A_BFW_ENERGY | 3 | BOILER_A_BFW_ENERGY | no sensor in PEEO
BOILER_A_BLOWDOWN_LOSS | 3 | BOILER_A_BLOWDOWN_LOSS | no sensor in PEEO
BOILER_A_FUEL_GAS_CORRECTED_TPH | 3 | BOILER_A_FUEL_GAS_CORRECTED_TPH | no sensor in PEEO
BOILER_A_CONVECTION_DUTY | 3 | BOILER_A_CONVECTION_DUTY | no sensor in PEEO
BOILER_A_ENERGY_GAINED | 3 | BOILER_A_ENERGY_GAINED | no sensor in PEEO
BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] | 3 | BOILER_B_COMBUSTION_AIR_TEMPERATURE | sensor:UN.UO.71TI1214B.PV
BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | 3 | BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 3 | BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | no sensor in PEEO
ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] | 3 | ECONOMIZER_B_INLET_TEMPERATURE | sensor:UN.UO.71TI1210.PV
CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV] | 3 | CBD_BLOW_DOWN_B | sensor:UN.UO.71FC1200.PV
BOILER_B_CORRECTED_BFW_FLOW | 3 | BOILER_B_CORRECTED_BFW_FLOW | no sensor in PEEO
BOILER_B_FG_FLOW_RATE | 3 | BOILER_B_FG_FLOW_RATE | no sensor in PEEO
BOILER_B_BFW_ENERGY | 3 | BOILER_B_BFW_ENERGY | no sensor in PEEO
BOILER_B_BLOWDOWN_LOSS | 3 | BOILER_B_BLOWDOWN_LOSS | no sensor in PEEO
BOILER_B_FUEL_GAS_CORRECTED_TPH | 3 | BOILER_B_FUEL_GAS_CORRECTED_TPH | no sensor in PEEO
BOILER_B_CONVECTION_DUTY | 3 | BOILER_B_CONVECTION_DUTY | no sensor in PEEO
BOILER_B_ENERGY_GAINED | 3 | BOILER_B_ENERGY_GAINED | no sensor in PEEO
BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] | 3 | BOILER_C_COMBUSTION_AIR_TEMPERATURE | sensor:UN.UO.71TI1314B.PV
BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | 3 | BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 3 | BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | no sensor in PEEO
ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] | 3 | ECONOMIZER_C_INLET_TEMPERATURE | sensor:UN.UO.71TI1310.PV
CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV] | 3 | CBD_BLOW_DOWN_C | sensor:UN.UO.71FC1300.PV
BOILER_C_CORRECTED_BFW_FLOW | 3 | BOILER_C_CORRECTED_BFW_FLOW | no sensor in PEEO
BOILER_C_BFW_ENERGY | 3 | BOILER_C_BFW_ENERGY | no sensor in PEEO
BOILER_C_BLOWDOWN_LOSS | 3 | BOILER_C_BLOWDOWN_LOSS | no sensor in PEEO
BOILER_C_FUEL_GAS_CORRECTED_TPH | 3 | BOILER_C_FUEL_GAS_CORRECTED_TPH | no sensor in PEEO
BOILER_C_CONVECTION_DUTY | 3 | BOILER_C_CONVECTION_DUTY | no sensor in PEEO
BOILER_C_ENERGY_GAINED | 3 | BOILER_C_ENERGY_GAINED | no sensor in PEEO
BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] | 3 | BOILER_D_COMBUSTION_AIR_TEMPERATURE | sensor:UN.UO.71TI1414B.PV
BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | 3 | BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 3 | BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | no sensor in PEEO
ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] | 3 | ECONOMIZER_D_INLET_TEMPERATURE | sensor:UN.UO.71TI1410.PV
CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV] | 3 | CBD_BLOW_DOWN_D | sensor:UN.UO.71FC1400.PV
BOILER_D_CORRECTED_BFW_FLOW | 3 | BOILER_D_CORRECTED_BFW_FLOW | no sensor in PEEO
BOILER_D_BFW_ENERGY | 3 | BOILER_D_BFW_ENERGY | no sensor in PEEO
BOILER_D_BLOWDOWN_LOSS | 3 | BOILER_D_BLOWDOWN_LOSS | no sensor in PEEO
BOILER_D_FUEL_GAS_CORRECTED_TPH | 3 | BOILER_D_FUEL_GAS_CORRECTED_TPH | no sensor in PEEO
BOILER_D_CONVECTION_DUTY | 3 | BOILER_D_CONVECTION_DUTY | no sensor in PEEO
BOILER_D_ENERGY_GAINED | 3 | BOILER_D_ENERGY_GAINED | no sensor in PEEO
BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] | 3 | BOILER_E_FLUE_GAS_OXGYGEN_NEW | sensor:UN.UO.71AC1504AA.PV
BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV] | 3 | BOILER_E_COMBUSTION_AIR_TEMP | sensor:UN.UO.71TI1514.PV
BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | 3 | BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | 3 | BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | no sensor in PEEO
ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] | 3 | ECONOMIZER_E_INLET_TEMPERATURE | sensor:UN.UO.71TI1510.PV
CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV] | 3 | CBD_BLOW_DOWN_E | sensor:UN.UO.71FC1500.PV
BOILER_E_CORRECTED_BFW_FLOW | 3 | BOILER_E_CORRECTED_BFW_FLOW | no sensor in PEEO
BOILER_E_BFW_ENERGY | 3 | BOILER_E_BFW_ENERGY | no sensor in PEEO
BOILER_E_BLOWDOWN_LOSS | 3 | BOILER_E_BLOWDOWN_LOSS | no sensor in PEEO
BOILER_E_FUEL_GAS_CORRECTED_TPH | 3 | BOILER_E_FUEL_GAS_CORRECTED_TPH | no sensor in PEEO
BOILER_E_CONVECTION_DUTY | 3 | BOILER_E_CONVECTION_DUTY | no sensor in PEEO
BOILER_E_ENERGY_GAINED | 3 | BOILER_E_ENERGY_GAINED | no sensor in PEEO
TOTAL_STEAM_PRODUCTION | 3 | TOTAL_STEAM_PRODUCTION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | 2 | NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | no sensor in PEEO
BOILER_A_FG_CH4_MASS_PERCENTAGE | 2 | BOILER_A_FG_CH4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_ETHANE_MASS_PERCENTAGE | 2 | BOILER_A_FG_ETHANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE | 2 | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE | 2 | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_IC4_MASS_PERCENTAGE | 2 | BOILER_A_FG_IC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_IC5_MASS_PERCENTAGE | 2 | BOILER_A_FG_IC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_NC4_MASS_PERCENTAGE | 2 | BOILER_A_FG_NC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_NC5_MASS_PERCENTAGE | 2 | BOILER_A_FG_NC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | 2 | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_FG_PROPANE_MASS_PERCENTAGE | 2 | BOILER_A_FG_PROPANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 2 | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | no sensor in PEEO
BOILER_A_CORRECTED_COMBUSTION_AIR | 2 | BOILER_A_CORRECTED_COMBUSTION_AIR | no sensor in PEEO
BOILER_A_H2O_FORMED | 2 | BOILER_A_H2O_FORMED | no sensor in PEEO
BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV] | 2 | BOILER_A_FLUE_GAS_OXGYGEN | sensor:UN.UO.71AC1104.PV
BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 2 | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | 2 | BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | no sensor in PEEO
BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | 2 | BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | no sensor in PEEO
SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV] | 2 | SUPERHEATER_INLET_TEMPERATURE | sensor:UN.UO.71TI1119.PV
BOILER_A_FUEL_CONSUMPTION | 2 | BOILER_A_FUEL_CONSUMPTION | no sensor in PEEO
ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] | 2 | ECONIMIZER_A_OUTLET_TEMPERATURE | sensor:UN.UO.71TI1102.PV
BOILER_A_ECONOMIZER_DUTY | 2 | BOILER_A_ECONOMIZER_DUTY | no sensor in PEEO
BOILER_A_SH_DUTY | 2 | BOILER_A_SH_DUTY | no sensor in PEEO
BOILER_A_STACK_LOSS_CORRECTED | 2 | BOILER_A_STACK_LOSS_CORRECTED | no sensor in PEEO
BOILER_A_RADIATION_DUTY | 2 | BOILER_A_RADIATION_DUTY | no sensor in PEEO
NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | 2 | NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | no sensor in PEEO
BOILER_B_FG_CH4_MASS_PERCENTAGE | 2 | BOILER_B_FG_CH4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_ETHANE_MASS_PERCENTAGE | 2 | BOILER_B_FG_ETHANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE | 2 | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE | 2 | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_IC4_MASS_PERCENTAGE | 2 | BOILER_B_FG_IC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_IC5_MASS_PERCENTAGE | 2 | BOILER_B_FG_IC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_NC4_MASS_PERCENTAGE | 2 | BOILER_B_FG_NC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_NC5_MASS_PERCENTAGE | 2 | BOILER_B_FG_NC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_NITROGEN_MASS_PERCENTAGE | 2 | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_FG_PROPANE_MASS_PERCENTAGE | 2 | BOILER_B_FG_PROPANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 2 | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | no sensor in PEEO
BOILER_B_CORRECTED_COMBUSTION_AIR | 2 | BOILER_B_CORRECTED_COMBUSTION_AIR | no sensor in PEEO
BOILER_B_H2O_FORMED | 2 | BOILER_B_H2O_FORMED | no sensor in PEEO
BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV] | 2 | BOILER_B_FLUE_GAS_OXGYGEN | sensor:UN.UO.71AC1204.PV
BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 2 | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | 2 | BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | no sensor in PEEO
BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | 2 | BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV] | 2 | BOILER_B_SUPERHEATER_INLET_TEMPERATURE | sensor:UN.UO.71TI1219.PV
BOILER_B_FUEL_CONSUMPTION | 2 | BOILER_B_FUEL_CONSUMPTION | no sensor in PEEO
ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV] | 2 | ECONOMIZER_B_OUTLET_TEMPERATURE | sensor:UN.UO.71TI1202.PV
BOILER_B_ECONOMIZER_DUTY | 2 | BOILER_B_ECONOMIZER_DUTY | no sensor in PEEO
BOILER_B_SH_DUTY | 2 | BOILER_B_SH_DUTY | no sensor in PEEO
BOILER_B_STACK_LOSS_CORRECTED | 2 | BOILER_B_STACK_LOSS_CORRECTED | no sensor in PEEO
BOILER_B_RADIATION_DUTY | 2 | BOILER_B_RADIATION_DUTY | no sensor in PEEO
NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | 2 | NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | no sensor in PEEO
BOILER_C_FG_CH4_MASS_PERCENTAGE | 2 | BOILER_C_FG_CH4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_ETHANE_MASS_PERCENTAGE | 2 | BOILER_C_FG_ETHANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE | 2 | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE | 2 | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_IC4_MASS_PERCENTAGE | 2 | BOILER_C_FG_IC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_IC5_MASS_PERCENTAGE | 2 | BOILER_C_FG_IC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_NC4_MASS_PERCENTAGE | 2 | BOILER_C_FG_NC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_NC5_MASS_PERCENTAGE | 2 | BOILER_C_FG_NC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_NITROGEN_MASS_PERCENTAGE | 2 | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_FG_PROPANE_MASS_PERCENTAGE | 2 | BOILER_C_FG_PROPANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 2 | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | no sensor in PEEO
BOILER_C_CORRECTED_COMBUSTION_AIR | 2 | BOILER_C_CORRECTED_COMBUSTION_AIR | no sensor in PEEO
BOILER_C_H2O_FORMED | 2 | BOILER_C_H2O_FORMED | no sensor in PEEO
BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV] | 2 | BOILER_C_FLUE_GAS_OXGYGEN | sensor:UN.UO.71AC1304.PV
BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 2 | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | 2 | BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | no sensor in PEEO
BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | 2 | BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV] | 2 | BOILER_C_SUPERHEATER_INLET_TEMPERATURE | sensor:UN.UO.71TI1319.PV
BOILER_C_FUEL_CONSUMPTION | 2 | BOILER_C_FUEL_CONSUMPTION | no sensor in PEEO
ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV] | 2 | ECONOMIZER_C_OUTLET_TEMPERATURE | sensor:UN.UO.71TI1302.PV
BOILER_C_ECONOMIZER_DUTY | 2 | BOILER_C_ECONOMIZER_DUTY | no sensor in PEEO
BOILER_C_SH_DUTY | 2 | BOILER_C_SH_DUTY | no sensor in PEEO
BOILER_C_STACK_LOSS_CORRECTED | 2 | BOILER_C_STACK_LOSS_CORRECTED | no sensor in PEEO
BOILER_C_RADIATION_DUTY | 2 | BOILER_C_RADIATION_DUTY | no sensor in PEEO
NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | 2 | NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | no sensor in PEEO
BOILER_D_FG_CH4_MASS_PERCENTAGE | 2 | BOILER_D_FG_CH4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_ETHANE_MASS_PERCENTAGE | 2 | BOILER_D_FG_ETHANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE | 2 | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE | 2 | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_IC4_MASS_PERCENTAGE | 2 | BOILER_D_FG_IC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_IC5_MASS_PERCENTAGE | 2 | BOILER_D_FG_IC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_NC4_MASS_PERCENTAGE | 2 | BOILER_D_FG_NC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_NC5_MASS_PERCENTAGE | 2 | BOILER_D_FG_NC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_NITROGEN_MASS_PERCENTAGE | 2 | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_FG_PROPANE_MASS_PERCENTAGE | 2 | BOILER_D_FG_PROPANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 2 | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | no sensor in PEEO
BOILER_D_CORRECTED_COMBUSTION_AIR | 2 | BOILER_D_CORRECTED_COMBUSTION_AIR | no sensor in PEEO
BOILER_D_H2O_FORMED | 2 | BOILER_D_H2O_FORMED | no sensor in PEEO
BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV] | 2 | BOILER_D_FLUE_GAS_OXGYGEN | sensor:UN.UO.71AC1404.PV
BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 2 | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | 2 | BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | no sensor in PEEO
BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | 2 | BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV] | 2 | BOILER_D_SUPERHEATER_INLET_TEMPERATURE | sensor:UN.UO.71TI1419.PV
BOILER_D_FUEL_CONSUMPTION | 2 | BOILER_D_FUEL_CONSUMPTION | no sensor in PEEO
ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV] | 2 | ECONOMIZER_D_OUTLET_TEMPERATURE | sensor:UN.UO.71TI1402.PV
BOILER_D_ECONOMIZER_DUTY | 2 | BOILER_D_ECONOMIZER_DUTY | no sensor in PEEO
BOILER_D_SH_DUTY | 2 | BOILER_D_SH_DUTY | no sensor in PEEO
BOILER_D_STACK_LOSS_CORRECTED | 2 | BOILER_D_STACK_LOSS_CORRECTED | no sensor in PEEO
BOILER_D_RADIATION_DUTY | 2 | BOILER_D_RADIATION_DUTY | no sensor in PEEO
NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | no sensor in PEEO
NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | 2 | NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | no sensor in PEEO
BOILER_E_FG_CH4_MASS_PERCENTAGE | 2 | BOILER_E_FG_CH4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_ETHANE_MASS_PERCENTAGE | 2 | BOILER_E_FG_ETHANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE | 2 | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE | 2 | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_IC4_MASS_PERCENTAGE | 2 | BOILER_E_FG_IC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_IC5_MASS_PERCENTAGE | 2 | BOILER_E_FG_IC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_NC4_MASS_PERCENTAGE | 2 | BOILER_E_FG_NC4_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_NC5_MASS_PERCENTAGE | 2 | BOILER_E_FG_NC5_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_NITROGEN_MASS_PERCENTAGE | 2 | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_FG_PROPANE_MASS_PERCENTAGE | 2 | BOILER_E_FG_PROPANE_MASS_PERCENTAGE | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | 2 | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | no sensor in PEEO
BOILER_E_CORRECTED_COMBUSTION_AIR | 2 | BOILER_E_CORRECTED_COMBUSTION_AIR | no sensor in PEEO
BOILER_E_H2O_FORMED | 2 | BOILER_E_H2O_FORMED | no sensor in PEEO
BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | 2 | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | no sensor in PEEO
BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | 2 | BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | no sensor in PEEO
BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | 2 | BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_E_FUEL_CONSUMPTION | 2 | BOILER_E_FUEL_CONSUMPTION | no sensor in PEEO
ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV] | 2 | ECONOMIZER_E_OUTLET_TEMPERATURE | sensor:UN.UO.71TI1502.PV
BOILER_E_ECONOMIZER_DUTY | 2 | BOILER_E_ECONOMIZER_DUTY | no sensor in PEEO
BOILER_E_STACK_LOSS_CORRECTED | 2 | BOILER_E_STACK_LOSS_CORRECTED | no sensor in PEEO
BOILER_E_RADIATION_DUTY | 2 | BOILER_E_RADIATION_DUTY | no sensor in PEEO
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 2 | BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | no sensor in PEEO
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 2 | BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | no sensor in PEEO
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 2 | BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | no sensor in PEEO
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 2 | BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | no sensor in PEEO
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | 2 | BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | no sensor in PEEO
ARRAZI_PLANT_LOAD[sensor:AR.AR5.DCS.Process.REFLOAD5.CPV] | 1 | ARRAZI_PLANT_LOAD | sensor:AR.AR5.DCS.Process.REFLOAD5.CPV
ARRAZI_PLANT_LOAD_1 | 1 | ARRAZI_PLANT_LOAD_1 | no sensor in PEEO
BOILER_A_FG_DENSITY | 1 | BOILER_A_FG_DENSITY | no sensor in PEEO
BOILER_A_FG_NITROGEN_MASS_FRACTION | 1 | BOILER_A_FG_NITROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION | no sensor in PEEO
BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 1 | BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | no sensor in PEEO
BOILER_A_CH4_CO2_COMBUSTION | 1 | BOILER_A_CH4_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_ETHANE_CO2_COMBUSTION | 1 | BOILER_A_ETHANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_ETHYLENE_CO2_COMBUSTION | 1 | BOILER_A_ETHYLENE_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_IC4_CO2_COMBUSTION | 1 | BOILER_A_IC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_IC5_CO2_COMBUSTION | 1 | BOILER_A_IC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_NC4_CO2_COMBUSTION | 1 | BOILER_A_NC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_NC5_CO2_COMBUSTION | 1 | BOILER_A_NC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_PROPANE_CO2_COMBUSTION | 1 | BOILER_A_PROPANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_A_CH4_N2_COMBUSTION | 1 | BOILER_A_CH4_N2_COMBUSTION | no sensor in PEEO
BOILER_A_ETHANE_N2_COMBUSTION | 1 | BOILER_A_ETHANE_N2_COMBUSTION | no sensor in PEEO
BOILER_A_ETHYLENE_N2_COMBUSTION | 1 | BOILER_A_ETHYLENE_N2_COMBUSTION | no sensor in PEEO
BOILER_A_H2_N2_COMBUSTION | 1 | BOILER_A_H2_N2_COMBUSTION | no sensor in PEEO
BOILER_A_IC4_N2_COMBUSTION | 1 | BOILER_A_IC4_N2_COMBUSTION | no sensor in PEEO
BOILER_A_IC5_N2_COMBUSTION | 1 | BOILER_A_IC5_N2_COMBUSTION | no sensor in PEEO
BOILER_A_NC4_N2_COMBUSTION | 1 | BOILER_A_NC4_N2_COMBUSTION | no sensor in PEEO
BOILER_A_NC5_N2_COMBUSTION | 1 | BOILER_A_NC5_N2_COMBUSTION | no sensor in PEEO
BOILER_A_PROPANE_N2_COMBUSTION | 1 | BOILER_A_PROPANE_N2_COMBUSTION | no sensor in PEEO
BOILER_A_CH4_H2O_COMBUSTION | 1 | BOILER_A_CH4_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_ETHANE_H2O_COMBUSTION | 1 | BOILER_A_ETHANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_ETHYLENE_H2O_COMBUSTION | 1 | BOILER_A_ETHYLENE_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_H2_H2O_COMBUSTION | 1 | BOILER_A_H2_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_IC4_H2O_COMBUSTION | 1 | BOILER_A_IC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_IC5_H2O_COMBUSTION | 1 | BOILER_A_IC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_NC4_H2O_COMBUSTION | 1 | BOILER_A_NC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_NC5_H2O_COMBUSTION | 1 | BOILER_A_NC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_PROPANE_H2O_COMBUSTION | 1 | BOILER_A_PROPANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_A_CORRECTED_COMBUTION_H2O_FORMED | 1 | BOILER_A_CORRECTED_COMBUTION_H2O_FORMED | no sensor in PEEO
BOILER_A_TOTAL_MOISTURE_WITH_AIR | 1 | BOILER_A_TOTAL_MOISTURE_WITH_AIR | no sensor in PEEO
BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | 1 | BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | no sensor in PEEO
BOILER_A_CP_CH4_FUEL_TEMP | 1 | BOILER_A_CP_CH4_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_ETHANE_FUEL_TEMP | 1 | BOILER_A_CP_ETHANE_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_ETHYLENE_FUEL_TEMP | 1 | BOILER_A_CP_ETHYLENE_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_H2_FUEL_TEMP | 1 | BOILER_A_CP_H2_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_IC4_FUEL_TEMP | 1 | BOILER_A_CP_IC4_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_IC5_FUEL_TEMP | 1 | BOILER_A_CP_IC5_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_NC4_FUEL_TEMP | 1 | BOILER_A_CP_NC4_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_NC5_FUEL_TEMP | 1 | BOILER_A_CP_NC5_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_PROPANE_FUEL_TEMP | 1 | BOILER_A_CP_PROPANE_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP | 1 | BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP | no sensor in PEEO
BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP | 1 | BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP | no sensor in PEEO
BOILER_A_FLUE_GAS_MW | 1 | BOILER_A_FLUE_GAS_MW | no sensor in PEEO
BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR | 1 | BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR | no sensor in PEEO
BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | 1 | BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | no sensor in PEEO
BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1 | BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | no sensor in PEEO
BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1 | BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | no sensor in PEEO
BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | 1 | BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | no sensor in PEEO
BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | 1 | BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | no sensor in PEEO
BOILER_A_RADIATION_LOSSES | 1 | BOILER_A_RADIATION_LOSSES | no sensor in PEEO
BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 1 | BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | 1 | BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_A_HP_STEAM_ENTHALPY | 1 | BOILER_A_HP_STEAM_ENTHALPY | no sensor in PEEO
BFW_FLOW_TO_DESUPERHEATER_A[sensor:UN.UO.71FI1102.PV] | 1 | BFW_FLOW_TO_DESUPERHEATER_A | sensor:UN.UO.71FI1102.PV
BFW_FLOW_TO_ECOMONIZER_A[sensor:UN.UO.71FI1103.PV] | 1 | BFW_FLOW_TO_ECOMONIZER_A | sensor:UN.UO.71FI1103.PV
BOILER_A_BFW_ENTHALPY | 1 | BOILER_A_BFW_ENTHALPY | no sensor in PEEO
BOILER_A_FUEL_GAS_ENERGY_INPUT | 1 | BOILER_A_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_A_STACK_LOSS | 1 | BOILER_A_STACK_LOSS | no sensor in PEEO
BOILER_A_LMTD_ECONOMIZER | 1 | BOILER_A_LMTD_ECONOMIZER | no sensor in PEEO
BOILER_A_UA_ECONOMIZER | 1 | BOILER_A_UA_ECONOMIZER | no sensor in PEEO
DESUPERHEATER_TEMPERATURE[sensor:UN.UO.71TI1106.PV] | 1 | DESUPERHEATER_TEMPERATURE | sensor:UN.UO.71TI1106.PV
BOILER_A_SH_SPECIFIC_DUTY | 1 | BOILER_A_SH_SPECIFIC_DUTY | no sensor in PEEO
BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | 1 | BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | no sensor in PEEO
BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION | 1 | BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION | no sensor in PEEO
BOILER_B_FG_DENSITY | 1 | BOILER_B_FG_DENSITY | no sensor in PEEO
BOILER_B_FG_NITROGEN_MASS_FRACTION | 1 | BOILER_B_FG_NITROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION | no sensor in PEEO
BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 1 | BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | no sensor in PEEO
BOILER_B_CH4_CO2_COMBUSTION | 1 | BOILER_B_CH4_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_ETHANE_CO2_COMBUSTION | 1 | BOILER_B_ETHANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_ETHYLENE_CO2_COMBUSTION | 1 | BOILER_B_ETHYLENE_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_IC4_CO2_COMBUSTION | 1 | BOILER_B_IC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_IC5_CO2_COMBUSTION | 1 | BOILER_B_IC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_NC4_CO2_COMBUSTION | 1 | BOILER_B_NC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_NC5_CO2_COMBUSTION | 1 | BOILER_B_NC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_PROPANE_CO2_COMBUSTION | 1 | BOILER_B_PROPANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_B_CH4_N2_COMBUSTION | 1 | BOILER_B_CH4_N2_COMBUSTION | no sensor in PEEO
BOILER_B_ETHANE_N2_COMBUSTION | 1 | BOILER_B_ETHANE_N2_COMBUSTION | no sensor in PEEO
BOILER_B_ETHYLENE_N2_COMBUSTION | 1 | BOILER_B_ETHYLENE_N2_COMBUSTION | no sensor in PEEO
BOILER_B_H2_N2_COMBUSTION | 1 | BOILER_B_H2_N2_COMBUSTION | no sensor in PEEO
BOILER_B_IC4_N2_COMBUSTION | 1 | BOILER_B_IC4_N2_COMBUSTION | no sensor in PEEO
BOILER_B_IC5_N2_COMBUSTION | 1 | BOILER_B_IC5_N2_COMBUSTION | no sensor in PEEO
BOILER_B_NC4_N2_COMBUSTION | 1 | BOILER_B_NC4_N2_COMBUSTION | no sensor in PEEO
BOILER_B_NC5_N2_COMBUSTION | 1 | BOILER_B_NC5_N2_COMBUSTION | no sensor in PEEO
BOILER_B_PROPANE_N2_COMBUSTION | 1 | BOILER_B_PROPANE_N2_COMBUSTION | no sensor in PEEO
BOILER_B_CH4_H2O_COMBUSTION | 1 | BOILER_B_CH4_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_ETHANE_H2O_COMBUSTION | 1 | BOILER_B_ETHANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_ETHYLENE_H2O_COMBUSTION | 1 | BOILER_B_ETHYLENE_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_H2_H2O_COMBUSTION | 1 | BOILER_B_H2_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_IC4_H2O_COMBUSTION | 1 | BOILER_B_IC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_IC5_H2O_COMBUSTION | 1 | BOILER_B_IC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_NC4_H2O_COMBUSTION | 1 | BOILER_B_NC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_NC5_H2O_COMBUSTION | 1 | BOILER_B_NC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_PROPANE_H2O_COMBUSTION | 1 | BOILER_B_PROPANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_B_CORRECTED_COMBUTION_H2O_FORMED | 1 | BOILER_B_CORRECTED_COMBUTION_H2O_FORMED | no sensor in PEEO
BOILER_B_TOTAL_MOISTURE_WITH_AIR | 1 | BOILER_B_TOTAL_MOISTURE_WITH_AIR | no sensor in PEEO
BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | 1 | BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | no sensor in PEEO
BOILER_B_CP_CH4_FUEL_TEMP | 1 | BOILER_B_CP_CH4_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_ETHANE_FUEL_TEMP | 1 | BOILER_B_CP_ETHANE_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_ETHYLENE_FUEL_TEMP | 1 | BOILER_B_CP_ETHYLENE_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_H2_FUEL_TEMP | 1 | BOILER_B_CP_H2_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_IC4_FUEL_TEMP | 1 | BOILER_B_CP_IC4_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_IC5_FUEL_TEMP | 1 | BOILER_B_CP_IC5_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_NC4_FUEL_TEMP | 1 | BOILER_B_CP_NC4_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_NC5_FUEL_TEMP | 1 | BOILER_B_CP_NC5_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_PROPANE_FUEL_TEMP | 1 | BOILER_B_CP_PROPANE_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP | 1 | BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP | no sensor in PEEO
BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP | 1 | BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP | no sensor in PEEO
BOILER_B_FLUE_GAS_MW | 1 | BOILER_B_FLUE_GAS_MW | no sensor in PEEO
BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR | 1 | BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR | no sensor in PEEO
BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | 1 | BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | no sensor in PEEO
BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1 | BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | no sensor in PEEO
BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1 | BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | no sensor in PEEO
BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | 1 | BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | no sensor in PEEO
BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | 1 | BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | no sensor in PEEO
BOILER_B_RADIATION_LOSSES | 1 | BOILER_B_RADIATION_LOSSES | no sensor in PEEO
BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 1 | BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | 1 | BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_B_HP_STEAM_ENTHALPY | 1 | BOILER_B_HP_STEAM_ENTHALPY | no sensor in PEEO
BFW_FLOW_TO_DESUPERHEATER_B[sensor:UN.UO.71FI1202.PV] | 1 | BFW_FLOW_TO_DESUPERHEATER_B | sensor:UN.UO.71FI1202.PV
BFW_FLOW_TO_ECONOMIZER_B[sensor:UN.UO.71FI1203.PV] | 1 | BFW_FLOW_TO_ECONOMIZER_B | sensor:UN.UO.71FI1203.PV
BOILER_B_BFW_ENTHALPY | 1 | BOILER_B_BFW_ENTHALPY | no sensor in PEEO
BOILER_B_FUEL_GAS_ENERGY_INPUT | 1 | BOILER_B_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_B_STACK_LOSS | 1 | BOILER_B_STACK_LOSS | no sensor in PEEO
BOILER_B_LMTD_ECONOMIZER | 1 | BOILER_B_LMTD_ECONOMIZER | no sensor in PEEO
BOILER_B_UA_ECONOMIZER | 1 | BOILER_B_UA_ECONOMIZER | no sensor in PEEO
BOILER_B_SH_SPECIFIC_DUTY | 1 | BOILER_B_SH_SPECIFIC_DUTY | no sensor in PEEO
BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | 1 | BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | no sensor in PEEO
BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION | 1 | BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION | no sensor in PEEO
BOILER_C_FG_DENSITY | 1 | BOILER_C_FG_DENSITY | no sensor in PEEO
BOILER_C_FG_NITROGEN_MASS_FRACTION | 1 | BOILER_C_FG_NITROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION | no sensor in PEEO
BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 1 | BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | no sensor in PEEO
BOILER_C_CH4_CO2_COMBUSTION | 1 | BOILER_C_CH4_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_ETHANE_CO2_COMBUSTION | 1 | BOILER_C_ETHANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_ETHYLENE_CO2_COMBUSTION | 1 | BOILER_C_ETHYLENE_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_IC4_CO2_COMBUSTION | 1 | BOILER_C_IC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_IC5_CO2_COMBUSTION | 1 | BOILER_C_IC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_NC4_CO2_COMBUSTION | 1 | BOILER_C_NC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_NC5_CO2_COMBUSTION | 1 | BOILER_C_NC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_PROPANE_CO2_COMBUSTION | 1 | BOILER_C_PROPANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_C_CH4_N2_COMBUSTION | 1 | BOILER_C_CH4_N2_COMBUSTION | no sensor in PEEO
BOILER_C_ETHANE_N2_COMBUSTION | 1 | BOILER_C_ETHANE_N2_COMBUSTION | no sensor in PEEO
BOILER_C_ETHYLENE_N2_COMBUSTION | 1 | BOILER_C_ETHYLENE_N2_COMBUSTION | no sensor in PEEO
BOILER_C_H2_N2_COMBUSTION | 1 | BOILER_C_H2_N2_COMBUSTION | no sensor in PEEO
BOILER_C_IC4_N2_COMBUSTION | 1 | BOILER_C_IC4_N2_COMBUSTION | no sensor in PEEO
BOILER_C_IC5_N2_COMBUSTION | 1 | BOILER_C_IC5_N2_COMBUSTION | no sensor in PEEO
BOILER_C_NC4_N2_COMBUSTION | 1 | BOILER_C_NC4_N2_COMBUSTION | no sensor in PEEO
BOILER_C_NC5_N2_COMBUSTION | 1 | BOILER_C_NC5_N2_COMBUSTION | no sensor in PEEO
BOILER_C_PROPANE_N2_COMBUSTION | 1 | BOILER_C_PROPANE_N2_COMBUSTION | no sensor in PEEO
BOILER_C_CH4_H2O_COMBUSTION | 1 | BOILER_C_CH4_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_ETHANE_H2O_COMBUSTION | 1 | BOILER_C_ETHANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_ETHYLENE_H2O_COMBUSTION | 1 | BOILER_C_ETHYLENE_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_H2_H2O_COMBUSTION | 1 | BOILER_C_H2_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_IC4_H2O_COMBUSTION | 1 | BOILER_C_IC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_IC5_H2O_COMBUSTION | 1 | BOILER_C_IC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_NC4_H2O_COMBUSTION | 1 | BOILER_C_NC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_NC5_H2O_COMBUSTION | 1 | BOILER_C_NC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_PROPANE_H2O_COMBUSTION | 1 | BOILER_C_PROPANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_C_CORRECTED_COMBUTION_H2O_FORMED | 1 | BOILER_C_CORRECTED_COMBUTION_H2O_FORMED | no sensor in PEEO
BOILER_C_TOTAL_MOISTURE_WITH_AIR | 1 | BOILER_C_TOTAL_MOISTURE_WITH_AIR | no sensor in PEEO
BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | 1 | BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | no sensor in PEEO
BOILER_C_CP_CH4_FUEL_TEMP | 1 | BOILER_C_CP_CH4_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_ETHANE_FUEL_TEMP | 1 | BOILER_C_CP_ETHANE_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_ETHYLENE_FUEL_TEMP | 1 | BOILER_C_CP_ETHYLENE_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_H2_FUEL_TEMP | 1 | BOILER_C_CP_H2_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_IC4_FUEL_TEMP | 1 | BOILER_C_CP_IC4_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_IC5_FUEL_TEMP | 1 | BOILER_C_CP_IC5_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_NC4_FUEL_TEMP | 1 | BOILER_C_CP_NC4_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_NC5_FUEL_TEMP | 1 | BOILER_C_CP_NC5_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_PROPANE_FUEL_TEMP | 1 | BOILER_C_CP_PROPANE_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP | 1 | BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP | no sensor in PEEO
BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP | 1 | BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP | no sensor in PEEO
BOILER_C_FLUE_GAS_MW | 1 | BOILER_C_FLUE_GAS_MW | no sensor in PEEO
BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR | 1 | BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR | no sensor in PEEO
BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | 1 | BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | no sensor in PEEO
BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1 | BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | no sensor in PEEO
BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1 | BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | no sensor in PEEO
BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | 1 | BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | no sensor in PEEO
BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | 1 | BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | no sensor in PEEO
BOILER_C_RADIATION_LOSSES | 1 | BOILER_C_RADIATION_LOSSES | no sensor in PEEO
BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 1 | BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | 1 | BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_C_HP_STEAM_ENTHALPY | 1 | BOILER_C_HP_STEAM_ENTHALPY | no sensor in PEEO
BFW_FLOW_TO_DESUPERHEATER_C[sensor:UN.UO.71FI1302.PV] | 1 | BFW_FLOW_TO_DESUPERHEATER_C | sensor:UN.UO.71FI1302.PV
BFW_FLOW_TO_ECONOMIZER_C[sensor:UN.UO.71FI1303.PV] | 1 | BFW_FLOW_TO_ECONOMIZER_C | sensor:UN.UO.71FI1303.PV
BOILER_C_BFW_ENTHALPY | 1 | BOILER_C_BFW_ENTHALPY | no sensor in PEEO
BOILER_C_FUEL_GAS_ENERGY_INPUT | 1 | BOILER_C_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_C_STACK_LOSS | 1 | BOILER_C_STACK_LOSS | no sensor in PEEO
BOILER_C_LMTD_ECONOMIZER | 1 | BOILER_C_LMTD_ECONOMIZER | no sensor in PEEO
BOILER_C_UA_ECONOMIZER | 1 | BOILER_C_UA_ECONOMIZER | no sensor in PEEO
BOILER_C_SH_SPECIFIC_DUTY | 1 | BOILER_C_SH_SPECIFIC_DUTY | no sensor in PEEO
BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | 1 | BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | no sensor in PEEO
BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION | 1 | BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION | no sensor in PEEO
BOILER_D_FG_DENSITY | 1 | BOILER_D_FG_DENSITY | no sensor in PEEO
BOILER_D_FG_NITROGEN_MASS_FRACTION | 1 | BOILER_D_FG_NITROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION | no sensor in PEEO
BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 1 | BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | no sensor in PEEO
BOILER_D_CH4_CO2_COMBUSTION | 1 | BOILER_D_CH4_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_ETHANE_CO2_COMBUSTION | 1 | BOILER_D_ETHANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_ETHYLENE_CO2_COMBUSTION | 1 | BOILER_D_ETHYLENE_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_IC4_CO2_COMBUSTION | 1 | BOILER_D_IC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_IC5_CO2_COMBUSTION | 1 | BOILER_D_IC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_NC4_CO2_COMBUSTION | 1 | BOILER_D_NC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_NC5_CO2_COMBUSTION | 1 | BOILER_D_NC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_PROPANE_CO2_COMBUSTION | 1 | BOILER_D_PROPANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_D_CH4_N2_COMBUSTION | 1 | BOILER_D_CH4_N2_COMBUSTION | no sensor in PEEO
BOILER_D_ETHANE_N2_COMBUSTION | 1 | BOILER_D_ETHANE_N2_COMBUSTION | no sensor in PEEO
BOILER_D_ETHYLENE_N2_COMBUSTION | 1 | BOILER_D_ETHYLENE_N2_COMBUSTION | no sensor in PEEO
BOILER_D_H2_N2_COMBUSTION | 1 | BOILER_D_H2_N2_COMBUSTION | no sensor in PEEO
BOILER_D_IC4_N2_COMBUSTION | 1 | BOILER_D_IC4_N2_COMBUSTION | no sensor in PEEO
BOILER_D_IC5_N2_COMBUSTION | 1 | BOILER_D_IC5_N2_COMBUSTION | no sensor in PEEO
BOILER_D_NC4_N2_COMBUSTION | 1 | BOILER_D_NC4_N2_COMBUSTION | no sensor in PEEO
BOILER_D_NC5_N2_COMBUSTION | 1 | BOILER_D_NC5_N2_COMBUSTION | no sensor in PEEO
BOILER_D_PROPANE_N2_COMBUSTION | 1 | BOILER_D_PROPANE_N2_COMBUSTION | no sensor in PEEO
BOILER_D_CH4_H2O_COMBUSTION | 1 | BOILER_D_CH4_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_ETHANE_H2O_COMBUSTION | 1 | BOILER_D_ETHANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_ETHYLENE_H2O_COMBUSTION | 1 | BOILER_D_ETHYLENE_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_H2_H2O_COMBUSTION | 1 | BOILER_D_H2_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_IC4_H2O_COMBUSTION | 1 | BOILER_D_IC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_IC5_H2O_COMBUSTION | 1 | BOILER_D_IC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_NC4_H2O_COMBUSTION | 1 | BOILER_D_NC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_NC5_H2O_COMBUSTION | 1 | BOILER_D_NC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_PROPANE_H2O_COMBUSTION | 1 | BOILER_D_PROPANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_D_CORRECTED_COMBUTION_H2O_FORMED | 1 | BOILER_D_CORRECTED_COMBUTION_H2O_FORMED | no sensor in PEEO
BOILER_D_TOTAL_MOISTURE_WITH_AIR | 1 | BOILER_D_TOTAL_MOISTURE_WITH_AIR | no sensor in PEEO
BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | 1 | BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | no sensor in PEEO
BOILER_D_CP_CH4_FUEL_TEMP | 1 | BOILER_D_CP_CH4_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_ETHANE_FUEL_TEMP | 1 | BOILER_D_CP_ETHANE_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_ETHYLENE_FUEL_TEMP | 1 | BOILER_D_CP_ETHYLENE_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_H2_FUEL_TEMP | 1 | BOILER_D_CP_H2_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_IC4_FUEL_TEMP | 1 | BOILER_D_CP_IC4_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_IC5_FUEL_TEMP | 1 | BOILER_D_CP_IC5_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_NC4_FUEL_TEMP | 1 | BOILER_D_CP_NC4_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_NC5_FUEL_TEMP | 1 | BOILER_D_CP_NC5_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_PROPANE_FUEL_TEMP | 1 | BOILER_D_CP_PROPANE_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP | 1 | BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP | no sensor in PEEO
BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP | 1 | BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP | no sensor in PEEO
BOILER_D_FLUE_GAS_MW | 1 | BOILER_D_FLUE_GAS_MW | no sensor in PEEO
BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR | 1 | BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR | no sensor in PEEO
BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | 1 | BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | no sensor in PEEO
BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1 | BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | no sensor in PEEO
BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1 | BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | no sensor in PEEO
BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | 1 | BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | no sensor in PEEO
BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | 1 | BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | no sensor in PEEO
BOILER_D_RADIATION_LOSSES | 1 | BOILER_D_RADIATION_LOSSES | no sensor in PEEO
BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 1 | BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | 1 | BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_D_HP_STEAM_ENTHALPY | 1 | BOILER_D_HP_STEAM_ENTHALPY | no sensor in PEEO
BFW_FLOW_TO_DESUPERHEATER_D[sensor:UN.UO.71FI1402.PV] | 1 | BFW_FLOW_TO_DESUPERHEATER_D | sensor:UN.UO.71FI1402.PV
BFW_FLOW_TO_ECONOMIZER_D[sensor:UN.UO.71FI1403.PV] | 1 | BFW_FLOW_TO_ECONOMIZER_D | sensor:UN.UO.71FI1403.PV
BOILER_D_BFW_ENTHALPY | 1 | BOILER_D_BFW_ENTHALPY | no sensor in PEEO
BOILER_D_FUEL_GAS_ENERGY_INPUT | 1 | BOILER_D_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_D_STACK_LOSS | 1 | BOILER_D_STACK_LOSS | no sensor in PEEO
BOILER_D_LMTD_ECONOMIZER | 1 | BOILER_D_LMTD_ECONOMIZER | no sensor in PEEO
BOILER_D_UA_ECONOMIZER | 1 | BOILER_D_UA_ECONOMIZER | no sensor in PEEO
BOILER_D_SH_SPECIFIC_DUTY | 1 | BOILER_D_SH_SPECIFIC_DUTY | no sensor in PEEO
BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | 1 | BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | no sensor in PEEO
BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION | 1 | BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION | no sensor in PEEO
BOILER_E_FG_DENSITY | 1 | BOILER_E_FG_DENSITY | no sensor in PEEO
BOILER_E_FG_NITROGEN_MASS_FRACTION | 1 | BOILER_E_FG_NITROGEN_MASS_FRACTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION | no sensor in PEEO
BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | 1 | BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | no sensor in PEEO
BOILER_E_CH4_CO2_COMBUSTION | 1 | BOILER_E_CH4_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_ETHANE_CO2_COMBUSTION | 1 | BOILER_E_ETHANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_ETHYLENE_CO2_COMBUSTION | 1 | BOILER_E_ETHYLENE_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_IC4_CO2_COMBUSTION | 1 | BOILER_E_IC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_IC5_CO2_COMBUSTION | 1 | BOILER_E_IC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_NC4_CO2_COMBUSTION | 1 | BOILER_E_NC4_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_NC5_CO2_COMBUSTION | 1 | BOILER_E_NC5_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_PROPANE_CO2_COMBUSTION | 1 | BOILER_E_PROPANE_CO2_COMBUSTION | no sensor in PEEO
BOILER_E_CH4_N2_COMBUSTION | 1 | BOILER_E_CH4_N2_COMBUSTION | no sensor in PEEO
BOILER_E_ETHANE_N2_COMBUSTION | 1 | BOILER_E_ETHANE_N2_COMBUSTION | no sensor in PEEO
BOILER_E_ETHYLENE_N2_COMBUSTION | 1 | BOILER_E_ETHYLENE_N2_COMBUSTION | no sensor in PEEO
BOILER_E_H2_N2_COMBUSTION | 1 | BOILER_E_H2_N2_COMBUSTION | no sensor in PEEO
BOILER_E_IC4_N2_COMBUSTION | 1 | BOILER_E_IC4_N2_COMBUSTION | no sensor in PEEO
BOILER_E_IC5_N2_COMBUSTION | 1 | BOILER_E_IC5_N2_COMBUSTION | no sensor in PEEO
BOILER_E_NC4_N2_COMBUSTION | 1 | BOILER_E_NC4_N2_COMBUSTION | no sensor in PEEO
BOILER_E_NC5_N2_COMBUSTION | 1 | BOILER_E_NC5_N2_COMBUSTION | no sensor in PEEO
BOILER_E_PROPANE_N2_COMBUSTION | 1 | BOILER_E_PROPANE_N2_COMBUSTION | no sensor in PEEO
BOILER_E_CH4_H2O_COMBUSTION | 1 | BOILER_E_CH4_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_ETHANE_H2O_COMBUSTION | 1 | BOILER_E_ETHANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_ETHYLENE_H2O_COMBUSTION | 1 | BOILER_E_ETHYLENE_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_H2_H2O_COMBUSTION | 1 | BOILER_E_H2_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_IC4_H2O_COMBUSTION | 1 | BOILER_E_IC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_IC5_H2O_COMBUSTION | 1 | BOILER_E_IC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_NC4_H2O_COMBUSTION | 1 | BOILER_E_NC4_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_NC5_H2O_COMBUSTION | 1 | BOILER_E_NC5_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_PROPANE_H2O_COMBUSTION | 1 | BOILER_E_PROPANE_H2O_COMBUSTION | no sensor in PEEO
BOILER_E_CORRECTED_COMBUTION_H2O_FORMED | 1 | BOILER_E_CORRECTED_COMBUTION_H2O_FORMED | no sensor in PEEO
BOILER_E_TOTAL_MOISTURE_WITH_AIR | 1 | BOILER_E_TOTAL_MOISTURE_WITH_AIR | no sensor in PEEO
BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | 1 | BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | no sensor in PEEO
BOILER_E_CP_CH4_FUEL_TEMP | 1 | BOILER_E_CP_CH4_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_ETHANE_FUEL_TEMP | 1 | BOILER_E_CP_ETHANE_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_ETHYLENE_FUEL_TEMP | 1 | BOILER_E_CP_ETHYLENE_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_H2_FUEL_TEMP | 1 | BOILER_E_CP_H2_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_IC4_FUEL_TEMP | 1 | BOILER_E_CP_IC4_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_IC5_FUEL_TEMP | 1 | BOILER_E_CP_IC5_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_NC4_FUEL_TEMP | 1 | BOILER_E_CP_NC4_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_NC5_FUEL_TEMP | 1 | BOILER_E_CP_NC5_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_PROPANE_FUEL_TEMP | 1 | BOILER_E_CP_PROPANE_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP | 1 | BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP | no sensor in PEEO
BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP | 1 | BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP | no sensor in PEEO
BOILER_E_FLUE_GAS_MW | 1 | BOILER_E_FLUE_GAS_MW | no sensor in PEEO
BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | 1 | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | no sensor in PEEO
BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR | 1 | BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR | no sensor in PEEO
BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | 1 | BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | no sensor in PEEO
BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | 1 | BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | no sensor in PEEO
BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | 1 | BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | no sensor in PEEO
BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | 1 | BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | no sensor in PEEO
BOILER_E_RADIATION_LOSSES | 1 | BOILER_E_RADIATION_LOSSES | no sensor in PEEO
BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | 1 | BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | 1 | BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | no sensor in PEEO
BOILER_E_HP_STEAM_ENTHALPY | 1 | BOILER_E_HP_STEAM_ENTHALPY | no sensor in PEEO
BFW_FLOW_TO_DESUPERHEATER_E[sensor:UN.UO.71FC1502.PV] | 1 | BFW_FLOW_TO_DESUPERHEATER_E | sensor:UN.UO.71FC1502.PV
BFW_FLOW_TO_ECONOMIZER_E[sensor:UN.UO.71FC1503.PV] | 1 | BFW_FLOW_TO_ECONOMIZER_E | sensor:UN.UO.71FC1503.PV
BOILER_E_BFW_ENTHALPY | 1 | BOILER_E_BFW_ENTHALPY | no sensor in PEEO
BOILER_E_FUEL_GAS_ENERGY_INPUT | 1 | BOILER_E_FUEL_GAS_ENERGY_INPUT | no sensor in PEEO
BOILER_E_STACK_LOSS | 1 | BOILER_E_STACK_LOSS | no sensor in PEEO
BOILER_E_LMTD_ECONOMIZER | 1 | BOILER_E_LMTD_ECONOMIZER | no sensor in PEEO
BOILER_E_UA_ECONOMIZER | 1 | BOILER_E_UA_ECONOMIZER | no sensor in PEEO
BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | 1 | BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | no sensor in PEEO
BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | 1 | BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | no sensor in PEEO
BOILER_A_BOILER_INDIRECT_EFFICIENCY | 1 | BOILER_A_BOILER_INDIRECT_EFFICIENCY | no sensor in PEEO
BOILER_B_BOILER_INDIRECT_EFFICIENCY | 1 | BOILER_B_BOILER_INDIRECT_EFFICIENCY | no sensor in PEEO
BOILER_C_BOILER_INDIRECT_EFFICIENCY | 1 | BOILER_C_BOILER_INDIRECT_EFFICIENCY | no sensor in PEEO
BOILER_D_BOILER_INDIRECT_EFFICIENCY | 1 | BOILER_D_BOILER_INDIRECT_EFFICIENCY | no sensor in PEEO
BOILER_E_BOILER_INDIRECT_EFFICIENCY | 1 | BOILER_E_BOILER_INDIRECT_EFFICIENCY | no sensor in PEEO
TOTAL_STEAM_ENERGY | 1 | TOTAL_STEAM_ENERGY | no sensor in PEEO
BOILER_A_SUPERHEATED_STEAM_BFW_RATIO | 1 | BOILER_A_SUPERHEATED_STEAM_BFW_RATIO | no sensor in PEEO
BOILER_B_SUPERHEATED_STEAM_BFW_RATIO | 1 | BOILER_B_SUPERHEATED_STEAM_BFW_RATIO | no sensor in PEEO
BOILER_C_SUPERHEATED_STEAM_BFW_RATIO | 1 | BOILER_C_SUPERHEATED_STEAM_BFW_RATIO | no sensor in PEEO
BOILER_D_SUPERHEATED_STEAM_BFW_RATIO | 1 | BOILER_D_SUPERHEATED_STEAM_BFW_RATIO | no sensor in PEEO
BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | 1 | BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | no sensor in PEEO
BOILER_A_CO2_EMISSIONS | 1 | BOILER_A_CO2_EMISSIONS | no sensor in PEEO
BOILER_B_CO2_EMISSIONS | 1 | BOILER_B_CO2_EMISSIONS | no sensor in PEEO
BOILER_C_CO2_EMISSIONS | 1 | BOILER_C_CO2_EMISSIONS | no sensor in PEEO
BOILER_D_CO2_EMISSIONS | 1 | BOILER_D_CO2_EMISSIONS | no sensor in PEEO
BOILER_E_CO2_EMISSIONS | 1 | BOILER_E_CO2_EMISSIONS | no sensor in PEEO
BOILER_A_CONDUCTIVITY[sensor:UN.UO.71AC1101.PV] | 1 | BOILER_A_CONDUCTIVITY | sensor:UN.UO.71AC1101.PV
BOILER_B_CONDUCTIVITY[sensor:UN.UO.71AC1201.PV] | 1 | BOILER_B_CONDUCTIVITY | sensor:UN.UO.71AC1201.PV
BOILER_C_CONDUCTIVITY[sensor:UN.UO.71AC1301.PV] | 1 | BOILER_C_CONDUCTIVITY | sensor:UN.UO.71AC1301.PV
BOILER_D_CONDUCTIVITY[sensor:UN.UO.71AC1401.PV] | 1 | BOILER_D_CONDUCTIVITY | sensor:UN.UO.71AC1401.PV
BOILER_E_CONDUCTIVITY[sensor:UN.UO.71AC1501A.PV] | 1 | BOILER_E_CONDUCTIVITY | sensor:UN.UO.71AC1501A.PV
STEAM_PRESS | 1 | STEAM_PRESS | no sensor in PEEO
STEAM_TEMP | 1 | STEAM_TEMP | no sensor in PEEO
BOILER_E_NOX[sensor:UN.UO.71AI1505A1.PV] | 1 | BOILER_E_NOX | sensor:UN.UO.71AI1505A1.PV
STEAM_MARGIN_TPH | 1 | STEAM_MARGIN_TPH | no sensor in PEEO
NUMBER_OF_BOILERS_ONLINE | 1 | NUMBER_OF_BOILERS_ONLINE | no sensor in PEEO
STEAM_MARGIN_NUMBER | 1 | STEAM_MARGIN_NUMBER | no sensor in PEEO
BFW_CONDUCTIVITY[sensor:UN.UO.71AI1005B.PV] | 1 | BFW_CONDUCTIVITY | sensor:UN.UO.71AI1005B.PV
BFW_OXYGEN[sensor:UN.UO.71AI1001.PV] | 1 | BFW_OXYGEN | sensor:UN.UO.71AI1001.PV
BFW_PH[sensor:UN.UO.71AI1005A.PV] | 1 | BFW_PH | sensor:UN.UO.71AI1005A.PV
BFW_SILICA[sensor:UN.UO.71AI1002.PV] | 1 | BFW_SILICA | sensor:UN.UO.71AI1002.PV
BFW_SODIUM[sensor:UN.UO.71AI1004.PV] | 1 | BFW_SODIUM | sensor:UN.UO.71AI1004.PV

## All_Results
tag_name | description | uom | category | formula | status | value | reason_if_not | missing_inputs
Timestamp | Timestamp | nan | fixed,LBM_,362_DM_ |  | NOT COMPUTED |  | No formula defined and no PI value
BOILER_E_STEAM_DRUM_PRESSURE | BOILER E STEAM DRUM PRESSURE | nan | LBM_preprocessing_inferred_tags_main | if(HP_STEAM_PRESSURE_FROM_DS_E==MISSING_NUMERIC,0,HP_STEAM_PRESSURE_FROM_DS_E) | COMPUTED | 1.884
LHV_H2_HYDROGEN | LHV H2 HYDROGEN | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 120.004 | COMPUTED | 120.004
LHV_CH4_METHANE | LHV CH4 METHANE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 50.026 | COMPUTED | 50.026
LHV_H2O_WATER | LHV H2O WATER | MJ/KG | LBM_preprocessing_inferred_tags_main | 0 | COMPUTED | 0
LHV_N2_NITROGEN | LHV N2 NITROGEN | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 0 | COMPUTED | 0
LHV_C2H4_ETHYLENE | LHV C2H4 ETHYLENE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 47.178 | COMPUTED | 47.178
LHV_C2H6_ETHANE | LHV C2H6 ETHANE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 47.497 | COMPUTED | 47.497
LHV_C3H8_PROPANE | LHV C3H8 PROPANE | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 46.362 | COMPUTED | 46.362
LHV_BUTANE | LHV BUTANE | MJ/KG | LBM_preprocessing_inferred_tags_main | 45.689 | COMPUTED | 45.689
LHV_CO | LHV CO | MJ/KG | LBM_preprocessing_inferred_tags_main | 10.105 | COMPUTED | 10.105
LHV_PENTANE | LHV PENTANE | MJ/KG | LBM_preprocessing_inferred_tags_main | 45.35 | COMPUTED | 45.35
LHV_NC4 | LHV NC4 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.75 | COMPUTED | 45.75
LHV_IC4 | LHV IC4 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.613 | COMPUTED | 45.613
LHV_NC5 | LHV NC5 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.36 | COMPUTED | 45.36
LHV_IC5 | LHV IC5 | MJ/KG | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 45.241 | COMPUTED | 45.241
LHV_FG | LHV FG | MJ/KG | LBM_preprocessing_inferred_tags_main | 31316 | COMPUTED | 31316
LHV_FG_E_DESIGN | LHV FG E | - | LBM_preprocessing_inferred_tags_main | 45108 | COMPUTED | 45108
COMPONENT_HYDROGEN_MW | COMPONENT HYDROGEN MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 2.016 | COMPUTED | 2.016
COMPONENT_NITROGEN_MW | COMPONENT NITROGEN MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 28.016 | COMPUTED | 28.016
COMPONENT_CO_MW | COMPONENT CO MW | g/gmol | LBM_preprocessing_inferred_tags_main | 28.01 | COMPUTED | 28.01
COMPONENT_METHANE_MW | COMPONENT METHANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 16.04 | COMPUTED | 16.04
COMPONENT_ETHANE_MW | COMPONENT ETHANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 30.07 | COMPUTED | 30.07
COMPONENT_PROPANE_MW | COMPONENT PROPANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 44.09 | COMPUTED | 44.09
COMPONENT_ETHYLENE_MW | COMPONENT ETHYLENE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 28.051 | COMPUTED | 28.051
COMPONENT_PENTANE_MW | COMPONENT PENTANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 72.15 | COMPUTED | 72.15
COMPONENT_BUTANE_MW | COMPONENT BUTANE MW | g/gmol | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 58.12 | COMPUTED | 58.12
BOILER_A_AIR_CP_REF_T | BOILER A AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | COMPUTED | 6.96
BOILER_B_AIR_CP_REF_T | BOILER B AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | COMPUTED | 6.96
BOILER_C_AIR_CP_REF_T | BOILER C AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | COMPUTED | 6.96
BOILER_D_AIR_CP_REF_T | BOILER D AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | COMPUTED | 6.96
BOILER_E_AIR_CP_REF_T | BOILER E AIR CP REF T | cal/kgK | LBM_preprocessing_inferred_tags_main | 6.96 | COMPUTED | 6.96
RELATIVE_HUMIDITY_CLEAN | RELATIVE HUMIDITY | % | LBM_preprocessing_inferred_tags_main | if((abs(RELATIVE_HUMIDITY)<1 && abs(RELATIVE_HUMIDITY)>0),abs(RELATIVE_HUMIDITY),0.6) | COMPUTED | 0.17
BOILER_A_BOILER_LOAD | BOILER A BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.7975
BOILER_B_BOILER_LOAD | BOILER B BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_B_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.8401
BOILER_C_BOILER_LOAD | BOILER C BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_C_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.7993
BOILER_D_BOILER_LOAD | BOILER D BOILER LOAD | % | LBM_preprocessing_inferred_tags_main | DESUPERHEATER_D_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.8534
BOILER_E_BOILER_LOAD | BOILER E BOILER LOAD | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | DESUPERHEATER_E_OUTLET_STEAM_FLOW/150000*100 | COMPUTED | 1.8692
BOILER_A_STATUS | BOILER A STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_A_BOILER_LOAD>25&&DESUPERHEATER_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS>40,1,0) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] | HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV]
BOILER_B_STATUS | BOILER B STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_B_BOILER_LOAD>25&&DESUPERHEATER_B_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_B>40,1,0) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] | HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV]
BOILER_C_STATUS | BOILER C STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_C_BOILER_LOAD>25&&DESUPERHEATER_C_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_C>40,1,0) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] | HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV]
BOILER_D_STATUS | BOILER D STATUS | - | LBM_preprocessing_inferred_tags_main | if(BOILER_D_BOILER_LOAD>25&&DESUPERHEATER_D_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_D>40,1,0) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV] | HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV]
BOILER_E_STATUS | BOILER E STATUS | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(BOILER_E_BOILER_LOAD>25&&DESUPERHEATER_E_OUTLET_TEMPERATURE>370&&HP_STEAM_PRESSURE_FROM_DS_E>40,1,0) | COMPUTED | 0
BOILERS_ONLINE | BOILERS ONLINE | - | LBM_preprocessing_inferred_tags_main | BOILER_A_STATUS+BOILER_B_STATUS+BOILER_C_STATUS+BOILER_D_STATUS+BOILER_E_STATUS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
plant_status | plant status | nan | LBM_preprocessing_inferred_tags_main | if(BOILERS_ONLINE==0,0,1) | NOT COMPUTED |  | Unknown/no sensor: BOILERS_ONLINE | BOILERS_ONLINE
ARRAZI_PLANT_LOAD_1 | ARRAZI PLANT LOAD 1 | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_LOAD==MISSING_NUMERIC,0,ARRAZI_PLANT_LOAD) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ARRAZI_PLANT_LOAD[sensor:AR.AR5.DCS.Process.REFLOAD5.CPV] | ARRAZI_PLANT_LOAD[sensor:AR.AR5.DCS.Process.REFLOAD5.CPV]
ARRAZI_PLANT_STATUS | ARRAZI PLANT STATUS | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_LOAD_1<70,0,1) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_LOAD_1 | ARRAZI_PLANT_LOAD_1
BOILER_FG_ETHYLENE_CONCENTRATION | BOILER FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 0 | COMPUTED | 0
BOILER_FG_N2_CONCENTRATION | BOILER FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_N2_CONCENTRATION_ARRAZI,10.236) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_CH4_CONCENTRATION | BOILER FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CH4_CONCENTRATION_ARRAZI,87.548) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_ETHANE_CONCENTRATION | BOILER FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_ETHANE_CONCENTRATION_ARRAZI,1.569) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_PROPANE_CONCENTRATION | BOILER FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_PROPANE_CONCENTRATION_ARRAZI,.343) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_NC4_CONCENTRATION | BOILER FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC4_CONCENTRATION_ARRAZI,.115) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_IC4_CONCENTRATION | BOILER FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC4_CONCENTRATION_ARRAZI,.097) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_CO2_CONCENTRATION | BOILER FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_CO2_CONCENTRATION_ARRAZI,0) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_NC5_CONCENTRATION | BOILER FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_NC5_CONCENTRATION_ARRAZI,.001) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_IC5_CONCENTRATION | BOILER FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,BOILER_FG_IC5_CONCENTRATION_ARRAZI,.033) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_FG_HYDROGEN_CONCENTRATION | BOILER FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(ARRAZI_PLANT_STATUS==1,0,0) | NOT COMPUTED |  | Unknown/no sensor: ARRAZI_PLANT_STATUS | ARRAZI_PLANT_STATUS
BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER A FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | NORMALIZED BOILER A FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_FG_CH4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER A FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER A FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL | BOILER_A_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER A FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_A_FG_CO2_CONCENTRATION | NORMALIZED BOILER A FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | NORMALIZED BOILER A FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | NORMALIZED BOILER A FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | NORMALIZED BOILER A FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | NORMALIZED BOILER A FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | NORMALIZED BOILER A FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_FG_N2_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER A FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_A_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_A_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_A_FG_MW | BOILER A FG MW | G/MOL | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW+NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_A_F | NOT COMPUTED |  | Unknown/no sensor: NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION
BOILER_A_FG_CH4_MASS_PERCENTAGE | BOILER A FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_CH4_CONCENTRATION
BOILER_A_FG_ETHANE_MASS_PERCENTAGE | BOILER A FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHANE_CONCENTRATION
BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE | BOILER A FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_ETHYLENE_CONCENTRATION
BOILER_A_FG_PROPANE_MASS_PERCENTAGE | BOILER A FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_PROPANE_CONCENTRATION
BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | BOILER A FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_N2_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_N2_CONCENTRATION
BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE | BOILER A FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_HYDROGEN_CONCENTRATION
BOILER_A_FG_IC4_MASS_PERCENTAGE | BOILER A FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC4_CONCENTRATION
BOILER_A_FG_NC4_MASS_PERCENTAGE | BOILER A FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC4_CONCENTRATION
BOILER_A_FG_NC5_MASS_PERCENTAGE | BOILER A FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_NC5_CONCENTRATION
BOILER_A_FG_IC5_MASS_PERCENTAGE | BOILER A FG IC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_A_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION | BOILER_A_FG_MW ¦ NORMALIZED_BOILER_A_FG_IC5_CONCENTRATION
BOILER_A_FG_DENSITY | BOILER A FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_MW/22.414 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_MW | BOILER_A_FG_MW
BOILER_A_LHV_DESIGN | BOILER A LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_A_FG_DENSITY)/1000 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_DENSITY | BOILER_A_FG_DENSITY
TOTAL_FUEL_COMPOSTION_MASS | TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_A_FG_CH4_MASS_PERCENTAGE+BOILER_A_FG_ETHANE_MASS_PERCENTAGE+BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_A_FG_PROPANE_MASS_PERCENTAGE+BOILER_A_FG_NC4_MASS_PERCENTAGE+BOILER_A_FG_IC4_MASS_PERCENTAGE+BOILER_A_FG_NC5_MASS_PERCENTAGE+BOILER_A_FG_IC5_MASS_PERCENTAGE+BOILER_A_FG_NITROGEN_MASS_PERCENTAGE | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_A_FG_IC4_MASS_PERCENTAGE | BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_A_FG_IC4_MASS_PERCENTAGE ¦ BOILER_A_FG_IC5_MASS_PERCENTAGE ¦ BOILER_A_FG_NC4_MASS_PERCENTAGE ¦ BOILER_A_FG_NC5_MASS_PERCENTAGE ¦ BOILER_A_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_A_FG_PROPANE_MASS_PERCENTAGE
BOILER_A_FG_CH4_MASS_FRACTION | BOILER A FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_CH4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_CH4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER A FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_ETHANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER A FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_ETHYLENE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER A FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_PROPANE_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_PROPANE_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NITROGEN_MASS_FRACTION | BOILER A FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NITROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NITROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER A FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_HYDROGEN_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_IC4_MASS_FRACTION | BOILER A FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_IC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NC4_MASS_FRACTION | BOILER A FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_NC4_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC4_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_NC5_MASS_FRACTION | BOILER A FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_NC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_NC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_A_FG_IC5_MASS_FRACTION | BOILER A FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_A_FG_IC5_MASS_PERCENTAGE/TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS | BOILER_A_FG_IC5_MASS_PERCENTAGE ¦ TOTAL_FUEL_COMPOSTION_MASS
BOILER_LHV | BOILER LHV | Kcal/Kg | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_A_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_A_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_A_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_A_FG_ETHYLENE_MASS_FRACTION*LHV_C2H4_ETHYLENE+BOILER_A_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_A_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_A_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_A_F | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION ¦ BOILER_A_FG_IC5_MASS_FRACTION ¦ BOILER_A_FG_NC4_MASS_FRACTION ¦ BOILER_A_FG_NC5_MASS_FRACTION ¦ BOILER_A_FG_NITROGEN_MASS_FRACTION ¦ BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_FG_FLOW_RATE | BOILER A FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_A_FUEL_GAS_FLOW/1000 | COMPUTED | 0.17548
BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER A AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER A AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER A AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER A AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER A AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER A AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER A AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER A AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_H2_CO2_COMBUSTION | BOILER A H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_CH4_CO2_COMBUSTION | BOILER A CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_ETHANE_CO2_COMBUSTION | BOILER A ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHYLENE_CO2_COMBUSTION | BOILER A ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_PROPANE_CO2_COMBUSTION | BOILER A PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_NC4_CO2_COMBUSTION | BOILER A NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_IC4_CO2_COMBUSTION | BOILER A IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_NC5_CO2_COMBUSTION | BOILER A NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_IC5_CO2_COMBUSTION | BOILER A IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_H2_N2_COMBUSTION | BOILER A H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_CH4_N2_COMBUSTION | BOILER A CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_ETHANE_N2_COMBUSTION | BOILER A ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHYLENE_N2_COMBUSTION | BOILER A ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_PROPANE_N2_COMBUSTION | BOILER A PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_IC4_N2_COMBUSTION | BOILER A IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_NC4_N2_COMBUSTION | BOILER A NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_IC5_N2_COMBUSTION | BOILER A IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_NC5_N2_COMBUSTION | BOILER A NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_H2_H2O_COMBUSTION | BOILER A H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION | BOILER_A_FG_HYDROGEN_MASS_FRACTION
BOILER_A_CH4_H2O_COMBUSTION | BOILER A CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION
BOILER_A_ETHANE_H2O_COMBUSTION | BOILER A ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHANE_MASS_FRACTION | BOILER_A_FG_ETHANE_MASS_FRACTION
BOILER_A_ETHYLENE_H2O_COMBUSTION | BOILER A ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_ETHYLENE_MASS_FRACTION | BOILER_A_FG_ETHYLENE_MASS_FRACTION
BOILER_A_PROPANE_H2O_COMBUSTION | BOILER A PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_PROPANE_MASS_FRACTION | BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_IC4_H2O_COMBUSTION | BOILER A IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC4_MASS_FRACTION | BOILER_A_FG_NC4_MASS_FRACTION
BOILER_A_NC4_H2O_COMBUSTION | BOILER A NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_IC4_MASS_FRACTION
BOILER_A_IC5_H2O_COMBUSTION | BOILER A IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_IC5_MASS_FRACTION | BOILER_A_FG_IC5_MASS_FRACTION
BOILER_A_NC5_H2O_COMBUSTION | BOILER A NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_NC5_MASS_FRACTION | BOILER_A_FG_NC5_MASS_FRACTION
BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER A AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_A_AI | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_A_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_A_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_A_CO2_FORMED | BOILER A CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_CH4_CO2_COMBUSTION+BOILER_A_ETHANE_CO2_COMBUSTION+BOILER_A_ETHYLENE_CO2_COMBUSTION+BOILER_A_PROPANE_CO2_COMBUSTION+BOILER_A_NC4_CO2_COMBUSTION+BOILER_A_IC4_CO2_COMBUSTION+BOILER_A_NC5_CO2_COMBUSTION+BOILER_A_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CH4_CO2_COMBUSTION ¦ BOILER_A_ETHANE_CO2_COMBUSTION ¦ BOILER_A_ETHYLENE_CO2_COMBUSTION ¦ BOILER_A_IC4_CO2_COMBUSTION ¦ BOILER_A_IC5_CO2_COMBUSTION | BOILER_A_CH4_CO2_COMBUSTION ¦ BOILER_A_ETHANE_CO2_COMBUSTION ¦ BOILER_A_ETHYLENE_CO2_COMBUSTION ¦ BOILER_A_IC4_CO2_COMBUSTION ¦ BOILER_A_IC5_CO2_COMBUSTION ¦ BOILER_A_NC4_CO2_COMBUSTION ¦ BOILER_A_NC5_CO2_COMBUSTION ¦ BOILER_A_PROPANE_CO2_COMBUSTION
BOILER_A_N2_FORMED | BOILER A N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_H2_N2_COMBUSTION+BOILER_A_CH4_N2_COMBUSTION+BOILER_A_ETHANE_N2_COMBUSTION+BOILER_A_ETHYLENE_N2_COMBUSTION+BOILER_A_PROPANE_N2_COMBUSTION+BOILER_A_IC4_N2_COMBUSTION+BOILER_A_NC4_N2_COMBUSTION+BOILER_A_IC5_N2_COMBUSTION+BOILER_A_NC5_N2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CH4_N2_COMBUSTION ¦ BOILER_A_ETHANE_N2_COMBUSTION ¦ BOILER_A_ETHYLENE_N2_COMBUSTION ¦ BOILER_A_H2_N2_COMBUSTION ¦ BOILER_A_IC4_N2_COMBUSTION | BOILER_A_CH4_N2_COMBUSTION ¦ BOILER_A_ETHANE_N2_COMBUSTION ¦ BOILER_A_ETHYLENE_N2_COMBUSTION ¦ BOILER_A_H2_N2_COMBUSTION ¦ BOILER_A_IC4_N2_COMBUSTION ¦ BOILER_A_IC5_N2_COMBUSTION ¦ BOILER_A_NC4_N2_COMBUSTION ¦ BOILER_A_NC5_N2_COMBUSTION ¦ BOILER_A_PROPANE_N2_COMBUSTION
BOILER_A_H2O_FORMED | BOILER A H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_H2_H2O_COMBUSTION+BOILER_A_CH4_H2O_COMBUSTION+BOILER_A_ETHANE_H2O_COMBUSTION+BOILER_A_ETHYLENE_H2O_COMBUSTION+BOILER_A_PROPANE_H2O_COMBUSTION+BOILER_A_IC4_H2O_COMBUSTION+BOILER_A_NC4_H2O_COMBUSTION+BOILER_A_IC5_H2O_COMBUSTION+BOILER_A_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CH4_H2O_COMBUSTION ¦ BOILER_A_ETHANE_H2O_COMBUSTION ¦ BOILER_A_ETHYLENE_H2O_COMBUSTION ¦ BOILER_A_H2_H2O_COMBUSTION ¦ BOILER_A_IC4_H2O_COMBUSTION | BOILER_A_CH4_H2O_COMBUSTION ¦ BOILER_A_ETHANE_H2O_COMBUSTION ¦ BOILER_A_ETHYLENE_H2O_COMBUSTION ¦ BOILER_A_H2_H2O_COMBUSTION ¦ BOILER_A_IC4_H2O_COMBUSTION ¦ BOILER_A_IC5_H2O_COMBUSTION ¦ BOILER_A_NC4_H2O_COMBUSTION ¦ BOILER_A_NC5_H2O_COMBUSTION ¦ BOILER_A_PROPANE_H2O_COMBUSTION
BOILER_A_VAPOUR_PRESSURE_OF_H2O | BOILER A VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631
BOILER_A_AIR_MOISTURE | BOILER A AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_A_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_A_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645
BOILER_A_CORRECTED_COMBUSTION_AIR | BOILER A CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_A_AIR_MOISTURE) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_A_CORRECTED_COMBUTION_H2O_FORMED | BOILER A CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_A_H2O_FORMED+(BOILER_A_CORRECTED_COMBUSTION_AIR-BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_H2O_FORMED | BOILER_A_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_H2O_FORMED
BOILER_A_EXCESS_AIR | BOILER A EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_A_FLUE_GAS_OXGYGEN)*((BOILER_A_N2_FORMED/28.01)+(BOILER_A_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_A_CO2_FORMED/44.01))/(20.95-BOILER_A_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV]; Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_A_N2_FORMED | BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV] ¦ BOILER_A_CO2_FORMED ¦ BOILER_A_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_A_N2_FORMED
BOILER_A_AIR_FUEL_MASS_RATIO | BOILER A AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_EXCESS_AIR+BOILER_A_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_EXCESS_AIR | BOILER_A_CORRECTED_COMBUSTION_AIR ¦ BOILER_A_EXCESS_AIR
BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER A TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_AIR_MOISTURE | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO
BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER A TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_A_TOTAL_MOISTURE_WITH_AIR+BOILER_A_H2O_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_H2O_FORMED ¦ BOILER_A_TOTAL_MOISTURE_WITH_AIR | BOILER_A_H2O_FORMED ¦ BOILER_A_TOTAL_MOISTURE_WITH_AIR
BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER A CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_A_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] | BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV]
BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER A AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_AIR_CP_REF_T+BOILER_A_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CP_AT_COMBUSTION_TEMPERATURE | BOILER_A_CP_AT_COMBUSTION_TEMPERATURE
BOILER_A_CP_H2_FUEL_TEMP | BOILER A CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_CH4_FUEL_TEMP | BOILER A CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_ETHANE_FUEL_TEMP | BOILER A CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_PROPANE_FUEL_TEMP | BOILER A CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_ETHYLENE_FUEL_TEMP | BOILER A CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_NC4_FUEL_TEMP | BOILER A CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_IC4_FUEL_TEMP | BOILER A CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_NC5_FUEL_TEMP | BOILER A CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_IC5_FUEL_TEMP | BOILER A CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_A_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]
BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER A CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_A_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_A_FG_NC4_MASS_FRACTION/COMPONENT | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION | BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION ¦ BOILER_A_FG_IC5_MASS_FRACTION ¦ BOILER_A_FG_MW ¦ BOILER_A_FG_NC4_MASS_FRACTION ¦ BOILER_A_FG_NC5_MASS_FRACTION ¦ BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER A CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_A_CP_H2_FUEL_TEMP+BOILER_A_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_A_CP_CH4_FUEL_TEMP+(BOILER_A_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_A_CP_ETHYLENE_FUEL_TEMP+(BOILER_A_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_A_CP_ETHANE_FUEL_TEMP+(BOILER_A_FG_P | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CP_CH4_FUEL_TEMP ¦ BOILER_A_CP_ETHANE_FUEL_TEMP ¦ BOILER_A_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_A_CP_H2_FUEL_TEMP ¦ BOILER_A_CP_IC4_FUEL_TEMP (+9 more) | BOILER_A_CP_CH4_FUEL_TEMP ¦ BOILER_A_CP_ETHANE_FUEL_TEMP ¦ BOILER_A_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_A_CP_H2_FUEL_TEMP ¦ BOILER_A_CP_IC4_FUEL_TEMP ¦ BOILER_A_CP_IC5_FUEL_TEMP ¦ BOILER_A_CP_NC4_FUEL_TEMP ¦ BOILER_A_CP_NC5_FUEL_TEMP ¦ BOILER_A_CP_PROPANE_FUEL_TEMP ¦ BOILER_A_FG_CH4_MASS_FRACTION ¦ BOILER_A_FG_ETHANE_MASS_FRACTION ¦ BOILER_A_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_FG_IC4_MASS_FRACTION ¦ BOILER_A_FG_IC5_MASS_FRACTION ¦ BOILER_A_FG_MW ¦ BOILER_A_FG_NC4_MASS_FRACTION ¦ BOILER_A_FG_NC5_MASS_FRACTION ¦ BOILER_A_FG_PROPANE_MASS_FRACTION
BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER A AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_A_FG_MW)/2 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_A_FG_MW | BOILER_A_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_A_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_A_FG_MW
BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_EXCESS_AIR*(1-BOILER_A_AIR_MOISTURE)+BOILER_A_N2_FORMED+BOILER_A_CO2_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_N2_FORMED
BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER A FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_FLUE_GAS_MW | BOILER A FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_A_CO2_FORMED/44.01+BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.96) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_CP_OF_AIR_AT_STACK_TEMP | BOILER A CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_A_STACK_TEMPERATURE+273.15 | COMPUTED | 6.9676
BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER A CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6499
BOILER_A_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER A CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3662
BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER A CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_A_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586
BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER A AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_A_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_A_CO2_FORMED/44.01+BOILER_A_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_A_N2_FORMED/28.01+BOILER_A_EXCESS_AIR/28.85*BOILER_A_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_A_FLUE_GAS_MW)/BOILER_A_FLUE_GAS_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_MW ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED | BOILER_A_CO2_FORMED ¦ BOILER_A_EXCESS_AIR ¦ BOILER_A_FLUE_GAS_MW ¦ BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_N2_FORMED
BOILER_A_CP_OF_H2O_AT_STACK_TEMP | BOILER A CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_A_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_A_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644
BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER A SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_A_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV]; Unknown/no sensor: BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_A_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1113.PV] ¦ BOILER_A_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER A SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_A_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_A_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV]; Unknown/no sensor: BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_A_AIR_FUEL_MASS_RATIO | BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] ¦ BOILER_A_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_A_AIR_FUEL_MASS_RATIO
BOILER_A_MIXED_LHV_PER_KG | BOILER A MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | NOT COMPUTED |  | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER A TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_A_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_A_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER A HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_A_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS | BOILER_A_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_A_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER A HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,9*(BOILER_A_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_A_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_A_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_STATUS | BOILER_A_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_A_STATUS
BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER A HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_A_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER A HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,0*10^-6*28*5654*BOILER_A_BOILER_LOAD) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS | BOILER_A_STATUS
BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER A TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_A_STATUS | BOILER_A_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_A_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_A_STATUS
BOILER_A_RADIATION_LOSSES | BOILER A RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_MIXED_LHV_PER_KG*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOAD^2-0.0899*BOILER_A_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER A TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_A_RADIATION_LOSSES) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_RADIATION_LOSSES ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_RADIATION_LOSSES ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER A TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_A_BOILER_INDIRECT_EFFICIENCY | BOILER A BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_A_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_A_HP_STEAM_ENTHALPY | BOILER A HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS)+2.66244961166282*DESUPERHEATER_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] ¦ BOILER_A_STATUS
BOILER_A_TOTAL_STEAM_ENERGY | BOILER A TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_HP_STEAM_ENTHALPY ¦ BOILER_A_STATUS | BOILER_A_HP_STEAM_ENTHALPY ¦ BOILER_A_STATUS
BOILER_A_BFW_ENTHALPY | BOILER A BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_A_INLET_TEMPERATURE) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ BOILER_A_STATUS
BOILER_A_CORRECTED_BFW_FLOW | BOILER A CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-(BFW_FLOW_TO_ECOMONIZER_A+BFW_FLOW_TO_DESUPERHEATER_A-DESUPERHEATER_OUTLET_STEAM_FLOW-BOILER_A_CBD_BD))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_A[sensor:UN.UO.71FI1102.PV] ¦ BFW_FLOW_TO_ECOMONIZER_A[sensor:UN.UO.71FI1103.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV]; Unknown/no sensor: BOILER_A_STATUS | BFW_FLOW_TO_DESUPERHEATER_A[sensor:UN.UO.71FI1102.PV] ¦ BFW_FLOW_TO_ECOMONIZER_A[sensor:UN.UO.71FI1103.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ BOILER_A_STATUS
BOILER_A_BFW_ENERGY | BOILER A BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*BOILER_A_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_BFW_ENTHALPY ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS | BOILER_A_BFW_ENTHALPY ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS
BOILER_A_FUEL_GAS_ENERGY_INPUT | BOILER A FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FG_FLOW_RATE*1000*BOILER_A_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_STEAM_DRUM_TEMP | BOILER A STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,4.02521999671835*log(STEAM_DRUM_A_PRESSURE*98.065)^3-4.64392873298701*log(STEAM_DRUM_A_PRESSURE*98.065)^2+11.2370106828649*log(STEAM_DRUM_A_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | PI exists but NOT in hierarchy: STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV]; Unknown/no sensor: BOILER_A_STATUS | STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ BOILER_A_STATUS
BOILER_A_BLOWDOWN_LOSS | BOILER A BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,((BOILER_A_CBD_BD/1000)*((STEAM_DRUM_A_PRESSURE*2.11087739028321+SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV]; Unknown/no sensor: BOILER_A_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV] ¦ BOILER_A_STATUS
BOILER_A_TOTAL_FLUE_GAS_GENERATED | BOILER A TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW/1000*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_STATUS
BOILER_A_STACK_LOSS | BOILER A STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_CORRECTED_FUEL_FLOW | BOILER A CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_FLOW-((BOILER_A_FUEL_GAS_ENERGY_INPUT-(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY+BOILER_A_BLOWDOWN_LOSS+BOILER_A_STACK_LOSS+BOILER_A_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_A_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_A_BOILER_LOAD^3+0.001*BOILER_A_BOILER_LOAD^2-0.0899*BOILER_A_BOILER_LOAD+3.2426)/100+(BOILE | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_MIXED_LHV_PER_KG | BOILER_A_BFW_ENERGY ¦ BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STACK_LOSS ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_FUEL_CONSUMPTION | BOILER A FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER A SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS
BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER A SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_CONSUMPTION/(DESUPERHEATER_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS | BOILER_A_FUEL_CONSUMPTION ¦ BOILER_A_STATUS
BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER A CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW*BOILER_A_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_A_THERMAL_EFFICIENCY | BOILER A THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY)/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER A EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_BLOWDOWN_LOSS/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS | BOILER_A_BLOWDOWN_LOSS ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS
BOILER_A_ECONOMIZER_DUTY | BOILER A ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_BFW_FLOW*((STEAM_DRUM_A_PRESSURE*0.0336523715096497+ECONIMIZER_A_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_A_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV]; Unknown/no sensor: BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS
BOILER_A_LMTD_ECONOMIZER | BOILER A LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,((673-ECONIMIZER_A_OUTLET_TEMPERATURE)-(BOILER_A_STACK_TEMPERATURE-ECONOMIZER_A_INLET_TEMPERATURE))/ln((673-ECONIMIZER_A_OUTLET_TEMPERATURE)/(-ECONOMIZER_A_INLET_TEMPERATURE+BOILER_A_STACK_TEMPERATURE))) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONIMIZER_A_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1102.PV] ¦ ECONOMIZER_A_INLET_TEMPERATURE[sensor:UN.UO.71TI1110.PV] ¦ BOILER_A_STATUS
BOILER_A_UA_ECONOMIZER | BOILER A UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY/BOILER_A_LMTD_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_LMTD_ECONOMIZER ¦ BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_LMTD_ECONOMIZER ¦ BOILER_A_STATUS
BOILER_A_FOULING_INDEX | BOILER A FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,1/BOILER_A_UA_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_A_UA_ECONOMIZER | BOILER_A_STATUS ¦ BOILER_A_UA_ECONOMIZER
BOILER_A_SH_DUTY | BOILER A SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW*((STEAM_DRUM_A_PRESSURE*-2.64315212289699+DESUPERHEATER_TEMPERATURE*3.58096116723573+1939.73413132244)-(STEAM_DRUM_A_PRESSURE*-4.27591051303366+SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: DESUPERHEATER_TEMPERATURE[sensor:UN.UO.71TI1106.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV]; Unknown/no sensor: BOILER_A_STATUS | DESUPERHEATER_TEMPERATURE[sensor:UN.UO.71TI1106.PV] ¦ STEAM_DRUM_A_PRESSURE[sensor:UN.UO.71PC1103.PV] ¦ SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1119.PV] ¦ BOILER_A_STATUS
BOILER_A_SH_SPECIFIC_DUTY | BOILER A SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_SH_DUTY/DESUPERHEATER_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_SH_DUTY ¦ BOILER_A_STATUS | BOILER_A_SH_DUTY ¦ BOILER_A_STATUS
BOILER_A_FUEL_GAS_CORRECTED_TPH | BOILER A FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS
BOILER_A_TOTAL_FLUE_GAS_CORRECTED | BOILER A TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_FUEL_GAS_CORRECTED_TPH*BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS | BOILER_A_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS
BOILER_A_STACK_LOSS_CORRECTED | BOILER A STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_A_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_A_SUPERHEATED_STEAM_BFW_RATIO | BOILER A SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(DESUPERHEATER_OUTLET_STEAM_FLOW+BOILER_A_CBD_BD)/(BOILER_A_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV]; Unknown/no sensor: BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS | BOILER_A_CBD_BD[sensor:UN.UO.71FC1100.PV] ¦ BOILER_A_CORRECTED_BFW_FLOW ¦ BOILER_A_STATUS
BOILER_A_CO2_EMISSIONS | BOILER A CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CO2_FORMED*BOILER_A_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CO2_FORMED ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS | BOILER_A_CO2_FORMED ¦ BOILER_A_FUEL_GAS_CORRECTED_TPH ¦ BOILER_A_STATUS
BOILER_A_CALCULATED_AIRFLOW_NM3H | BOILER A CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_AIR_FUEL_MASS_RATIO*BOILER_A_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS | BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_A_CORRECTED_FUEL_FLOW ¦ BOILER_A_STATUS
BOILER_A_SH_PERFORMANCE | BOILER A SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(BOILER_A_SH_SPECIFIC_DUTY)/0.128049016*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_SH_SPECIFIC_DUTY ¦ BOILER_A_STATUS | BOILER_A_SH_SPECIFIC_DUTY ¦ BOILER_A_STATUS
BOILER_A_ENERGY_GAINED | BOILER A ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_TOTAL_STEAM_ENERGY-BOILER_A_BFW_ENERGY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_BFW_ENERGY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY | BOILER_A_BFW_ENERGY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY
BOILER_A_CONVECTION_DUTY | BOILER A CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_ECONOMIZER_DUTY+BOILER_A_SH_DUTY+BOILER_A_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_SH_DUTY ¦ BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_A_STATUS | BOILER_A_ECONOMIZER_DUTY ¦ BOILER_A_SH_DUTY ¦ BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_A_STATUS
BOILER_A_RADIATION_DUTY | BOILER A RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_ENERGY_GAINED-BOILER_A_CONVECTION_DUTY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS
BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER A PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY ¦ BOILER_A_ENERGY_GAINED ¦ BOILER_A_STATUS
BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER A PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_ENERGY_GAINED ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS | BOILER_A_ENERGY_GAINED ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS
BOILER_A_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER A RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_A_STATUS | BOILER_A_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_A_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_A_STATUS
BOILER_A_RADIATION_SECTION_EFFICIENCY | BOILER A RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_RADIATION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_RADIATION_DUTY ¦ BOILER_A_STATUS
BOILER_A_CONVECTION_SECTION_EFFICIENCY | BOILER A CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,BOILER_A_CONVECTION_DUTY/BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CONVECTION_DUTY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS | BOILER_A_CONVECTION_DUTY ¦ BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_A_STATUS
BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER B FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | NORMALIZED BOILER B FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER B FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER B FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL | BOILER_B_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER B FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_B_FG_CO2_CONCENTRATION | NORMALIZED BOILER B FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | NORMALIZED BOILER B FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | NORMALIZED BOILER B FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | NORMALIZED BOILER B FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | NORMALIZED BOILER B FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | NORMALIZED BOILER B FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER B FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_B_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_B_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_B_FG_MW | BOILER B FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_B_FG_NC5_C | NOT COMPUTED |  | Unknown/no sensor: NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION
BOILER_B_FG_CH4_MASS_PERCENTAGE | BOILER B FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_CH4_CONCENTRATION
BOILER_B_FG_ETHANE_MASS_PERCENTAGE | BOILER B FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHANE_CONCENTRATION
BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE | BOILER B FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_ETHYLENE_CONCENTRATION
BOILER_B_FG_PROPANE_MASS_PERCENTAGE | BOILER B FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_PROPANE_CONCENTRATION
BOILER_B_FG_NITROGEN_MASS_PERCENTAGE | BOILER B FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_N2_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_N2_CONCENTRATION
BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE | BOILER B FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_HYDROGEN_CONCENTRATION
BOILER_B_FG_IC4_MASS_PERCENTAGE | BOILER B FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC4_CONCENTRATION
BOILER_B_FG_NC4_MASS_PERCENTAGE | BOILER B FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC4_CONCENTRATION
BOILER_B_FG_NC5_MASS_PERCENTAGE | BOILER B FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_NC5_CONCENTRATION
BOILER_B_FG_IC5_MASS_PERCENTAGE | BOILER B FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_B_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION | BOILER_B_FG_MW ¦ NORMALIZED_BOILER_B_FG_IC5_CONCENTRATION
BOILER_B_FG_DENSITY | BOILER B FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_MW/22.414 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_MW | BOILER_B_FG_MW
BOILER_B_LHV_DESIGN | BOILER B LHV DESIGN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_B_FG_DENSITY)/1000 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_DENSITY | BOILER_B_FG_DENSITY
BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER B TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_PERCENTAGE+BOILER_B_FG_ETHANE_MASS_PERCENTAGE+BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_B_FG_PROPANE_MASS_PERCENTAGE+BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_B_FG_NITROGEN_MASS_PERCENTAGE+BOILER_B_FG_IC4_MASS_PERCENTAGE+BOILER_B_FG_NC4_MASS_PERCENTAGE+BOILER_B_FG_NC5_MASS_PERCENTAGE+BOILER_B_FG_IC5_MASS_PERCENTAGE | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_FG_IC4_MASS_PERCENTAGE | BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_FG_IC4_MASS_PERCENTAGE ¦ BOILER_B_FG_IC5_MASS_PERCENTAGE ¦ BOILER_B_FG_NC4_MASS_PERCENTAGE ¦ BOILER_B_FG_NC5_MASS_PERCENTAGE ¦ BOILER_B_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_B_FG_PROPANE_MASS_PERCENTAGE
BOILER_B_FG_CH4_MASS_FRACTION | BOILER B FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_CH4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER B FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER B FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER B FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NITROGEN_MASS_FRACTION | BOILER B FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER B FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_IC4_MASS_FRACTION | BOILER B FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NC4_MASS_FRACTION | BOILER B FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC4_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_NC5_MASS_FRACTION | BOILER B FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_NC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_FG_IC5_MASS_FRACTION | BOILER B FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_PERCENTAGE/BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS | BOILER_B_FG_IC5_MASS_PERCENTAGE ¦ BOILER_B_TOTAL_FUEL_COMPOSTION_MASS
BOILER_B_LHV | BOILER B LHV | Kcal/Kg | LBM_preprocessing_inferred_tags_main | (BOILER_B_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_B_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_B_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_B_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_B_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_B_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_B_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_B_FG_NC5_MASS_FRAC | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION ¦ BOILER_B_FG_NC4_MASS_FRACTION ¦ BOILER_B_FG_NC5_MASS_FRACTION ¦ BOILER_B_FG_NITROGEN_MASS_FRACTION ¦ BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_FG_FLOW_RATE | BOILER B FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_B_FUEL_GAS_FLOW/1000 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]
BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER B AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER B AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER B AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER B AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER B AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER B AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER B AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER B AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_H2_CO2_COMBUSTION | BOILER B H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_CH4_CO2_COMBUSTION | BOILER B CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_ETHANE_CO2_COMBUSTION | BOILER B ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHYLENE_CO2_COMBUSTION | BOILER B ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_PROPANE_CO2_COMBUSTION | BOILER B PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_NC4_CO2_COMBUSTION | BOILER B NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_IC4_CO2_COMBUSTION | BOILER B IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_NC5_CO2_COMBUSTION | BOILER B NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_IC5_CO2_COMBUSTION | BOILER B IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_H2_N2_COMBUSTION | BOILER B H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_CH4_N2_COMBUSTION | BOILER B CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_ETHANE_N2_COMBUSTION | BOILER B ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHYLENE_N2_COMBUSTION | BOILER B ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_PROPANE_N2_COMBUSTION | BOILER B PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_IC4_N2_COMBUSTION | BOILER B IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_NC4_N2_COMBUSTION | BOILER B NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_IC5_N2_COMBUSTION | BOILER B IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_NC5_N2_COMBUSTION | BOILER B NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_H2_H2O_COMBUSTION | BOILER B H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION | BOILER_B_FG_HYDROGEN_MASS_FRACTION
BOILER_B_CH4_H2O_COMBUSTION | BOILER B CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION
BOILER_B_ETHANE_H2O_COMBUSTION | BOILER B ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHANE_MASS_FRACTION | BOILER_B_FG_ETHANE_MASS_FRACTION
BOILER_B_ETHYLENE_H2O_COMBUSTION | BOILER B ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_ETHYLENE_MASS_FRACTION | BOILER_B_FG_ETHYLENE_MASS_FRACTION
BOILER_B_PROPANE_H2O_COMBUSTION | BOILER B PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_PROPANE_MASS_FRACTION | BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_IC4_H2O_COMBUSTION | BOILER B IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC4_MASS_FRACTION | BOILER_B_FG_NC4_MASS_FRACTION
BOILER_B_NC4_H2O_COMBUSTION | BOILER B NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_IC4_MASS_FRACTION
BOILER_B_IC5_H2O_COMBUSTION | BOILER B IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_IC5_MASS_FRACTION | BOILER_B_FG_IC5_MASS_FRACTION
BOILER_B_NC5_H2O_COMBUSTION | BOILER B NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_NC5_MASS_FRACTION | BOILER_B_FG_NC5_MASS_FRACTION
BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER B AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_B_AI | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_B_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_B_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_B_CO2_FORMED | BOILER B CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_CH4_CO2_COMBUSTION+BOILER_B_ETHANE_CO2_COMBUSTION+BOILER_B_ETHYLENE_CO2_COMBUSTION+BOILER_B_PROPANE_CO2_COMBUSTION+BOILER_B_NC4_CO2_COMBUSTION+BOILER_B_IC4_CO2_COMBUSTION+BOILER_B_NC5_CO2_COMBUSTION+BOILER_B_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CH4_CO2_COMBUSTION ¦ BOILER_B_ETHANE_CO2_COMBUSTION ¦ BOILER_B_ETHYLENE_CO2_COMBUSTION ¦ BOILER_B_IC4_CO2_COMBUSTION ¦ BOILER_B_IC5_CO2_COMBUSTION | BOILER_B_CH4_CO2_COMBUSTION ¦ BOILER_B_ETHANE_CO2_COMBUSTION ¦ BOILER_B_ETHYLENE_CO2_COMBUSTION ¦ BOILER_B_IC4_CO2_COMBUSTION ¦ BOILER_B_IC5_CO2_COMBUSTION ¦ BOILER_B_NC4_CO2_COMBUSTION ¦ BOILER_B_NC5_CO2_COMBUSTION ¦ BOILER_B_PROPANE_CO2_COMBUSTION
BOILER_B_N2_FORMED | BOILER B N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_H2_N2_COMBUSTION+BOILER_B_CH4_N2_COMBUSTION+BOILER_B_ETHANE_N2_COMBUSTION+BOILER_B_ETHYLENE_N2_COMBUSTION+BOILER_B_PROPANE_N2_COMBUSTION+BOILER_B_IC4_N2_COMBUSTION+BOILER_B_NC4_N2_COMBUSTION+BOILER_B_IC5_N2_COMBUSTION+BOILER_B_NC5_N2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CH4_N2_COMBUSTION ¦ BOILER_B_ETHANE_N2_COMBUSTION ¦ BOILER_B_ETHYLENE_N2_COMBUSTION ¦ BOILER_B_H2_N2_COMBUSTION ¦ BOILER_B_IC4_N2_COMBUSTION | BOILER_B_CH4_N2_COMBUSTION ¦ BOILER_B_ETHANE_N2_COMBUSTION ¦ BOILER_B_ETHYLENE_N2_COMBUSTION ¦ BOILER_B_H2_N2_COMBUSTION ¦ BOILER_B_IC4_N2_COMBUSTION ¦ BOILER_B_IC5_N2_COMBUSTION ¦ BOILER_B_NC4_N2_COMBUSTION ¦ BOILER_B_NC5_N2_COMBUSTION ¦ BOILER_B_PROPANE_N2_COMBUSTION
BOILER_B_H2O_FORMED | BOILER B H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_H2_H2O_COMBUSTION+BOILER_B_CH4_H2O_COMBUSTION+BOILER_B_ETHANE_H2O_COMBUSTION+BOILER_B_ETHYLENE_H2O_COMBUSTION+BOILER_B_PROPANE_H2O_COMBUSTION+BOILER_B_IC4_H2O_COMBUSTION+BOILER_B_NC4_H2O_COMBUSTION+BOILER_B_IC5_H2O_COMBUSTION+BOILER_B_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CH4_H2O_COMBUSTION ¦ BOILER_B_ETHANE_H2O_COMBUSTION ¦ BOILER_B_ETHYLENE_H2O_COMBUSTION ¦ BOILER_B_H2_H2O_COMBUSTION ¦ BOILER_B_IC4_H2O_COMBUSTION | BOILER_B_CH4_H2O_COMBUSTION ¦ BOILER_B_ETHANE_H2O_COMBUSTION ¦ BOILER_B_ETHYLENE_H2O_COMBUSTION ¦ BOILER_B_H2_H2O_COMBUSTION ¦ BOILER_B_IC4_H2O_COMBUSTION ¦ BOILER_B_IC5_H2O_COMBUSTION ¦ BOILER_B_NC4_H2O_COMBUSTION ¦ BOILER_B_NC5_H2O_COMBUSTION ¦ BOILER_B_PROPANE_H2O_COMBUSTION
BOILER_B_VAPOUR_PRESSURE_OF_H2O | BOILER B VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631
BOILER_B_AIR_MOISTURE | BOILER B AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_B_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_B_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645
BOILER_B_CORRECTED_COMBUSTION_AIR | BOILER B CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_B_AIR_MOISTURE) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_B_CORRECTED_COMBUTION_H2O_FORMED | BOILER B CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_B_H2O_FORMED+(BOILER_B_CORRECTED_COMBUSTION_AIR-BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_H2O_FORMED | BOILER_B_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_H2O_FORMED
BOILER_B_EXCESS_AIR | BOILER B EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_B_FLUE_GAS_OXGYGEN)*((BOILER_B_N2_FORMED/28.01)+(BOILER_B_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_B_CO2_FORMED/44.01))/(20.95-BOILER_B_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV]; Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_B_N2_FORMED | BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV] ¦ BOILER_B_CO2_FORMED ¦ BOILER_B_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_B_N2_FORMED
BOILER_B_AIR_FUEL_MASS_RATIO | BOILER B AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_EXCESS_AIR+BOILER_B_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_EXCESS_AIR | BOILER_B_CORRECTED_COMBUSTION_AIR ¦ BOILER_B_EXCESS_AIR
BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER B TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_AIR_MOISTURE | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_AIR_FUEL_MASS_RATIO | BOILER_B_AIR_FUEL_MASS_RATIO
BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER B TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_B_TOTAL_MOISTURE_WITH_AIR+BOILER_B_H2O_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_H2O_FORMED ¦ BOILER_B_TOTAL_MOISTURE_WITH_AIR | BOILER_B_H2O_FORMED ¦ BOILER_B_TOTAL_MOISTURE_WITH_AIR
BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER B CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_B_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] | BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV]
BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER B AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_AIR_CP_REF_T+BOILER_B_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CP_AT_COMBUSTION_TEMPERATURE | BOILER_B_CP_AT_COMBUSTION_TEMPERATURE
BOILER_B_CP_H2_FUEL_TEMP | BOILER B CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_CH4_FUEL_TEMP | BOILER B CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_ETHANE_FUEL_TEMP | BOILER B CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_PROPANE_FUEL_TEMP | BOILER B CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_ETHYLENE_FUEL_TEMP | BOILER B CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_NC4_FUEL_TEMP | BOILER B CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_IC4_FUEL_TEMP | BOILER B CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_NC5_FUEL_TEMP | BOILER B CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_IC5_FUEL_TEMP | BOILER B CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_B_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]
BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER B CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_B_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_B_FG_NC4_MASS_FRACTION/COMPONENT | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION | BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION ¦ BOILER_B_FG_MW ¦ BOILER_B_FG_NC4_MASS_FRACTION ¦ BOILER_B_FG_NC5_MASS_FRACTION ¦ BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER B CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_B_CP_H2_FUEL_TEMP+BOILER_B_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_B_CP_CH4_FUEL_TEMP+(BOILER_B_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_B_CP_ETHYLENE_FUEL_TEMP+(BOILER_B_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_B_CP_ETHANE_FUEL_TEMP+(BOILER_B_FG_P | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CP_CH4_FUEL_TEMP ¦ BOILER_B_CP_ETHANE_FUEL_TEMP ¦ BOILER_B_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_B_CP_H2_FUEL_TEMP ¦ BOILER_B_CP_IC4_FUEL_TEMP (+9 more) | BOILER_B_CP_CH4_FUEL_TEMP ¦ BOILER_B_CP_ETHANE_FUEL_TEMP ¦ BOILER_B_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_B_CP_H2_FUEL_TEMP ¦ BOILER_B_CP_IC4_FUEL_TEMP ¦ BOILER_B_CP_IC5_FUEL_TEMP ¦ BOILER_B_CP_NC4_FUEL_TEMP ¦ BOILER_B_CP_NC5_FUEL_TEMP ¦ BOILER_B_CP_PROPANE_FUEL_TEMP ¦ BOILER_B_FG_CH4_MASS_FRACTION ¦ BOILER_B_FG_ETHANE_MASS_FRACTION ¦ BOILER_B_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_FG_IC4_MASS_FRACTION ¦ BOILER_B_FG_IC5_MASS_FRACTION ¦ BOILER_B_FG_MW ¦ BOILER_B_FG_NC4_MASS_FRACTION ¦ BOILER_B_FG_NC5_MASS_FRACTION ¦ BOILER_B_FG_PROPANE_MASS_FRACTION
BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER B AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_B_FG_MW)/2 | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_B_FG_MW | BOILER_B_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_B_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_B_FG_MW
BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_B_EXCESS_AIR*(1-BOILER_B_AIR_MOISTURE)+BOILER_B_N2_FORMED+BOILER_B_CO2_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_N2_FORMED
BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER B FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_FLUE_GAS_MW | BOILER B FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_B_CO2_FORMED/44.01+BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.96) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_CP_OF_AIR_AT_STACK_TEMP | BOILER B CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_B_STACK_TEMPERATURE+273.15 | COMPUTED | 6.9675
BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER B CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6497
BOILER_B_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER B CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3662
BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER B CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_B_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586
BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER B AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_B_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_B_CO2_FORMED/44.01+BOILER_B_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_B_N2_FORMED/28.01+BOILER_B_EXCESS_AIR/28.85*BOILER_B_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_B_FLUE_GAS_MW)/BOILER_B_FLUE_GAS_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_MW ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED | BOILER_B_CO2_FORMED ¦ BOILER_B_EXCESS_AIR ¦ BOILER_B_FLUE_GAS_MW ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_N2_FORMED
BOILER_B_CP_OF_H2O_AT_STACK_TEMP | BOILER B CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_B_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_B_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644
BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER B SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_B_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV]; Unknown/no sensor: BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_B_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1213.PV] ¦ BOILER_B_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER B SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_B_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_B_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV]; Unknown/no sensor: BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_B_AIR_FUEL_MASS_RATIO | BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] ¦ BOILER_B_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_B_AIR_FUEL_MASS_RATIO
BOILER_B_MIXED_LHV_PER_KG | BOILER B MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | NOT COMPUTED |  | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER B TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_B_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_B_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER B HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_B_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS | BOILER_B_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_B_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER B HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,9*(BOILER_B_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_B_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_B_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_STATUS | BOILER_B_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_B_STATUS
BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER B HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_B_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_B_STATUS ¦ BOILER_B_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER B HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,0*10^-6*28*5654*BOILER_B_BOILER_LOAD) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_STATUS | BOILER_B_STATUS
BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER B TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_B_STATUS | BOILER_B_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_B_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_B_STATUS
BOILER_B_RADIATION_LOSSES | BOILER B RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_MIXED_LHV_PER_KG*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOAD^2-0.0899*BOILER_B_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER B TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_B_RADIATION_LOSSES) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_RADIATION_LOSSES ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_RADIATION_LOSSES ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER B TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_B_BOILER_INDIRECT_EFFICIENCY | BOILER B BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_B_STATUS ¦ BOILER_B_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_B_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_B_HP_STEAM_ENTHALPY | BOILER B HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_B)+2.66244961166282*DESUPERHEATER_B_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] ¦ BOILER_A_STATUS
BOILER_B_TOTAL_STEAM_ENERGY | BOILER B TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_HP_STEAM_ENTHALPY ¦ BOILER_B_STATUS | BOILER_B_HP_STEAM_ENTHALPY ¦ BOILER_B_STATUS
BOILER_B_BFW_ENTHALPY | BOILER B BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_B_INLET_TEMPERATURE) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ BOILER_A_STATUS
BOILER_B_CORRECTED_BFW_FLOW | BOILER B CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-(BFW_FLOW_TO_ECONOMIZER_B+BFW_FLOW_TO_DESUPERHEATER_B-DESUPERHEATER_B_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_B))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_B[sensor:UN.UO.71FI1202.PV] ¦ BFW_FLOW_TO_ECONOMIZER_B[sensor:UN.UO.71FI1203.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV]; Unknown/no sensor: BOILER_B_STATUS | BFW_FLOW_TO_DESUPERHEATER_B[sensor:UN.UO.71FI1202.PV] ¦ BFW_FLOW_TO_ECONOMIZER_B[sensor:UN.UO.71FI1203.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV] ¦ BOILER_B_STATUS
BOILER_B_BFW_ENERGY | BOILER B BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*BOILER_B_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_BFW_ENTHALPY ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS | BOILER_B_BFW_ENTHALPY ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS
BOILER_B_FUEL_GAS_ENERGY_INPUT | BOILER B FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FG_FLOW_RATE*1000*BOILER_B_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_STEAM_DRUM_TEMP | BOILER B STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,4.02521999671835*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_B_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV]; Unknown/no sensor: BOILER_B_STATUS | BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_STATUS
BOILER_B_BLOWDOWN_LOSS | BOILER B BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,((CBD_BLOW_DOWN_B/1000)*((BOILER_B_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV]; Unknown/no sensor: BOILER_B_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV] ¦ CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV] ¦ BOILER_B_STATUS
BOILER_B_TOTAL_FLUE_GAS_GENERATED | BOILER B TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW/1000*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]; Unknown/no sensor: BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] ¦ BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_STATUS
BOILER_B_STACK_LOSS | BOILER B STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]; Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_CORRECTED_FUEL_FLOW | BOILER B CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_FLOW-((BOILER_B_FUEL_GAS_ENERGY_INPUT-(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY+BOILER_B_BLOWDOWN_LOSS+BOILER_B_STACK_LOSS+BOILER_B_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_B_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_B_BOILER_LOAD^3+0.001*BOILER_B_BOILER_LOAD^2-0.0899*BOILER_B_BOILER_LOAD+3.2426)/100+(BOILE | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]; Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_MIXED_LHV_PER_KG | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] ¦ BOILER_B_BFW_ENERGY ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STACK_LOSS ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_FUEL_CONSUMPTION | BOILER B FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER B SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS
BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER B SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_CONSUMPTION/(DESUPERHEATER_B_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS | BOILER_B_FUEL_CONSUMPTION ¦ BOILER_B_STATUS
BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER B CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW*BOILER_B_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_B_THERMAL_EFFICIENCY | BOILER B THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY)/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER B EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_BLOWDOWN_LOSS/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS | BOILER_B_BLOWDOWN_LOSS ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS
BOILER_B_ECONOMIZER_DUTY | BOILER B ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_BFW_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_B_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_B_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV]; Unknown/no sensor: BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV] ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS
BOILER_B_LMTD_ECONOMIZER | BOILER B LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,((673-ECONOMIZER_B_OUTLET_TEMPERATURE)-(BOILER_B_STACK_TEMPERATURE-ECONOMIZER_B_INLET_TEMPERATURE))/ln((673-ECONOMIZER_B_OUTLET_TEMPERATURE)/(-ECONOMIZER_B_INLET_TEMPERATURE+BOILER_B_STACK_TEMPERATURE))) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV]; Unknown/no sensor: BOILER_B_STATUS | ECONOMIZER_B_INLET_TEMPERATURE[sensor:UN.UO.71TI1210.PV] ¦ ECONOMIZER_B_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1202.PV] ¦ BOILER_B_STATUS
BOILER_B_UA_ECONOMIZER | BOILER B UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY/BOILER_B_LMTD_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_LMTD_ECONOMIZER ¦ BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_LMTD_ECONOMIZER ¦ BOILER_B_STATUS
BOILER_B_FOULING_INDEX | BOILER B FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,1/BOILER_B_UA_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_STATUS ¦ BOILER_B_UA_ECONOMIZER | BOILER_B_STATUS ¦ BOILER_B_UA_ECONOMIZER
BOILER_B_SH_DUTY | BOILER B SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW*((BOILER_B_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_B_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_B_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_B_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV]; Unknown/no sensor: BOILER_B_STATUS | BOILER_B_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1203.PV] ¦ BOILER_B_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1219.PV] ¦ BOILER_B_STATUS
BOILER_B_SH_SPECIFIC_DUTY | BOILER B SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_SH_DUTY/DESUPERHEATER_B_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_SH_DUTY ¦ BOILER_B_STATUS | BOILER_B_SH_DUTY ¦ BOILER_B_STATUS
BOILER_B_FUEL_GAS_CORRECTED_TPH | BOILER B FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS
BOILER_B_TOTAL_FLUE_GAS_CORRECTED | BOILER B TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_FUEL_GAS_CORRECTED_TPH*BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS | BOILER_B_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS
BOILER_B_STACK_LOSS_CORRECTED | BOILER B STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_B_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_B_SUPERHEATED_STEAM_BFW_RATIO | BOILER B SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(DESUPERHEATER_B_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_B)/(BOILER_B_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV]; Unknown/no sensor: BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS | CBD_BLOW_DOWN_B[sensor:UN.UO.71FC1200.PV] ¦ BOILER_B_CORRECTED_BFW_FLOW ¦ BOILER_B_STATUS
BOILER_B_CO2_EMISSIONS | BOILER B CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CO2_FORMED*BOILER_B_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CO2_FORMED ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS | BOILER_B_CO2_FORMED ¦ BOILER_B_FUEL_GAS_CORRECTED_TPH ¦ BOILER_B_STATUS
BOILER_B_CALCULATED_AIRFLOW_NM3H | BOILER B CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_AIR_FUEL_MASS_RATIO*BOILER_B_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS | BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_B_CORRECTED_FUEL_FLOW ¦ BOILER_B_STATUS
BOILER_B_SH_PERFORMANCE | BOILER B SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,(BOILER_B_SH_SPECIFIC_DUTY)/0.110075721*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_SH_SPECIFIC_DUTY ¦ BOILER_B_STATUS | BOILER_B_SH_SPECIFIC_DUTY ¦ BOILER_B_STATUS
BOILER_B_ENERGY_GAINED | BOILER B ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_TOTAL_STEAM_ENERGY-BOILER_B_BFW_ENERGY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_BFW_ENERGY ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY | BOILER_B_BFW_ENERGY ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY
BOILER_B_CONVECTION_DUTY | BOILER B CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_ECONOMIZER_DUTY+BOILER_B_SH_DUTY+BOILER_B_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_SH_DUTY ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_B_STATUS | BOILER_B_ECONOMIZER_DUTY ¦ BOILER_B_SH_DUTY ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_B_STATUS
BOILER_B_RADIATION_DUTY | BOILER B RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_ENERGY_GAINED-BOILER_B_CONVECTION_DUTY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS
BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER B PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY ¦ BOILER_B_ENERGY_GAINED ¦ BOILER_B_STATUS
BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER B PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_ENERGY_GAINED ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS | BOILER_B_ENERGY_GAINED ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS
BOILER_B_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER B RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_B_STATUS | BOILER_B_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_B_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_B_STATUS
BOILER_B_RADIATION_SECTION_EFFICIENCY | BOILER B RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_RADIATION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS | BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_RADIATION_DUTY ¦ BOILER_B_STATUS
BOILER_B_CONVECTION_SECTION_EFFICIENCY | BOILER B CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,BOILER_B_CONVECTION_DUTY/BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_CONVECTION_DUTY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS | BOILER_B_CONVECTION_DUTY ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_STATUS
BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER C FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | NORMALIZED BOILER C FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER C FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER C FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL | BOILER_C_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER C FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_C_FG_CO2_CONCENTRATION | NORMALIZED BOILER C FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | NORMALIZED BOILER C FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | NORMALIZED BOILER C FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | NORMALIZED BOILER C FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | NORMALIZED BOILER C FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | NORMALIZED BOILER C FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER C FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_C_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_C_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_C_FG_MW | BOILER C FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_C_FG_NC5_C | NOT COMPUTED |  | Unknown/no sensor: NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION
BOILER_C_FG_CH4_MASS_PERCENTAGE | BOILER C FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_CH4_CONCENTRATION
BOILER_C_FG_ETHANE_MASS_PERCENTAGE | BOILER C FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHANE_CONCENTRATION
BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE | BOILER C FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_ETHYLENE_CONCENTRATION
BOILER_C_FG_PROPANE_MASS_PERCENTAGE | BOILER C FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_PROPANE_CONCENTRATION
BOILER_C_FG_NITROGEN_MASS_PERCENTAGE | BOILER C FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_N2_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_N2_CONCENTRATION
BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE | BOILER C FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_HYDROGEN_CONCENTRATION
BOILER_C_FG_IC4_MASS_PERCENTAGE | BOILER C FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC4_CONCENTRATION
BOILER_C_FG_NC4_MASS_PERCENTAGE | BOILER C FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC4_CONCENTRATION
BOILER_C_FG_NC5_MASS_PERCENTAGE | BOILER C FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_NC5_CONCENTRATION
BOILER_C_FG_IC5_MASS_PERCENTAGE | BOILER C FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_C_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION | BOILER_C_FG_MW ¦ NORMALIZED_BOILER_C_FG_IC5_CONCENTRATION
BOILER_C_FG_DENSITY | BOILER C FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_MW/22.414 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_MW | BOILER_C_FG_MW
BOILER_C_LHV_DESIGEN | BOILER C LHV DESIGEN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_C_FG_DENSITY)/1000 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_DENSITY | BOILER_C_FG_DENSITY
BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER C TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_PERCENTAGE+BOILER_C_FG_ETHANE_MASS_PERCENTAGE+BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_C_FG_PROPANE_MASS_PERCENTAGE+BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_C_FG_NITROGEN_MASS_PERCENTAGE+BOILER_C_FG_IC4_MASS_PERCENTAGE+BOILER_C_FG_NC4_MASS_PERCENTAGE+BOILER_C_FG_NC5_MASS_PERCENTAGE+BOILER_C_FG_IC5_MASS_PERCENTAGE | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_FG_IC4_MASS_PERCENTAGE | BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_FG_IC4_MASS_PERCENTAGE ¦ BOILER_C_FG_IC5_MASS_PERCENTAGE ¦ BOILER_C_FG_NC4_MASS_PERCENTAGE ¦ BOILER_C_FG_NC5_MASS_PERCENTAGE ¦ BOILER_C_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_C_FG_PROPANE_MASS_PERCENTAGE
BOILER_C_FG_CH4_MASS_FRACTION | BOILER C FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_CH4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER C FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER C FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER C FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NITROGEN_MASS_FRACTION | BOILER C FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER C FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_IC4_MASS_FRACTION | BOILER C FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NC4_MASS_FRACTION | BOILER C FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC4_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_NC5_MASS_FRACTION | BOILER C FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_NC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_FG_IC5_MASS_FRACTION | BOILER C FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_PERCENTAGE/BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS | BOILER_C_FG_IC5_MASS_PERCENTAGE ¦ BOILER_C_TOTAL_FUEL_COMPOSTION_MASS
BOILER_C_LHV | BOILER C LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (BOILER_C_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_C_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_C_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_C_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_C_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_C_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_C_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_C_FG_NC5_MASS_FRAC | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION ¦ BOILER_C_FG_NC4_MASS_FRACTION ¦ BOILER_C_FG_NC5_MASS_FRACTION ¦ BOILER_C_FG_NITROGEN_MASS_FRACTION ¦ BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_FG_FLOW_RATE | BOILER C FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_C_FUEL_GAS_FLOW/1000 | COMPUTED | 0.1755
BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER C AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER C AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER C AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER C AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER C AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER C AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER C AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER C AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_H2_CO2_COMBUSTION | BOILER C H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_CH4_CO2_COMBUSTION | BOILER C CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_ETHANE_CO2_COMBUSTION | BOILER C ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHYLENE_CO2_COMBUSTION | BOILER C ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_PROPANE_CO2_COMBUSTION | BOILER C PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_NC4_CO2_COMBUSTION | BOILER C NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_IC4_CO2_COMBUSTION | BOILER C IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_NC5_CO2_COMBUSTION | BOILER C NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_IC5_CO2_COMBUSTION | BOILER C IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_H2_N2_COMBUSTION | BOILER C H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_CH4_N2_COMBUSTION | BOILER C CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_ETHANE_N2_COMBUSTION | BOILER C ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHYLENE_N2_COMBUSTION | BOILER C ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_PROPANE_N2_COMBUSTION | BOILER C PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_IC4_N2_COMBUSTION | BOILER C IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_NC4_N2_COMBUSTION | BOILER C NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_IC5_N2_COMBUSTION | BOILER C IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_NC5_N2_COMBUSTION | BOILER C NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_H2_H2O_COMBUSTION | BOILER C H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION | BOILER_C_FG_HYDROGEN_MASS_FRACTION
BOILER_C_CH4_H2O_COMBUSTION | BOILER C CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION
BOILER_C_ETHANE_H2O_COMBUSTION | BOILER C ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHANE_MASS_FRACTION | BOILER_C_FG_ETHANE_MASS_FRACTION
BOILER_C_ETHYLENE_H2O_COMBUSTION | BOILER C ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_ETHYLENE_MASS_FRACTION | BOILER_C_FG_ETHYLENE_MASS_FRACTION
BOILER_C_PROPANE_H2O_COMBUSTION | BOILER C PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_PROPANE_MASS_FRACTION | BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_IC4_H2O_COMBUSTION | BOILER C IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC4_MASS_FRACTION | BOILER_C_FG_NC4_MASS_FRACTION
BOILER_C_NC4_H2O_COMBUSTION | BOILER C NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_IC4_MASS_FRACTION
BOILER_C_IC5_H2O_COMBUSTION | BOILER C IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_IC5_MASS_FRACTION | BOILER_C_FG_IC5_MASS_FRACTION
BOILER_C_NC5_H2O_COMBUSTION | BOILER C NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_NC5_MASS_FRACTION | BOILER_C_FG_NC5_MASS_FRACTION
BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER C AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_C_AI | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_C_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_C_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_C_CO2_FORMED | BOILER C CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_CH4_CO2_COMBUSTION+BOILER_C_ETHANE_CO2_COMBUSTION+BOILER_C_ETHYLENE_CO2_COMBUSTION+BOILER_C_PROPANE_CO2_COMBUSTION+BOILER_C_NC4_CO2_COMBUSTION+BOILER_C_IC4_CO2_COMBUSTION+BOILER_C_NC5_CO2_COMBUSTION+BOILER_C_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CH4_CO2_COMBUSTION ¦ BOILER_C_ETHANE_CO2_COMBUSTION ¦ BOILER_C_ETHYLENE_CO2_COMBUSTION ¦ BOILER_C_IC4_CO2_COMBUSTION ¦ BOILER_C_IC5_CO2_COMBUSTION | BOILER_C_CH4_CO2_COMBUSTION ¦ BOILER_C_ETHANE_CO2_COMBUSTION ¦ BOILER_C_ETHYLENE_CO2_COMBUSTION ¦ BOILER_C_IC4_CO2_COMBUSTION ¦ BOILER_C_IC5_CO2_COMBUSTION ¦ BOILER_C_NC4_CO2_COMBUSTION ¦ BOILER_C_NC5_CO2_COMBUSTION ¦ BOILER_C_PROPANE_CO2_COMBUSTION
BOILER_C_N2_FORMED | BOILER C N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_H2_N2_COMBUSTION+BOILER_C_CH4_N2_COMBUSTION+BOILER_C_ETHANE_N2_COMBUSTION+BOILER_C_ETHYLENE_N2_COMBUSTION+BOILER_C_PROPANE_N2_COMBUSTION+BOILER_C_IC4_N2_COMBUSTION+BOILER_C_NC4_N2_COMBUSTION+BOILER_C_IC5_N2_COMBUSTION+BOILER_C_NC5_N2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CH4_N2_COMBUSTION ¦ BOILER_C_ETHANE_N2_COMBUSTION ¦ BOILER_C_ETHYLENE_N2_COMBUSTION ¦ BOILER_C_H2_N2_COMBUSTION ¦ BOILER_C_IC4_N2_COMBUSTION | BOILER_C_CH4_N2_COMBUSTION ¦ BOILER_C_ETHANE_N2_COMBUSTION ¦ BOILER_C_ETHYLENE_N2_COMBUSTION ¦ BOILER_C_H2_N2_COMBUSTION ¦ BOILER_C_IC4_N2_COMBUSTION ¦ BOILER_C_IC5_N2_COMBUSTION ¦ BOILER_C_NC4_N2_COMBUSTION ¦ BOILER_C_NC5_N2_COMBUSTION ¦ BOILER_C_PROPANE_N2_COMBUSTION
BOILER_C_H2O_FORMED | BOILER C H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_H2_H2O_COMBUSTION+BOILER_C_CH4_H2O_COMBUSTION+BOILER_C_ETHANE_H2O_COMBUSTION+BOILER_C_ETHYLENE_H2O_COMBUSTION+BOILER_C_PROPANE_H2O_COMBUSTION+BOILER_C_IC4_H2O_COMBUSTION+BOILER_C_NC4_H2O_COMBUSTION+BOILER_C_IC5_H2O_COMBUSTION+BOILER_C_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CH4_H2O_COMBUSTION ¦ BOILER_C_ETHANE_H2O_COMBUSTION ¦ BOILER_C_ETHYLENE_H2O_COMBUSTION ¦ BOILER_C_H2_H2O_COMBUSTION ¦ BOILER_C_IC4_H2O_COMBUSTION | BOILER_C_CH4_H2O_COMBUSTION ¦ BOILER_C_ETHANE_H2O_COMBUSTION ¦ BOILER_C_ETHYLENE_H2O_COMBUSTION ¦ BOILER_C_H2_H2O_COMBUSTION ¦ BOILER_C_IC4_H2O_COMBUSTION ¦ BOILER_C_IC5_H2O_COMBUSTION ¦ BOILER_C_NC4_H2O_COMBUSTION ¦ BOILER_C_NC5_H2O_COMBUSTION ¦ BOILER_C_PROPANE_H2O_COMBUSTION
BOILER_C_VAPOUR_PRESSURE_OF_H2O | BOILER C VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631
BOILER_C_AIR_MOISTURE | BOILER C AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_C_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_C_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645
BOILER_C_CORRECTED_COMBUSTION_AIR | BOILER C CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_C_AIR_MOISTURE) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_C_CORRECTED_COMBUTION_H2O_FORMED | BOILER C CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_C_H2O_FORMED+(BOILER_C_CORRECTED_COMBUSTION_AIR-BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_H2O_FORMED | BOILER_C_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_H2O_FORMED
BOILER_C_EXCESS_AIR | BOILER C EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_C_FLUE_GAS_OXGYGEN)*((BOILER_C_N2_FORMED/28.01)+(BOILER_C_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_C_CO2_FORMED/44.01))/(20.95-BOILER_C_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV]; Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_C_N2_FORMED | BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV] ¦ BOILER_C_CO2_FORMED ¦ BOILER_C_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_C_N2_FORMED
BOILER_C_AIR_FUEL_MASS_RATIO | BOILER C AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_EXCESS_AIR+BOILER_C_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_EXCESS_AIR | BOILER_C_CORRECTED_COMBUSTION_AIR ¦ BOILER_C_EXCESS_AIR
BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER C TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_AIR_MOISTURE | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_AIR_FUEL_MASS_RATIO | BOILER_C_AIR_FUEL_MASS_RATIO
BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER C TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_C_TOTAL_MOISTURE_WITH_AIR+BOILER_C_H2O_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_H2O_FORMED ¦ BOILER_C_TOTAL_MOISTURE_WITH_AIR | BOILER_C_H2O_FORMED ¦ BOILER_C_TOTAL_MOISTURE_WITH_AIR
BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER C CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_C_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] | BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV]
BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER C AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_AIR_CP_REF_T+BOILER_C_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CP_AT_COMBUSTION_TEMPERATURE | BOILER_C_CP_AT_COMBUSTION_TEMPERATURE
BOILER_C_CP_H2_FUEL_TEMP | BOILER C CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_CH4_FUEL_TEMP | BOILER C CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_ETHANE_FUEL_TEMP | BOILER C CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_PROPANE_FUEL_TEMP | BOILER C CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_ETHYLENE_FUEL_TEMP | BOILER C CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_NC4_FUEL_TEMP | BOILER C CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_IC4_FUEL_TEMP | BOILER C CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_NC5_FUEL_TEMP | BOILER C CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_IC5_FUEL_TEMP | BOILER C CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_C_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]
BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER C CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_C_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_C_FG_NC4_MASS_FRACTION/COMPONENT | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION | BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION ¦ BOILER_C_FG_MW ¦ BOILER_C_FG_NC4_MASS_FRACTION ¦ BOILER_C_FG_NC5_MASS_FRACTION ¦ BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER C CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_C_CP_H2_FUEL_TEMP+BOILER_C_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_C_CP_CH4_FUEL_TEMP+(BOILER_C_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_C_CP_ETHYLENE_FUEL_TEMP+(BOILER_C_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_C_CP_ETHANE_FUEL_TEMP+(BOILER_C_FG_P | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CP_CH4_FUEL_TEMP ¦ BOILER_C_CP_ETHANE_FUEL_TEMP ¦ BOILER_C_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_C_CP_H2_FUEL_TEMP ¦ BOILER_C_CP_IC4_FUEL_TEMP (+9 more) | BOILER_C_CP_CH4_FUEL_TEMP ¦ BOILER_C_CP_ETHANE_FUEL_TEMP ¦ BOILER_C_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_C_CP_H2_FUEL_TEMP ¦ BOILER_C_CP_IC4_FUEL_TEMP ¦ BOILER_C_CP_IC5_FUEL_TEMP ¦ BOILER_C_CP_NC4_FUEL_TEMP ¦ BOILER_C_CP_NC5_FUEL_TEMP ¦ BOILER_C_CP_PROPANE_FUEL_TEMP ¦ BOILER_C_FG_CH4_MASS_FRACTION ¦ BOILER_C_FG_ETHANE_MASS_FRACTION ¦ BOILER_C_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_FG_IC4_MASS_FRACTION ¦ BOILER_C_FG_IC5_MASS_FRACTION ¦ BOILER_C_FG_MW ¦ BOILER_C_FG_NC4_MASS_FRACTION ¦ BOILER_C_FG_NC5_MASS_FRACTION ¦ BOILER_C_FG_PROPANE_MASS_FRACTION
BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER C AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_C_FG_MW)/2 | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_C_FG_MW | BOILER_C_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_C_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_C_FG_MW
BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_C_EXCESS_AIR*(1-BOILER_C_AIR_MOISTURE)+BOILER_C_N2_FORMED+BOILER_C_CO2_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_N2_FORMED
BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER C FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_FLUE_GAS_MW | BOILER C FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_C_CO2_FORMED/44.01+BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.96) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_CP_OF_AIR_AT_STACK_TEMP | BOILER C CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_C_STACK_TEMPERATURE+273.15 | COMPUTED | 6.9676
BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER C CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6502
BOILER_C_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER C CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3662
BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER C CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_C_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586
BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER C AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_C_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_C_CO2_FORMED/44.01+BOILER_C_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_C_N2_FORMED/28.01+BOILER_C_EXCESS_AIR/28.85*BOILER_C_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_C_FLUE_GAS_MW)/BOILER_C_FLUE_GAS_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_MW ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED | BOILER_C_CO2_FORMED ¦ BOILER_C_EXCESS_AIR ¦ BOILER_C_FLUE_GAS_MW ¦ BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_N2_FORMED
BOILER_C_CP_OF_H2O_AT_STACK_TEMP | BOILER C CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_C_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_C_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644
BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER C SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_C_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV]; Unknown/no sensor: BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_C_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1313.PV] ¦ BOILER_C_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER C SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_C_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_C_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV]; Unknown/no sensor: BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_C_AIR_FUEL_MASS_RATIO | BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] ¦ BOILER_C_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_C_AIR_FUEL_MASS_RATIO
BOILER_C_MIXED_LHV_PER_KG | BOILER C MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | NOT COMPUTED |  | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER C TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_C_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_C_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER C HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_C_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS | BOILER_C_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_C_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER C HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,9*(BOILER_C_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_C_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_C_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_STATUS | BOILER_C_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_C_STATUS
BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER C HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_C_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER C HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,0*10^-6*28*5654*BOILER_C_BOILER_LOAD) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_STATUS | BOILER_C_STATUS
BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER C TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_C_STATUS | BOILER_C_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_C_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_C_STATUS
BOILER_C_RADIATION_LOSSES | BOILER C RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_MIXED_LHV_PER_KG*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOAD^2-0.0899*BOILER_C_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER C TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_C_RADIATION_LOSSES) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_RADIATION_LOSSES ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_RADIATION_LOSSES ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER C TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_C_BOILER_INDIRECT_EFFICIENCY | BOILER C BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_C_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_C_HP_STEAM_ENTHALPY | BOILER C HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_C)+2.66244961166282*DESUPERHEATER_C_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] ¦ BOILER_A_STATUS
BOILER_C_TOTAL_STEAM_ENERGY | BOILER C TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_HP_STEAM_ENTHALPY ¦ BOILER_C_STATUS | BOILER_C_HP_STEAM_ENTHALPY ¦ BOILER_C_STATUS
BOILER_C_BFW_ENTHALPY | BOILER C BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_C_INLET_TEMPERATURE) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ BOILER_A_STATUS
BOILER_C_CORRECTED_BFW_FLOW | BOILER C CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-(BFW_FLOW_TO_ECONOMIZER_C+BFW_FLOW_TO_DESUPERHEATER_C-DESUPERHEATER_C_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_C))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_C[sensor:UN.UO.71FI1302.PV] ¦ BFW_FLOW_TO_ECONOMIZER_C[sensor:UN.UO.71FI1303.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV]; Unknown/no sensor: BOILER_C_STATUS | BFW_FLOW_TO_DESUPERHEATER_C[sensor:UN.UO.71FI1302.PV] ¦ BFW_FLOW_TO_ECONOMIZER_C[sensor:UN.UO.71FI1303.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV] ¦ BOILER_C_STATUS
BOILER_C_BFW_ENERGY | BOILER C BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*BOILER_C_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_BFW_ENTHALPY ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS | BOILER_C_BFW_ENTHALPY ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS
BOILER_C_FUEL_GAS_ENERGY_INPUT | BOILER C FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FG_FLOW_RATE*1000*BOILER_C_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_STEAM_DRUM_TEMP | BOILER C STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,4.02521999671835*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_C_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV]; Unknown/no sensor: BOILER_C_STATUS | BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_STATUS
BOILER_C_BLOWDOWN_LOSS | BOILER C BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,((CBD_BLOW_DOWN_C/1000)*((BOILER_C_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV]; Unknown/no sensor: BOILER_C_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV] ¦ CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV] ¦ BOILER_C_STATUS
BOILER_C_TOTAL_FLUE_GAS_GENERATED | BOILER C TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW/1000*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_STATUS
BOILER_C_STACK_LOSS | BOILER C STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_CORRECTED_FUEL_FLOW | BOILER C CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_FLOW-((BOILER_C_FUEL_GAS_ENERGY_INPUT-(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY+BOILER_C_BLOWDOWN_LOSS+BOILER_C_STACK_LOSS+BOILER_C_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_C_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_C_BOILER_LOAD^3+0.001*BOILER_C_BOILER_LOAD^2-0.0899*BOILER_C_BOILER_LOAD+3.2426)/100+(BOILE | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_MIXED_LHV_PER_KG | BOILER_C_BFW_ENERGY ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STACK_LOSS ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_FUEL_CONSUMPTION | BOILER C FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER C SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS
BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER C SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_CONSUMPTION/(DESUPERHEATER_C_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS | BOILER_C_FUEL_CONSUMPTION ¦ BOILER_C_STATUS
BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER C CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW*BOILER_C_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_C_THERMAL_EFFICIENCY | BOILER C THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY)/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER C EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_BLOWDOWN_LOSS/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS | BOILER_C_BLOWDOWN_LOSS ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS
BOILER_C_ECONOMIZER_DUTY | BOILER C ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_BFW_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_C_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_C_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV]; Unknown/no sensor: BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV] ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS
BOILER_C_LMTD_ECONOMIZER | BOILER C LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,((673-ECONOMIZER_C_OUTLET_TEMPERATURE)-(BOILER_C_STACK_TEMPERATURE-ECONOMIZER_C_INLET_TEMPERATURE))/ln((673-ECONOMIZER_C_OUTLET_TEMPERATURE)/(-ECONOMIZER_C_INLET_TEMPERATURE+BOILER_C_STACK_TEMPERATURE))) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV]; Unknown/no sensor: BOILER_C_STATUS | ECONOMIZER_C_INLET_TEMPERATURE[sensor:UN.UO.71TI1310.PV] ¦ ECONOMIZER_C_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1302.PV] ¦ BOILER_C_STATUS
BOILER_C_UA_ECONOMIZER | BOILER C UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY/BOILER_C_LMTD_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_LMTD_ECONOMIZER ¦ BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_LMTD_ECONOMIZER ¦ BOILER_C_STATUS
BOILER_C_FOULING_INDEX | BOILER C FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,1/BOILER_C_UA_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_STATUS ¦ BOILER_C_UA_ECONOMIZER | BOILER_C_STATUS ¦ BOILER_C_UA_ECONOMIZER
BOILER_C_SH_DUTY | BOILER C SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW*((BOILER_C_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_C_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_C_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_C_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV]; Unknown/no sensor: BOILER_C_STATUS | BOILER_C_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1303.PV] ¦ BOILER_C_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1319.PV] ¦ BOILER_C_STATUS
BOILER_C_SH_SPECIFIC_DUTY | BOILER C SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_SH_DUTY/DESUPERHEATER_C_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_SH_DUTY ¦ BOILER_C_STATUS | BOILER_C_SH_DUTY ¦ BOILER_C_STATUS
BOILER_C_FUEL_GAS_CORRECTED_TPH | BOILER C FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS
BOILER_C_TOTAL_FLUE_GAS_CORRECTED | BOILER C TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_FUEL_GAS_CORRECTED_TPH*BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS | BOILER_C_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS
BOILER_C_STACK_LOSS_CORRECTED | BOILER C STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_C_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_C_SUPERHEATED_STEAM_BFW_RATIO | BOILER C SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(DESUPERHEATER_C_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_C)/(BOILER_C_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV]; Unknown/no sensor: BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS | CBD_BLOW_DOWN_C[sensor:UN.UO.71FC1300.PV] ¦ BOILER_C_CORRECTED_BFW_FLOW ¦ BOILER_C_STATUS
BOILER_C_CO2_EMISSIONS | BOILER C CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CO2_FORMED*BOILER_C_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CO2_FORMED ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS | BOILER_C_CO2_FORMED ¦ BOILER_C_FUEL_GAS_CORRECTED_TPH ¦ BOILER_C_STATUS
BOILER_C_CALCULATED_AIRFLOW_NM3H | BOILER C CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_AIR_FUEL_MASS_RATIO*BOILER_C_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS | BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_C_CORRECTED_FUEL_FLOW ¦ BOILER_C_STATUS
BOILER_C_SH_PERFORMANCE | BOILER C SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,(BOILER_C_SH_SPECIFIC_DUTY)/0.110075721*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_SH_SPECIFIC_DUTY ¦ BOILER_C_STATUS | BOILER_C_SH_SPECIFIC_DUTY ¦ BOILER_C_STATUS
BOILER_C_ENERGY_GAINED | BOILER C ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_TOTAL_STEAM_ENERGY-BOILER_C_BFW_ENERGY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_BFW_ENERGY ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY | BOILER_C_BFW_ENERGY ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY
BOILER_C_CONVECTION_DUTY | BOILER C CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_ECONOMIZER_DUTY+BOILER_C_SH_DUTY+BOILER_C_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_SH_DUTY ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_C_STATUS | BOILER_C_ECONOMIZER_DUTY ¦ BOILER_C_SH_DUTY ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_C_STATUS
BOILER_C_RADIATION_DUTY | BOILER C RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_ENERGY_GAINED-BOILER_C_CONVECTION_DUTY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS
BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER C PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY ¦ BOILER_C_ENERGY_GAINED ¦ BOILER_C_STATUS
BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER C PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_ENERGY_GAINED ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS | BOILER_C_ENERGY_GAINED ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS
BOILER_C_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER C RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_C_STATUS | BOILER_C_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_C_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_C_STATUS
BOILER_C_RADIATION_SECTION_EFFICIENCY | BOILER C RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_RADIATION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS | BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_RADIATION_DUTY ¦ BOILER_C_STATUS
BOILER_C_CONVECTION_SECTION_EFFICIENCY | BOILER C CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,BOILER_C_CONVECTION_DUTY/BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_CONVECTION_DUTY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS | BOILER_C_CONVECTION_DUTY ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_STATUS
BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER D FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | NORMALIZED BOILER D FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER D FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER D FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL | BOILER_D_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER D FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_D_FG_CO2_CONCENTRATION | NORMALIZED BOILER D FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | NORMALIZED BOILER D FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | NORMALIZED BOILER D FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | NORMALIZED BOILER D FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | NORMALIZED BOILER D FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | NORMALIZED BOILER D FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER D FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_D_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_D_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_D_FG_MW | BOILER D FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_D_FG_NC5_C | NOT COMPUTED |  | Unknown/no sensor: NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION
BOILER_D_FG_CH4_MASS_PERCENTAGE | BOILER D FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_CH4_CONCENTRATION
BOILER_D_FG_ETHANE_MASS_PERCENTAGE | BOILER D FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHANE_CONCENTRATION
BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE | BOILER D FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_ETHYLENE_CONCENTRATION
BOILER_D_FG_PROPANE_MASS_PERCENTAGE | BOILER D FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_PROPANE_CONCENTRATION
BOILER_D_FG_NITROGEN_MASS_PERCENTAGE | BOILER D FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_N2_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_N2_CONCENTRATION
BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE | BOILER D FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_HYDROGEN_CONCENTRATION
BOILER_D_FG_IC4_MASS_PERCENTAGE | BOILER D FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC4_CONCENTRATION
BOILER_D_FG_NC4_MASS_PERCENTAGE | BOILER D FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC4_CONCENTRATION
BOILER_D_FG_NC5_MASS_PERCENTAGE | BOILER D FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_NC5_CONCENTRATION
BOILER_D_FG_IC5_MASS_PERCENTAGE | BOILER D FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_D_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION | BOILER_D_FG_MW ¦ NORMALIZED_BOILER_D_FG_IC5_CONCENTRATION
BOILER_D_FG_DENSITY | BOILER D FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_MW/22.414 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_MW | BOILER_D_FG_MW
BOILER_D_LHV_DESIGEN | BOILER D LHV DESIGEN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_D_FG_DENSITY)/1000 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_DENSITY | BOILER_D_FG_DENSITY
BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER D TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_PERCENTAGE+BOILER_D_FG_ETHANE_MASS_PERCENTAGE+BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_D_FG_PROPANE_MASS_PERCENTAGE+BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_D_FG_NITROGEN_MASS_PERCENTAGE+BOILER_D_FG_IC4_MASS_PERCENTAGE+BOILER_D_FG_NC4_MASS_PERCENTAGE+BOILER_D_FG_NC5_MASS_PERCENTAGE+BOILER_D_FG_IC5_MASS_PERCENTAGE | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_FG_IC4_MASS_PERCENTAGE | BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_FG_IC4_MASS_PERCENTAGE ¦ BOILER_D_FG_IC5_MASS_PERCENTAGE ¦ BOILER_D_FG_NC4_MASS_PERCENTAGE ¦ BOILER_D_FG_NC5_MASS_PERCENTAGE ¦ BOILER_D_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_D_FG_PROPANE_MASS_PERCENTAGE
BOILER_D_FG_CH4_MASS_FRACTION | BOILER D FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_CH4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER D FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER D FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER D FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NITROGEN_MASS_FRACTION | BOILER D FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER D FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_IC4_MASS_FRACTION | BOILER D FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NC4_MASS_FRACTION | BOILER D FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC4_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_NC5_MASS_FRACTION | BOILER D FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_NC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_FG_IC5_MASS_FRACTION | BOILER D FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_PERCENTAGE/BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS | BOILER_D_FG_IC5_MASS_PERCENTAGE ¦ BOILER_D_TOTAL_FUEL_COMPOSTION_MASS
BOILER_D_LHV | BOILER D LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (BOILER_D_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_D_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_D_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_D_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_D_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_D_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_D_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_D_FG_NC5_MASS_FRAC | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION ¦ BOILER_D_FG_NC4_MASS_FRACTION ¦ BOILER_D_FG_NC5_MASS_FRACTION ¦ BOILER_D_FG_NITROGEN_MASS_FRACTION ¦ BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_FG_FLOW_RATE | BOILER D FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main | BOILER_D_FUEL_GAS_FLOW/1000 | COMPUTED | 0.17549
BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER D AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER D AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER D AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER D AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER D AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER D AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER D AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER D AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_H2_CO2_COMBUSTION | BOILER D H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_CH4_CO2_COMBUSTION | BOILER D CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_ETHANE_CO2_COMBUSTION | BOILER D ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHYLENE_CO2_COMBUSTION | BOILER D ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_PROPANE_CO2_COMBUSTION | BOILER D PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_NC4_CO2_COMBUSTION | BOILER D NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_IC4_CO2_COMBUSTION | BOILER D IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_NC5_CO2_COMBUSTION | BOILER D NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_IC5_CO2_COMBUSTION | BOILER D IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_H2_N2_COMBUSTION | BOILER D H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_CH4_N2_COMBUSTION | BOILER D CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_ETHANE_N2_COMBUSTION | BOILER D ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHYLENE_N2_COMBUSTION | BOILER D ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_PROPANE_N2_COMBUSTION | BOILER D PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_IC4_N2_COMBUSTION | BOILER D IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_NC4_N2_COMBUSTION | BOILER D NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_IC5_N2_COMBUSTION | BOILER D IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_NC5_N2_COMBUSTION | BOILER D NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_H2_H2O_COMBUSTION | BOILER D H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION | BOILER_D_FG_HYDROGEN_MASS_FRACTION
BOILER_D_CH4_H2O_COMBUSTION | BOILER D CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION
BOILER_D_ETHANE_H2O_COMBUSTION | BOILER D ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_D_ETHYLENE_H2O_COMBUSTION | BOILER D ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHYLENE_MASS_FRACTION | BOILER_D_FG_ETHYLENE_MASS_FRACTION
BOILER_D_PROPANE_H2O_COMBUSTION | BOILER D PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_PROPANE_MASS_FRACTION | BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_IC4_H2O_COMBUSTION | BOILER D IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC4_MASS_FRACTION | BOILER_D_FG_NC4_MASS_FRACTION
BOILER_D_NC4_H2O_COMBUSTION | BOILER D NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_IC4_MASS_FRACTION
BOILER_D_IC5_H2O_COMBUSTION | BOILER D IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_IC5_MASS_FRACTION | BOILER_D_FG_IC5_MASS_FRACTION
BOILER_D_NC5_H2O_COMBUSTION | BOILER D NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_NC5_MASS_FRACTION | BOILER_D_FG_NC5_MASS_FRACTION
BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER D AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_D_AI | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_D_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_D_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_D_CO2_FORMED | BOILER D CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_CH4_CO2_COMBUSTION+BOILER_D_ETHANE_CO2_COMBUSTION+BOILER_D_ETHYLENE_CO2_COMBUSTION+BOILER_D_PROPANE_CO2_COMBUSTION+BOILER_D_NC4_CO2_COMBUSTION+BOILER_D_IC4_CO2_COMBUSTION+BOILER_D_NC5_CO2_COMBUSTION+BOILER_D_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CH4_CO2_COMBUSTION ¦ BOILER_D_ETHANE_CO2_COMBUSTION ¦ BOILER_D_ETHYLENE_CO2_COMBUSTION ¦ BOILER_D_IC4_CO2_COMBUSTION ¦ BOILER_D_IC5_CO2_COMBUSTION | BOILER_D_CH4_CO2_COMBUSTION ¦ BOILER_D_ETHANE_CO2_COMBUSTION ¦ BOILER_D_ETHYLENE_CO2_COMBUSTION ¦ BOILER_D_IC4_CO2_COMBUSTION ¦ BOILER_D_IC5_CO2_COMBUSTION ¦ BOILER_D_NC4_CO2_COMBUSTION ¦ BOILER_D_NC5_CO2_COMBUSTION ¦ BOILER_D_PROPANE_CO2_COMBUSTION
BOILER_D_N2_FORMED | BOILER D N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_H2_N2_COMBUSTION+BOILER_D_CH4_N2_COMBUSTION+BOILER_D_ETHANE_N2_COMBUSTION+BOILER_D_ETHYLENE_N2_COMBUSTION+BOILER_D_PROPANE_N2_COMBUSTION+BOILER_D_IC4_N2_COMBUSTION+BOILER_D_NC4_N2_COMBUSTION+BOILER_D_IC5_N2_COMBUSTION+BOILER_D_NC5_N2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CH4_N2_COMBUSTION ¦ BOILER_D_ETHANE_N2_COMBUSTION ¦ BOILER_D_ETHYLENE_N2_COMBUSTION ¦ BOILER_D_H2_N2_COMBUSTION ¦ BOILER_D_IC4_N2_COMBUSTION | BOILER_D_CH4_N2_COMBUSTION ¦ BOILER_D_ETHANE_N2_COMBUSTION ¦ BOILER_D_ETHYLENE_N2_COMBUSTION ¦ BOILER_D_H2_N2_COMBUSTION ¦ BOILER_D_IC4_N2_COMBUSTION ¦ BOILER_D_IC5_N2_COMBUSTION ¦ BOILER_D_NC4_N2_COMBUSTION ¦ BOILER_D_NC5_N2_COMBUSTION ¦ BOILER_D_PROPANE_N2_COMBUSTION
BOILER_D_H2O_FORMED | BOILER D H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_H2_H2O_COMBUSTION+BOILER_D_CH4_H2O_COMBUSTION+BOILER_D_ETHANE_H2O_COMBUSTION+BOILER_D_ETHYLENE_H2O_COMBUSTION+BOILER_D_PROPANE_H2O_COMBUSTION+BOILER_D_IC4_H2O_COMBUSTION+BOILER_D_NC4_H2O_COMBUSTION+BOILER_D_IC5_H2O_COMBUSTION+BOILER_D_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CH4_H2O_COMBUSTION ¦ BOILER_D_ETHANE_H2O_COMBUSTION ¦ BOILER_D_ETHYLENE_H2O_COMBUSTION ¦ BOILER_D_H2_H2O_COMBUSTION ¦ BOILER_D_IC4_H2O_COMBUSTION | BOILER_D_CH4_H2O_COMBUSTION ¦ BOILER_D_ETHANE_H2O_COMBUSTION ¦ BOILER_D_ETHYLENE_H2O_COMBUSTION ¦ BOILER_D_H2_H2O_COMBUSTION ¦ BOILER_D_IC4_H2O_COMBUSTION ¦ BOILER_D_IC5_H2O_COMBUSTION ¦ BOILER_D_NC4_H2O_COMBUSTION ¦ BOILER_D_NC5_H2O_COMBUSTION ¦ BOILER_D_PROPANE_H2O_COMBUSTION
BOILER_D_VAPOUR_PRESSURE_OF_H2O | BOILER D VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631
BOILER_D_AIR_MOISTURE | BOILER D AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_D_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_D_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645
BOILER_D_CORRECTED_COMBUSTION_AIR | BOILER D CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_D_AIR_MOISTURE) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_D_CORRECTED_COMBUTION_H2O_FORMED | BOILER D CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_D_H2O_FORMED+(BOILER_D_CORRECTED_COMBUSTION_AIR-BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_H2O_FORMED | BOILER_D_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_H2O_FORMED
BOILER_D_EXCESS_AIR | BOILER D EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_D_FLUE_GAS_OXGYGEN)*((BOILER_D_N2_FORMED/28.01)+(BOILER_D_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_D_CO2_FORMED/44.01))/(20.95-BOILER_D_FLUE_GAS_OXGYGEN)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV]; Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_D_N2_FORMED | BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV] ¦ BOILER_D_CO2_FORMED ¦ BOILER_D_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_D_N2_FORMED
BOILER_D_AIR_FUEL_MASS_RATIO | BOILER D AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_EXCESS_AIR+BOILER_D_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_EXCESS_AIR | BOILER_D_CORRECTED_COMBUSTION_AIR ¦ BOILER_D_EXCESS_AIR
BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER D TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_AIR_MOISTURE | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_AIR_FUEL_MASS_RATIO | BOILER_D_AIR_FUEL_MASS_RATIO
BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER D TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_TOTAL_MOISTURE_WITH_AIR+BOILER_D_H2O_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_H2O_FORMED ¦ BOILER_D_TOTAL_MOISTURE_WITH_AIR | BOILER_D_H2O_FORMED ¦ BOILER_D_TOTAL_MOISTURE_WITH_AIR
BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER D CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_D_COMBUSTION_AIR_TEMPERATURE+273.15)/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] | BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV]
BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER D AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_AIR_CP_REF_T+BOILER_D_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CP_AT_COMBUSTION_TEMPERATURE | BOILER_D_CP_AT_COMBUSTION_TEMPERATURE
BOILER_D_CP_H2_FUEL_TEMP | BOILER D CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_CH4_FUEL_TEMP | BOILER D CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_ETHANE_FUEL_TEMP | BOILER D CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_PROPANE_FUEL_TEMP | BOILER D CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_ETHYLENE_FUEL_TEMP | BOILER D CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_NC4_FUEL_TEMP | BOILER D CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_IC4_FUEL_TEMP | BOILER D CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_NC5_FUEL_TEMP | BOILER D CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_IC5_FUEL_TEMP | BOILER D CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_D_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]
BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER D CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_D_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_D_FG_NC4_MASS_FRACTION/COMPONENT | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION | BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION ¦ BOILER_D_FG_MW ¦ BOILER_D_FG_NC4_MASS_FRACTION ¦ BOILER_D_FG_NC5_MASS_FRACTION ¦ BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER D CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_D_CP_H2_FUEL_TEMP+BOILER_D_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_D_CP_CH4_FUEL_TEMP+(BOILER_D_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_D_CP_ETHYLENE_FUEL_TEMP+(BOILER_D_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_D_CP_ETHANE_FUEL_TEMP+(BOILER_D_FG_P | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CP_CH4_FUEL_TEMP ¦ BOILER_D_CP_ETHANE_FUEL_TEMP ¦ BOILER_D_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_D_CP_H2_FUEL_TEMP ¦ BOILER_D_CP_IC4_FUEL_TEMP (+9 more) | BOILER_D_CP_CH4_FUEL_TEMP ¦ BOILER_D_CP_ETHANE_FUEL_TEMP ¦ BOILER_D_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_D_CP_H2_FUEL_TEMP ¦ BOILER_D_CP_IC4_FUEL_TEMP ¦ BOILER_D_CP_IC5_FUEL_TEMP ¦ BOILER_D_CP_NC4_FUEL_TEMP ¦ BOILER_D_CP_NC5_FUEL_TEMP ¦ BOILER_D_CP_PROPANE_FUEL_TEMP ¦ BOILER_D_FG_CH4_MASS_FRACTION ¦ BOILER_D_FG_ETHANE_MASS_FRACTION ¦ BOILER_D_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_FG_IC4_MASS_FRACTION ¦ BOILER_D_FG_IC5_MASS_FRACTION ¦ BOILER_D_FG_MW ¦ BOILER_D_FG_NC4_MASS_FRACTION ¦ BOILER_D_FG_NC5_MASS_FRACTION ¦ BOILER_D_FG_PROPANE_MASS_FRACTION
BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER D AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_D_FG_MW)/2 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_D_FG_MW | BOILER_D_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_D_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_D_FG_MW
BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_D_EXCESS_AIR*(1-BOILER_D_AIR_MOISTURE)+BOILER_D_N2_FORMED+BOILER_D_CO2_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_N2_FORMED
BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER D FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_FLUE_GAS_MW | BOILER D FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_D_CO2_FORMED/44.01+BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.96) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_CP_OF_AIR_AT_STACK_TEMP | BOILER D CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_D_STACK_TEMPERATURE+273.15 | COMPUTED | 6.9675
BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER D CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6481
BOILER_D_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER D CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3661
BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER D CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_D_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9586
BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER D AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_D_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_D_CO2_FORMED/44.01+BOILER_D_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_D_N2_FORMED/28.01+BOILER_D_EXCESS_AIR/28.85*BOILER_D_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_D_FLUE_GAS_MW)/BOILER_D_FLUE_GAS_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_MW ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED | BOILER_D_CO2_FORMED ¦ BOILER_D_EXCESS_AIR ¦ BOILER_D_FLUE_GAS_MW ¦ BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_N2_FORMED
BOILER_D_CP_OF_H2O_AT_STACK_TEMP | BOILER D CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_D_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_D_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.4644
BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER D SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_D_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV]; Unknown/no sensor: BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_D_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1413.PV] ¦ BOILER_D_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER D SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_D_COMBUSTION_AIR_TEMPERATURE-15.6)*BOILER_D_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV]; Unknown/no sensor: BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_D_AIR_FUEL_MASS_RATIO | BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] ¦ BOILER_D_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_D_AIR_FUEL_MASS_RATIO
BOILER_D_MIXED_LHV_PER_KG | BOILER D MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main | (BOILER_LHV) | NOT COMPUTED |  | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER D TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_D_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_D_SENSIBLE_HEAT_CORRECTION_FOR_FUEL ¦ BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER D HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_D_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS | BOILER_D_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_D_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER D HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,9*(BOILER_D_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_D_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_D_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_STATUS | BOILER_D_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_D_STATUS
BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER D HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_D_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER D HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,0*10^-6*28*5654*BOILER_D_BOILER_LOAD) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_STATUS | BOILER_D_STATUS
BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER D TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_D_STATUS | BOILER_D_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_D_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 ¦ BOILER_D_STATUS
BOILER_D_RADIATION_LOSSES | BOILER D RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_MIXED_LHV_PER_KG*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOAD^2-0.0899*BOILER_D_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER D TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_D_RADIATION_LOSSES) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_RADIATION_LOSSES ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_RADIATION_LOSSES ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER D TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_D_BOILER_INDIRECT_EFFICIENCY | BOILER D BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_D_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_D_HP_STEAM_ENTHALPY | BOILER D HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_D)+2.66244961166282*DESUPERHEATER_D_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV]; Unknown/no sensor: BOILER_A_STATUS | HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV] ¦ BOILER_A_STATUS
BOILER_D_TOTAL_STEAM_ENERGY | BOILER D TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_HP_STEAM_ENTHALPY ¦ BOILER_D_STATUS | BOILER_D_HP_STEAM_ENTHALPY ¦ BOILER_D_STATUS
BOILER_D_BFW_ENTHALPY | BOILER D BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_D_INLET_TEMPERATURE) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ BOILER_A_STATUS
BOILER_D_CORRECTED_BFW_FLOW | BOILER D CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-(BFW_FLOW_TO_ECONOMIZER_D+BFW_FLOW_TO_DESUPERHEATER_D-DESUPERHEATER_D_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_D))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_D[sensor:UN.UO.71FI1402.PV] ¦ BFW_FLOW_TO_ECONOMIZER_D[sensor:UN.UO.71FI1403.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV]; Unknown/no sensor: BOILER_D_STATUS | BFW_FLOW_TO_DESUPERHEATER_D[sensor:UN.UO.71FI1402.PV] ¦ BFW_FLOW_TO_ECONOMIZER_D[sensor:UN.UO.71FI1403.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV] ¦ BOILER_D_STATUS
BOILER_D_BFW_ENERGY | BOILER D BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*BOILER_D_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_BFW_ENTHALPY ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS | BOILER_D_BFW_ENTHALPY ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS
BOILER_D_FUEL_GAS_ENERGY_INPUT | BOILER D FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FG_FLOW_RATE*1000*BOILER_D_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_STEAM_DRUM_TEMP | BOILER D STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,4.02521999671835*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_D_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV]; Unknown/no sensor: BOILER_D_STATUS | BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_STATUS
BOILER_D_BLOWDOWN_LOSS | BOILER D BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,((CBD_BLOW_DOWN_D/1000)*((BOILER_D_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*4.22416911685416-3.01717714574329)*0.2390006))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV]; Unknown/no sensor: BOILER_D_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV] ¦ CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV] ¦ BOILER_D_STATUS
BOILER_D_TOTAL_FLUE_GAS_GENERATED | BOILER D TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW/1000*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_STATUS
BOILER_D_STACK_LOSS | BOILER D STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_FLOW/(1000*1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_CORRECTED_FUEL_FLOW | BOILER D CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_FLOW-((BOILER_D_FUEL_GAS_ENERGY_INPUT-(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY+BOILER_D_BLOWDOWN_LOSS+BOILER_D_STACK_LOSS+BOILER_D_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_D_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_D_BOILER_LOAD^3+0.001*BOILER_D_BOILER_LOAD^2-0.0899*BOILER_D_BOILER_LOAD+3.2426)/100+(BOILE | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_MIXED_LHV_PER_KG | BOILER_D_BFW_ENERGY ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STACK_LOSS ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_FUEL_CONSUMPTION | BOILER D FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER D SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS
BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER D SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_CONSUMPTION/(DESUPERHEATER_D_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS | BOILER_D_FUEL_CONSUMPTION ¦ BOILER_D_STATUS
BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER D CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW*BOILER_D_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_D_THERMAL_EFFICIENCY | BOILER D THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY)/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER D EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_BLOWDOWN_LOSS/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS | BOILER_D_BLOWDOWN_LOSS ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS
BOILER_D_ECONOMIZER_DUTY | BOILER D ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_BFW_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_D_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_D_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV]; Unknown/no sensor: BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV] ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS
BOILER_D_LMTD_ECONOMIZER | BOILER D LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,((673-ECONOMIZER_D_OUTLET_TEMPERATURE)-(BOILER_D_STACK_TEMPERATURE-ECONOMIZER_D_INLET_TEMPERATURE))/ln((673-ECONOMIZER_D_OUTLET_TEMPERATURE)/(-ECONOMIZER_D_INLET_TEMPERATURE+BOILER_D_STACK_TEMPERATURE))) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV]; Unknown/no sensor: BOILER_D_STATUS | ECONOMIZER_D_INLET_TEMPERATURE[sensor:UN.UO.71TI1410.PV] ¦ ECONOMIZER_D_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1402.PV] ¦ BOILER_D_STATUS
BOILER_D_UA_ECONOMIZER | BOILER D UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY/BOILER_D_LMTD_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_LMTD_ECONOMIZER ¦ BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_LMTD_ECONOMIZER ¦ BOILER_D_STATUS
BOILER_D_FOULING_INDEX | BOILER D FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,1/BOILER_D_UA_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_STATUS ¦ BOILER_D_UA_ECONOMIZER | BOILER_D_STATUS ¦ BOILER_D_UA_ECONOMIZER
BOILER_D_SH_DUTY | BOILER D SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW*((BOILER_D_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_D_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_D_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_D_SUPERHEATER_INLET_TEMPERATURE*3.45877718874616+2082.10231045632))*0.239006/1000000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV]; Unknown/no sensor: BOILER_D_STATUS | BOILER_D_STEAM_DRUM_PRESSURE[sensor:UN.UO.71PC1403.PV] ¦ BOILER_D_SUPERHEATER_INLET_TEMPERATURE[sensor:UN.UO.71TI1419.PV] ¦ BOILER_D_STATUS
BOILER_D_SH_SPECIFIC_DUTY | BOILER D SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_SH_DUTY/DESUPERHEATER_D_OUTLET_STEAM_FLOW*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_SH_DUTY ¦ BOILER_D_STATUS | BOILER_D_SH_DUTY ¦ BOILER_D_STATUS
BOILER_D_FUEL_GAS_CORRECTED_TPH | BOILER D FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS
BOILER_D_TOTAL_FLUE_GAS_CORRECTED | BOILER D TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_FUEL_GAS_CORRECTED_TPH*BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS | BOILER_D_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS
BOILER_D_STACK_LOSS_CORRECTED | BOILER D STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_D_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_D_SUPERHEATED_STEAM_BFW_RATIO | BOILER D SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(DESUPERHEATER_D_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_D)/(BOILER_D_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV]; Unknown/no sensor: BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS | CBD_BLOW_DOWN_D[sensor:UN.UO.71FC1400.PV] ¦ BOILER_D_CORRECTED_BFW_FLOW ¦ BOILER_D_STATUS
BOILER_D_CO2_EMISSIONS | BOILER D CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CO2_FORMED*BOILER_D_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CO2_FORMED ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS | BOILER_D_CO2_FORMED ¦ BOILER_D_FUEL_GAS_CORRECTED_TPH ¦ BOILER_D_STATUS
BOILER_D_CALCULATED_AIRFLOW_NM3H | BOILER D CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_AIR_FUEL_MASS_RATIO*BOILER_D_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS | BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_D_CORRECTED_FUEL_FLOW ¦ BOILER_D_STATUS
BOILER_D_SH_PERFORMANCE | BOILER D SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,(BOILER_D_SH_SPECIFIC_DUTY)/0.110075721*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_SH_SPECIFIC_DUTY ¦ BOILER_D_STATUS | BOILER_D_SH_SPECIFIC_DUTY ¦ BOILER_D_STATUS
BOILER_D_ENERGY_GAINED | BOILER D ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_TOTAL_STEAM_ENERGY-BOILER_D_BFW_ENERGY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_BFW_ENERGY ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY | BOILER_D_BFW_ENERGY ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY
BOILER_D_CONVECTION_DUTY | BOILER D CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_ECONOMIZER_DUTY+BOILER_D_SH_DUTY+BOILER_D_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_SH_DUTY ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_D_STATUS | BOILER_D_ECONOMIZER_DUTY ¦ BOILER_D_SH_DUTY ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_D_STATUS
BOILER_D_RADIATION_DUTY | BOILER D RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_ENERGY_GAINED-BOILER_D_CONVECTION_DUTY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS
BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER D PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY ¦ BOILER_D_ENERGY_GAINED ¦ BOILER_D_STATUS
BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER D PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_ENERGY_GAINED ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS | BOILER_D_ENERGY_GAINED ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS
BOILER_D_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER D RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_D_STATUS | BOILER_D_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_D_PER_DUTY_GAINED_IN_RADIANT_SECTION ¦ BOILER_D_STATUS
BOILER_D_RADIATION_SECTION_EFFICIENCY | BOILER D RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_RADIATION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS | BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_RADIATION_DUTY ¦ BOILER_D_STATUS
BOILER_D_CONVECTION_SECTION_EFFICIENCY | BOILER D CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,BOILER_D_CONVECTION_DUTY/BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_CONVECTION_DUTY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS | BOILER_D_CONVECTION_DUTY ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_STATUS
BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER E FUEL COMPOSITION TOTAL | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_CH4_CONCENTRATION+BOILER_FG_ETHANE_CONCENTRATION+BOILER_FG_ETHYLENE_CONCENTRATION+BOILER_FG_PROPANE_CONCENTRATION+BOILER_FG_NC5_CONCENTRATION+BOILER_FG_IC5_CONCENTRATION+BOILER_FG_IC4_CONCENTRATION+BOILER_FG_NC4_CONCENTRATION+BOILER_FG_HYDROGEN_CONCENTRATION+BOILER_FG_N2_CONCENTRATION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_FG_CH4_CONCENTRATION ¦ BOILER_FG_ETHANE_CONCENTRATION ¦ BOILER_FG_HYDROGEN_CONCENTRATION ¦ BOILER_FG_IC4_CONCENTRATION ¦ BOILER_FG_IC5_CONCENTRATION ¦ BOILER_FG_N2_CONCENTRATION ¦ BOILER_FG_NC4_CONCENTRATION ¦ BOILER_FG_NC5_CONCENTRATION ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | NORMALIZED BOILER E FG CH4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_CH4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CH4_CONCENTRATION
NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | NORMALIZED BOILER E FG ETHANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_ETHANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_ETHANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | NORMALIZED BOILER E FG ETHYLENE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | (BOILER_FG_ETHYLENE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL)*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL | BOILER_E_FUEL_COMPOSITION_TOTAL
NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | NORMALIZED BOILER E FG PROPANE CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_PROPANE_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_PROPANE_CONCENTRATION
NORMALIZED_BOILER_E_FG_CO2_CONCENTRATION | NORMALIZED BOILER E FG CO2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_CO2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_CO2_CONCENTRATION
NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | NORMALIZED BOILER E FG IC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC4_CONCENTRATION
NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | NORMALIZED BOILER E FG NC4 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC4_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC4_CONCENTRATION
NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | NORMALIZED BOILER E FG NC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_NC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_NC5_CONCENTRATION
NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | NORMALIZED BOILER E FG IC5 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_IC5_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_IC5_CONCENTRATION
NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | NORMALIZED BOILER E FG N2 CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | BOILER_FG_N2_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL*100 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_N2_CONCENTRATION
NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | NORMALIZED BOILER E FG HYDROGEN CONCENTRATION | MOLE% | LBM_preprocessing_inferred_tags_main | 100*(BOILER_FG_HYDROGEN_CONCENTRATION/BOILER_E_FUEL_COMPOSITION_TOTAL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION | BOILER_E_FUEL_COMPOSITION_TOTAL ¦ BOILER_FG_HYDROGEN_CONCENTRATION
BOILER_E_FG_MW | BOILER E FG MW | G/MOL | LBM_preprocessing_inferred_tags_main | (NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW+NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW+NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW+NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW+NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW+NORMALIZED_BOILER_E_FG_NC5_C | NOT COMPUTED |  | Unknown/no sensor: NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_N2_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION ¦ NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION
BOILER_E_FG_CH4_MASS_PERCENTAGE | BOILER E FG CH4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION*COMPONENT_METHANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_CH4_CONCENTRATION
BOILER_E_FG_ETHANE_MASS_PERCENTAGE | BOILER E FG ETHANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION*COMPONENT_ETHANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHANE_CONCENTRATION
BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE | BOILER E FG ETHYLENE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION*COMPONENT_ETHYLENE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_ETHYLENE_CONCENTRATION
BOILER_E_FG_PROPANE_MASS_PERCENTAGE | BOILER E FG PROPANE MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION*COMPONENT_PROPANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_PROPANE_CONCENTRATION
BOILER_E_FG_NITROGEN_MASS_PERCENTAGE | BOILER E FG NITROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_N2_CONCENTRATION*COMPONENT_NITROGEN_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_N2_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_N2_CONCENTRATION
BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE | BOILER E FG HYDROGEN MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION*COMPONENT_HYDROGEN_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_HYDROGEN_CONCENTRATION
BOILER_E_FG_IC4_MASS_PERCENTAGE | BOILER E FG IC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC4_CONCENTRATION
BOILER_E_FG_NC4_MASS_PERCENTAGE | BOILER E FG NC4 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION*COMPONENT_BUTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC4_CONCENTRATION
BOILER_E_FG_NC5_MASS_PERCENTAGE | BOILER E FG NC5 MASS PERCENTAGE | WT% | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_NC5_CONCENTRATION
BOILER_E_FG_IC5_MASS_PERCENTAGE | BOILER E FG IC5 MASS PERCENTAGE | % | LBM_preprocessing_inferred_tags_main | NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION*COMPONENT_PENTANE_MW/BOILER_E_FG_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION | BOILER_E_FG_MW ¦ NORMALIZED_BOILER_E_FG_IC5_CONCENTRATION
BOILER_E_FG_DENSITY | BOILER E FG DENSITY | KG/NM3 | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_MW/22.414 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_MW | BOILER_E_FG_MW
BOILER_E_LHV_DESIGN | BOILER E LHV DESIGN | - | LBM_preprocessing_inferred_tags_main | (LHV_FG/BOILER_E_FG_DENSITY)/1000 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_DENSITY | BOILER_E_FG_DENSITY
BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER E TOTAL FUEL COMPOSTION MASS | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_PERCENTAGE+BOILER_E_FG_ETHANE_MASS_PERCENTAGE+BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE+BOILER_E_FG_PROPANE_MASS_PERCENTAGE+BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE+BOILER_E_FG_NITROGEN_MASS_PERCENTAGE+BOILER_E_FG_IC4_MASS_PERCENTAGE+BOILER_E_FG_NC4_MASS_PERCENTAGE+BOILER_E_FG_NC5_MASS_PERCENTAGE+BOILER_E_FG_IC5_MASS_PERCENTAGE | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_FG_IC4_MASS_PERCENTAGE | BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_FG_IC4_MASS_PERCENTAGE ¦ BOILER_E_FG_IC5_MASS_PERCENTAGE ¦ BOILER_E_FG_NC4_MASS_PERCENTAGE ¦ BOILER_E_FG_NC5_MASS_PERCENTAGE ¦ BOILER_E_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_E_FG_PROPANE_MASS_PERCENTAGE
BOILER_E_FG_CH4_MASS_FRACTION | BOILER E FG CH4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_CH4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER E FG ETHANE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER E FG ETHYLENE MASS FRACTION | - | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_ETHYLENE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER E FG PROPANE MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_PROPANE_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NITROGEN_MASS_FRACTION | BOILER E FG NITROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NITROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER E FG HYDROGEN MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_HYDROGEN_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_IC4_MASS_FRACTION | BOILER E FG IC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NC4_MASS_FRACTION | BOILER E FG NC4 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC4_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_NC5_MASS_FRACTION | BOILER E FG NC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_NC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_FG_IC5_MASS_FRACTION | BOILER E FG IC5 MASS FRACTION | % | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_PERCENTAGE/BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS | BOILER_E_FG_IC5_MASS_PERCENTAGE ¦ BOILER_E_TOTAL_FUEL_COMPOSTION_MASS
BOILER_E_LHV | BOILER E LHV | MJ/KG | LBM_preprocessing_inferred_tags_main | (BOILER_E_FG_HYDROGEN_MASS_FRACTION*LHV_H2_HYDROGEN+BOILER_E_FG_CH4_MASS_FRACTION*LHV_CH4_METHANE+BOILER_E_FG_NITROGEN_MASS_FRACTION*LHV_N2_NITROGEN+BOILER_E_FG_ETHANE_MASS_FRACTION*LHV_C2H6_ETHANE+BOILER_E_FG_PROPANE_MASS_FRACTION*LHV_C3H8_PROPANE+BOILER_E_FG_IC4_MASS_FRACTION*LHV_IC4+BOILER_E_FG_NC4_MASS_FRACTION*LHV_NC4+BOILER_E_FG_NC5_MASS_FRAC | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION ¦ BOILER_E_FG_NC4_MASS_FRACTION ¦ BOILER_E_FG_NC5_MASS_FRACTION ¦ BOILER_E_FG_NITROGEN_MASS_FRACTION ¦ BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_FG_FLOW_RATE | BOILER E FG FLOW RATE | TPH | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | BOILER_E_FUEL_GAS_FLOW/1.295/1000 | COMPUTED | 0.17993
BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION | BOILER E AIR REQUIRED FOR H2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*34.344 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION | BOILER E AIR REQUIRED FOR CH4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*17.265 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_D_FG_ETHANE_MASS_FRACTION*16.119 | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_FG_ETHANE_MASS_FRACTION | BOILER_D_FG_ETHANE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION | BOILER E AIR REQUIRED FOR ETHYLENE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*14.807 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION | BOILER E AIR REQUIRED FOR PROPANE COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*15.703 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION | BOILER E AIR REQUIRED FOR NC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER E AIR REQUIRED FOR IC4 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*15.487 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION | BOILER E AIR REQUIRED FOR NC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION | BOILER E AIR REQUIRED FOR IC5 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*15.353 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_H2_CO2_COMBUSTION | BOILER E H2 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*0 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_CH4_CO2_COMBUSTION | BOILER E CH4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*2.744 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_ETHANE_CO2_COMBUSTION | BOILER E ETHANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_FRACTION*2.927 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHYLENE_CO2_COMBUSTION | BOILER E ETHYLENE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*3.138 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_PROPANE_CO2_COMBUSTION | BOILER E PROPANE CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*2.994 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_NC4_CO2_COMBUSTION | BOILER E NC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_IC4_CO2_COMBUSTION | BOILER E IC4 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*3.029 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_NC5_CO2_COMBUSTION | BOILER E NC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_IC5_CO2_COMBUSTION | BOILER E IC5 CO2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*3.05 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_H2_N2_COMBUSTION | BOILER E H2 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*26.407 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_CH4_N2_COMBUSTION | BOILER E CH4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*13.275 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_ETHANE_N2_COMBUSTION | BOILER E ETHANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_FRACTION*12.394 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHYLENE_N2_COMBUSTION | BOILER E ETHYLENE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*11.385 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_PROPANE_N2_COMBUSTION | BOILER E PROPANE N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*12.074 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_IC4_N2_COMBUSTION | BOILER E IC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_NC4_N2_COMBUSTION | BOILER E NC4 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*11.908 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_IC5_N2_COMBUSTION | BOILER E IC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_NC5_N2_COMBUSTION | BOILER E NC5 N2 COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*11.805 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_H2_H2O_COMBUSTION | BOILER E H2 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_HYDROGEN_MASS_FRACTION*8.937 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_CH4_H2O_COMBUSTION | BOILER E CH4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_CH4_MASS_FRACTION*2.246 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION
BOILER_E_ETHANE_H2O_COMBUSTION | BOILER E ETHANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHANE_MASS_FRACTION*1.798 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHANE_MASS_FRACTION | BOILER_E_FG_ETHANE_MASS_FRACTION
BOILER_E_ETHYLENE_H2O_COMBUSTION | BOILER E ETHYLENE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_ETHYLENE_MASS_FRACTION*1.285 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_ETHYLENE_MASS_FRACTION | BOILER_E_FG_ETHYLENE_MASS_FRACTION
BOILER_E_PROPANE_H2O_COMBUSTION | BOILER E PROPANE H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_PROPANE_MASS_FRACTION*1.634 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_PROPANE_MASS_FRACTION | BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_IC4_H2O_COMBUSTION | BOILER E IC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC4_MASS_FRACTION | BOILER_E_FG_NC4_MASS_FRACTION
BOILER_E_NC4_H2O_COMBUSTION | BOILER E NC4 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC4_MASS_FRACTION*1.55 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_IC4_MASS_FRACTION
BOILER_E_IC5_H2O_COMBUSTION | BOILER E IC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_IC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_IC5_MASS_FRACTION | BOILER_E_FG_IC5_MASS_FRACTION
BOILER_E_NC5_H2O_COMBUSTION | BOILER E NC5 H2O COMBUSTION | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_FG_NC5_MASS_FRACTION*1.498 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_NC5_MASS_FRACTION | BOILER_E_FG_NC5_MASS_FRACTION
BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER E AIR REQUIRED FOR COMPLETE COMBUSTION | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION+BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION+BOILER_E_AI | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION | BOILER_E_AIR_REQUIRED_FOR_CH4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHANE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_ETHYLENE_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_H2_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_IC4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_IC5_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_NC4_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_NC5_COMBUSTION ¦ BOILER_E_AIR_REQUIRED_FOR_PROPANE_COMBUSTION
BOILER_E_CO2_FORMED | BOILER E CO2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_CH4_CO2_COMBUSTION+BOILER_E_ETHANE_CO2_COMBUSTION+BOILER_E_ETHYLENE_CO2_COMBUSTION+BOILER_E_PROPANE_CO2_COMBUSTION+BOILER_E_NC4_CO2_COMBUSTION+BOILER_E_IC4_CO2_COMBUSTION+BOILER_E_NC5_CO2_COMBUSTION+BOILER_E_IC5_CO2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CH4_CO2_COMBUSTION ¦ BOILER_E_ETHANE_CO2_COMBUSTION ¦ BOILER_E_ETHYLENE_CO2_COMBUSTION ¦ BOILER_E_IC4_CO2_COMBUSTION ¦ BOILER_E_IC5_CO2_COMBUSTION | BOILER_E_CH4_CO2_COMBUSTION ¦ BOILER_E_ETHANE_CO2_COMBUSTION ¦ BOILER_E_ETHYLENE_CO2_COMBUSTION ¦ BOILER_E_IC4_CO2_COMBUSTION ¦ BOILER_E_IC5_CO2_COMBUSTION ¦ BOILER_E_NC4_CO2_COMBUSTION ¦ BOILER_E_NC5_CO2_COMBUSTION ¦ BOILER_E_PROPANE_CO2_COMBUSTION
BOILER_E_N2_FORMED | BOILER E N2 FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_H2_N2_COMBUSTION+BOILER_E_CH4_N2_COMBUSTION+BOILER_E_ETHANE_N2_COMBUSTION+BOILER_E_ETHYLENE_N2_COMBUSTION+BOILER_E_PROPANE_N2_COMBUSTION+BOILER_E_IC4_N2_COMBUSTION+BOILER_E_NC4_N2_COMBUSTION+BOILER_E_IC5_N2_COMBUSTION+BOILER_E_NC5_N2_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CH4_N2_COMBUSTION ¦ BOILER_E_ETHANE_N2_COMBUSTION ¦ BOILER_E_ETHYLENE_N2_COMBUSTION ¦ BOILER_E_H2_N2_COMBUSTION ¦ BOILER_E_IC4_N2_COMBUSTION | BOILER_E_CH4_N2_COMBUSTION ¦ BOILER_E_ETHANE_N2_COMBUSTION ¦ BOILER_E_ETHYLENE_N2_COMBUSTION ¦ BOILER_E_H2_N2_COMBUSTION ¦ BOILER_E_IC4_N2_COMBUSTION ¦ BOILER_E_IC5_N2_COMBUSTION ¦ BOILER_E_NC4_N2_COMBUSTION ¦ BOILER_E_NC5_N2_COMBUSTION ¦ BOILER_E_PROPANE_N2_COMBUSTION
BOILER_E_H2O_FORMED | BOILER E H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_H2_H2O_COMBUSTION+BOILER_E_CH4_H2O_COMBUSTION+BOILER_E_ETHANE_H2O_COMBUSTION+BOILER_E_ETHYLENE_H2O_COMBUSTION+BOILER_E_PROPANE_H2O_COMBUSTION+BOILER_E_IC4_H2O_COMBUSTION+BOILER_E_NC4_H2O_COMBUSTION+BOILER_E_IC5_H2O_COMBUSTION+BOILER_E_NC5_H2O_COMBUSTION | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CH4_H2O_COMBUSTION ¦ BOILER_E_ETHANE_H2O_COMBUSTION ¦ BOILER_E_ETHYLENE_H2O_COMBUSTION ¦ BOILER_E_H2_H2O_COMBUSTION ¦ BOILER_E_IC4_H2O_COMBUSTION | BOILER_E_CH4_H2O_COMBUSTION ¦ BOILER_E_ETHANE_H2O_COMBUSTION ¦ BOILER_E_ETHYLENE_H2O_COMBUSTION ¦ BOILER_E_H2_H2O_COMBUSTION ¦ BOILER_E_IC4_H2O_COMBUSTION ¦ BOILER_E_IC5_H2O_COMBUSTION ¦ BOILER_E_NC4_H2O_COMBUSTION ¦ BOILER_E_NC5_H2O_COMBUSTION ¦ BOILER_E_PROPANE_H2O_COMBUSTION
BOILER_E_VAPOUR_PRESSURE_OF_H2O | BOILER E VAPOUR PRESSURE OF H2O | MMHG | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631
BOILER_E_AIR_MOISTURE | BOILER E AIR MOISTURE | KG MOIST/KG AIR | LBM_preprocessing_inferred_tags_main | BOILER_E_VAPOUR_PRESSURE_OF_H2O/(760-BOILER_E_VAPOUR_PRESSURE_OF_H2O*RELATIVE_HUMIDITY_CLEAN)*RELATIVE_HUMIDITY_CLEAN*18.015/28.96 | COMPUTED | 0.000645
BOILER_E_CORRECTED_COMBUSTION_AIR | BOILER E CORRECTED COMBUSTION AIR | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION/(1-BOILER_E_AIR_MOISTURE) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION
BOILER_E_CORRECTED_COMBUTION_H2O_FORMED | BOILER E CORRECTED COMBUTION H2O FORMED | KG | LBM_preprocessing_inferred_tags_main | BOILER_E_H2O_FORMED+(BOILER_E_CORRECTED_COMBUSTION_AIR-BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_H2O_FORMED | BOILER_E_AIR_REQUIRED_FOR_COMPLETE_COMBUSTION ¦ BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_H2O_FORMED
BOILER_E_EXCESS_AIR | BOILER E EXCESS AIR | KG | LBM_preprocessing_inferred_tags_main | ((28.96*BOILER_E_FLUE_GAS_OXGYGEN_NEW)*((BOILER_E_N2_FORMED/28.01)+(BOILER_E_CORRECTED_COMBUTION_H2O_FORMED/18.015)+(BOILER_E_CO2_FORMED/44.01))/(20.95-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV]; Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_E_N2_FORMED | BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILER_E_CO2_FORMED ¦ BOILER_E_CORRECTED_COMBUTION_H2O_FORMED ¦ BOILER_E_N2_FORMED
BOILER_E_AIR_FUEL_MASS_RATIO | BOILER E AIR FUEL MASS RATIO | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_EXCESS_AIR+BOILER_E_CORRECTED_COMBUSTION_AIR | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_EXCESS_AIR | BOILER_E_CORRECTED_COMBUSTION_AIR ¦ BOILER_E_EXCESS_AIR
BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER E TOTAL MOISTURE WITH AIR | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_AIR_MOISTURE | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_E_AIR_FUEL_MASS_RATIO
BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER E TOTAL H2O PER KG OF FUEL | KG/ KG FUEL | LBM_preprocessing_inferred_tags_main | BOILER_E_TOTAL_MOISTURE_WITH_AIR+BOILER_E_H2O_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_H2O_FORMED ¦ BOILER_E_TOTAL_MOISTURE_WITH_AIR | BOILER_E_H2O_FORMED ¦ BOILER_E_TOTAL_MOISTURE_WITH_AIR
BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER E CP AT COMBUSTION TEMPERATURE | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)-9.647459*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2+16.63537*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^3+(0.000117/((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_COMBUSTION_AIR_TEMP+273.15)/1000)+57.86644*((BOILER_E_COMBUSTION_AIR | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV] | BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV]
BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED | BOILER E AIR CP FOR SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_AIR_CP_REF_T+BOILER_E_CP_AT_COMBUSTION_TEMPERATURE)/2)/28.96 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CP_AT_COMBUSTION_TEMPERATURE | BOILER_E_CP_AT_COMBUSTION_TEMPERATURE
BOILER_E_CP_H2_FUEL_TEMP | BOILER E CP H2 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((33.066178)-11.363417*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)+11.432816*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-2.772874*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(-0.158558/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_CH4_FUEL_TEMP | BOILER E CP CH4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((-0.703029)+108.4773*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-42.52157*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+5.862788*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.678565/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_ETHANE_FUEL_TEMP | BOILER E CP ETHANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (6.08160993967773+173.58246031667*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-66.9190547406319*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+9.08912024736972*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.129136456966982/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_PROPANE_FUEL_TEMP | BOILER E CP PROPANE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (12.6608072783283+232.070245794953*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-70.3446118121155*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+0.60714221002859*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0269571781100411/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_ETHYLENE_FUEL_TEMP | BOILER E CP ETHYLENE FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-6.38788+184.4019*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-112.9718*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2+28.49593*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+0.31554/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2)*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_NC4_FUEL_TEMP | BOILER E CP NC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (22.1581076705715+292.589410831127*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-85.8165101864775*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-1.01394039648879*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.00634969201331822/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_IC4_FUEL_TEMP | BOILER E CP IC4 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (8.32665517242186+344.923323425655*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)--141.649866470373*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-17.402696038734*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.0260047492494904/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_NC5_FUEL_TEMP | BOILER E CP NC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-36.7350853904756+580.375772029461*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-341.586537384626*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-78.4996542134237*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(1.08616950221781/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_IC5_FUEL_TEMP | BOILER E CP IC5 FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (-16.1426869390769+517.363683637786*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)-271.314078126683*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2-56.1566185580689*((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^3+(0.317133464208019/((BOILER_E_MAIN_FUEL_GAS_TEMPERATURE+273.15)/1000)^2))*0.239 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]
BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP | BOILER E CP TOTAL FUEL AT REF TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*6.876+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*8.45+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*10.02+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*12.52+(BOILER_E_FG_PROPANE_MASS_FRACTION/COMPONENT_PROPANE_MW*17.72+(BOILER_E_FG_NC4_MASS_FRACTION/COMPONENT | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION | BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION ¦ BOILER_E_FG_MW ¦ BOILER_E_FG_NC4_MASS_FRACTION ¦ BOILER_E_FG_NC5_MASS_FRACTION ¦ BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP | BOILER E CP TOTAL FUEL AT FUEL TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_FG_HYDROGEN_MASS_FRACTION/COMPONENT_HYDROGEN_MW)*BOILER_E_CP_H2_FUEL_TEMP+BOILER_E_FG_CH4_MASS_FRACTION/COMPONENT_METHANE_MW*BOILER_E_CP_CH4_FUEL_TEMP+(BOILER_E_FG_ETHYLENE_MASS_FRACTION/COMPONENT_ETHYLENE_MW)*BOILER_E_CP_ETHYLENE_FUEL_TEMP+(BOILER_E_FG_ETHANE_MASS_FRACTION/COMPONENT_ETHANE_MW)*BOILER_E_CP_ETHANE_FUEL_TEMP+(BOILER_E_FG_P | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CP_CH4_FUEL_TEMP ¦ BOILER_E_CP_ETHANE_FUEL_TEMP ¦ BOILER_E_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_E_CP_H2_FUEL_TEMP ¦ BOILER_E_CP_IC4_FUEL_TEMP (+9 more) | BOILER_E_CP_CH4_FUEL_TEMP ¦ BOILER_E_CP_ETHANE_FUEL_TEMP ¦ BOILER_E_CP_ETHYLENE_FUEL_TEMP ¦ BOILER_E_CP_H2_FUEL_TEMP ¦ BOILER_E_CP_IC4_FUEL_TEMP ¦ BOILER_E_CP_IC5_FUEL_TEMP ¦ BOILER_E_CP_NC4_FUEL_TEMP ¦ BOILER_E_CP_NC5_FUEL_TEMP ¦ BOILER_E_CP_PROPANE_FUEL_TEMP ¦ BOILER_E_FG_CH4_MASS_FRACTION ¦ BOILER_E_FG_ETHANE_MASS_FRACTION ¦ BOILER_E_FG_ETHYLENE_MASS_FRACTION ¦ BOILER_E_FG_HYDROGEN_MASS_FRACTION ¦ BOILER_E_FG_IC4_MASS_FRACTION ¦ BOILER_E_FG_IC5_MASS_FRACTION ¦ BOILER_E_FG_MW ¦ BOILER_E_FG_NC4_MASS_FRACTION ¦ BOILER_E_FG_NC5_MASS_FRACTION ¦ BOILER_E_FG_PROPANE_MASS_FRACTION
BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER E AVG CP OF FUEL GAS SENSIBLE HEAT CORRECTED | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | ((BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP+BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP)/BOILER_E_FG_MW)/2 | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_E_FG_MW | BOILER_E_CP_TOTAL_FUEL_AT_FUEL_TEMP ¦ BOILER_E_CP_TOTAL_FUEL_AT_REF_TEMP ¦ BOILER_E_FG_MW
BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E DRY FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_E_EXCESS_AIR*(1-BOILER_E_AIR_MOISTURE)+BOILER_E_N2_FORMED+BOILER_E_CO2_FORMED | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_N2_FORMED
BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER E FLUE GAS PER FUEL MASS RATIO | KG/KG fuel | LBM_preprocessing_inferred_tags_main | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_FLUE_GAS_MW | BOILER E FLUE GAS MW | kg/kmol | LBM_preprocessing_inferred_tags_main | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/(BOILER_E_CO2_FORMED/44.01+BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL/18.015+BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.96) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED ¦ BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_CP_OF_AIR_AT_STACK_TEMP | BOILER E CP OF AIR AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | (((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239*0.79)+(((31.32234)-20.23531*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)+57.86644*((BOILER_E_STACK_TEMPERATURE+273.15 | COMPUTED | 6.9677
BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP | BOILER E CP FLUE GAS CO2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((24.99735)+55.18696*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-33.69137*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+7.948387*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(-0.136638/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 8.6572
BOILER_E_CP_FLUE_GAS_H2O_AT_STACK_TEMP | BOILER E CP FLUE GAS H2O AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | 8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2) | COMPUTED | 8.3667
BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP | BOILER E CP FLUE GAS N2 AT STACK TEMP | CAL/MOL °C | LBM_preprocessing_inferred_tags_main | ((28.98641)+1.85398*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)-9.647459*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2+16.63537*((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^3+(0.000117/((BOILER_E_STACK_TEMPERATURE+273.15)/1000)^2))*0.239 | COMPUTED | 6.9587
BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP | BOILER E AVG CP OF FLUE GAS AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (BOILER_E_CP_FLUE_GAS_CO2_AT_STACK_TEMP*BOILER_E_CO2_FORMED/44.01+BOILER_E_CP_FLUE_GAS_N2_AT_STACK_TEMP*BOILER_E_N2_FORMED/28.01+BOILER_E_EXCESS_AIR/28.85*BOILER_E_CP_OF_AIR_AT_STACK_TEMP)/(BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO/BOILER_E_FLUE_GAS_MW)/BOILER_E_FLUE_GAS_MW | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_MW ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED | BOILER_E_CO2_FORMED ¦ BOILER_E_EXCESS_AIR ¦ BOILER_E_FLUE_GAS_MW ¦ BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_N2_FORMED
BOILER_E_CP_OF_H2O_AT_STACK_TEMP | BOILER E CP OF H2O AT STACK TEMP | KCAL/Kg°C | LBM_preprocessing_inferred_tags_main | (8.22+0.00015*(BOILER_E_STACK_TEMPERATURE+273.15)+0.00000134*((BOILER_E_STACK_TEMPERATURE+273.15)^2))/18.015 | COMPUTED | 0.46443
BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER E SENSIBLE HEAT CORRECTION FOR FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)<0,0,BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED*(BOILER_E_MAIN_FUEL_GAS_TEMPERATURE-15.6)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV]; Unknown/no sensor: BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED | BOILER_E_MAIN_FUEL_GAS_TEMPERATURE[sensor:UN.UO.71TI1513.PV] ¦ BOILER_E_AVG_CP_OF_FUEL_GAS_SENSIBLE_HEAT_CORRECTED
BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR | BOILER E SENSBILE HEAT CORRECTION FOR AIR | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED*(BOILER_E_COMBUSTION_AIR_TEMP-15.6)*BOILER_E_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV]; Unknown/no sensor: BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV] ¦ BOILER_E_AIR_CP_FOR_SENSIBLE_HEAT_CORRECTED ¦ BOILER_E_AIR_FUEL_MASS_RATIO
BOILER_E_MIXED_LHV_PER_KG | BOILER E MIXED LHV PER KG | Kcal/kg | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | (BOILER_LHV) | NOT COMPUTED |  | Unknown/no sensor: BOILER_LHV | BOILER_LHV
BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER E TOTAL HEAT INPUT PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL+BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR+BOILER_E_MIXED_LHV_PER_KG) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG ¦ BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL | BOILER_E_MIXED_LHV_PER_KG ¦ BOILER_E_SENSBILE_HEAT_CORRECTION_FOR_AIR ¦ BOILER_E_SENSIBLE_HEAT_CORRECTION_FOR_FUEL
BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 | BOILER E HEAT LOSS DUE TO DRY FLUE GAS L1 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO*((BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP*(BOILER_E_STACK_TEMPERATURE-15.6)))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_AVG_CP_OF_FLUE_GAS_AT_STACK_TEMP ¦ BOILER_E_DRY_FLUE_GAS_PER_FUEL_MASS_RATIO
BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 | BOILER E HEAT LOSS DUE TO EVAPORATION OF WATER FORMED DUE TO H2 IN FUEL L2 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,9*(BOILER_E_FG_HYDROGEN_MASS_FRACTION)*(584+(BOILER_E_CP_OF_H2O_AT_STACK_TEMP)*(BOILER_E_STACK_TEMPERATURE-AMBIENT_TEMPERATURE))) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FG_HYDROGEN_MASS_FRACTION | BOILER_E_FG_HYDROGEN_MASS_FRACTION
BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER E HEAT LOSS DUE TO H2O IN STACK L3 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL*(BOILER_E_STACK_TEMPERATURE*1.77251246754294+2494.5133413964-2529.43)/4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL | BOILER_E_TOTAL_H2O_PER_KG_OF_FUEL
BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4 | BOILER E HEAT LOSS DUE TO INCOMPLETE COMBUSTIONL4 | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,0*10^-6*28*5654*BOILER_E_BOILER_LOAD) | COMPUTED | 0
BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER E TOTAL BOILER STACK LOSS PER KG FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_HEAT_LOSS_DUE_TO_INCOMPLETE_COMBUSTIONL4+BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3+BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1+BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 | BOILER_E_HEAT_LOSS_DUE_TO_DRY_FLUE_GAS_L1 ¦ BOILER_E_HEAT_LOSS_DUE_TO_EVAPORATION_OF_WATER_FORMED_DUE_TO_H2_IN_FUEL_L2 ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3
BOILER_E_RADIATION_LOSSES | BOILER E RADIATION LOSSES | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_MIXED_LHV_PER_KG*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOILER_LOAD^2-0.0899*BOILER_E_BOILER_LOAD+3.2426)/100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER E TOTAL HEAT LOSS PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL+BOILER_E_RADIATION_LOSSES) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_RADIATION_LOSSES ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_RADIATION_LOSSES ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL | BOILER E TOTAL HEAT ABSORBED PER KG OF FUEL | KCAL/KG Fuel | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL-BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_LOSS_PER_KG_OF_FUEL
BOILER_E_BOILER_INDIRECT_EFFICIENCY | BOILER E BOILER INDIRECT EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL/BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL | BOILER_E_TOTAL_HEAT_ABSORBED_PER_KG_OF_FUEL ¦ BOILER_E_TOTAL_HEAT_INPUT_PER_KG_OF_FUEL
BOILER_E_HP_STEAM_ENTHALPY | BOILER E HP STEAM ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,(2175.54628147543-1.32764297764643*(HP_STEAM_PRESSURE_FROM_DS_E)+2.66244961166282*DESUPERHEATER_E_OUTLET_TEMPERATURE)*0.239+2) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS | BOILER_A_STATUS
BOILER_E_TOTAL_STEAM_ENERGY | BOILER E TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_HP_STEAM_ENTHALPY/1000000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_HP_STEAM_ENTHALPY | BOILER_E_HP_STEAM_ENTHALPY
BOILER_E_BFW_ENTHALPY | BOILER E BFW ENTHALPY | Kcal/Kg | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,ECONOMIZER_E_INLET_TEMPERATURE) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV]; Unknown/no sensor: BOILER_A_STATUS | ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ BOILER_A_STATUS
BOILER_E_CORRECTED_BFW_FLOW | BOILER E CORRECTED BFW FLOW | T/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-(BFW_FLOW_TO_ECONOMIZER_E+BFW_FLOW_TO_DESUPERHEATER_E-DESUPERHEATER_E_OUTLET_STEAM_FLOW-CBD_BLOW_DOWN_E))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_FLOW_TO_DESUPERHEATER_E[sensor:UN.UO.71FC1502.PV] ¦ BFW_FLOW_TO_ECONOMIZER_E[sensor:UN.UO.71FC1503.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV] | BFW_FLOW_TO_DESUPERHEATER_E[sensor:UN.UO.71FC1502.PV] ¦ BFW_FLOW_TO_ECONOMIZER_E[sensor:UN.UO.71FC1503.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV]
BOILER_E_BFW_ENERGY | BOILER E BFW ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*BOILER_E_BFW_ENTHALPY/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_BFW_ENTHALPY ¦ BOILER_E_CORRECTED_BFW_FLOW | BOILER_E_BFW_ENTHALPY ¦ BOILER_E_CORRECTED_BFW_FLOW
BOILER_E_FUEL_GAS_ENERGY_INPUT | BOILER E FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FG_FLOW_RATE*1000*BOILER_E_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
BOILER_E_STEAM_DRUM_TEMP | BOILER E STEAM DRUM TEMP | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,4.02521999671835*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^3-4.64392873298701*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)^2+11.2370106828649*log(BOILER_E_STEAM_DRUM_PRESSURE*98.065)+83.4806425229703) | COMPUTED | 0
BOILER_E_BLOWDOWN_LOSS | BOILER E BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,((CBD_BLOW_DOWN_E/1000)*((BOILER_E_STEAM_DRUM_PRESSURE*2.11087739028321+BOILER_E_STEAM_DRUM_TEMP*2.94757709065418+278.050085762461)*0.2390006-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+BOILER_E_STEAM_DRUM_TEMP*4.22416911685416-3.01717714574329)*0.2390006))/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV] | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV]
BOILER_E_TOTAL_FLUE_GAS_GENERATED | BOILER E TOTAL FLUE GAS GENERATED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295/1000*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO
BOILER_E_STACK_LOSS | BOILER E STACK LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_FLOW/1.295/(1000*1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_CORRECTED_FUEL_FLOW | BOILER E CORRECTED FUEL FLOW | kg/hr | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_FLOW/1.295-((BOILER_E_FUEL_GAS_ENERGY_INPUT-(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY+BOILER_E_BLOWDOWN_LOSS+BOILER_E_STACK_LOSS+BOILER_E_FUEL_GAS_ENERGY_INPUT*0.0112+BOILER_E_FUEL_GAS_ENERGY_INPUT*(-0.000004*BOILER_E_BOILER_LOAD^3+0.001*BOILER_E_BOILER_LOAD^2-0.0899*BOILER_E_BOILER_LOAD+3.2426)/100+ | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_E_MIXED_LHV_PER_KG | BOILER_E_BFW_ENERGY ¦ BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_HEAT_LOSS_DUE_TO_H2O_IN_STACK_L3 ¦ BOILER_E_MIXED_LHV_PER_KG ¦ BOILER_E_STACK_LOSS ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_FUEL_CONSUMPTION | BOILER E FUEL CONSUMPTION | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GCAL | BOILER E SPECIFIC ENERGY CONSUMPTION IN GCAL | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION
BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ | BOILER E SPECIFIC ENERGY CONSUMPTION IN GJ | GJ/t | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_CONSUMPTION/(DESUPERHEATER_E_OUTLET_STEAM_FLOW/1000)*4.184) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_CONSUMPTION | BOILER_E_FUEL_CONSUMPTION
BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER E CORRECTED FUEL GAS ENERGY INPUT | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW*BOILER_E_MIXED_LHV_PER_KG/10^6) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG | BOILER_E_CORRECTED_FUEL_FLOW ¦ BOILER_E_MIXED_LHV_PER_KG
BOILER_E_THERMAL_EFFICIENCY | BOILER E THERMAL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY)/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_EFFICIENCY_LOSS_DUE_TO_BLOWDOWN | BOILER E EFFICIENCY LOSS DUE TO BLOWDOWN | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_BLOWDOWN_LOSS/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_BLOWDOWN_LOSS ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
BOILER_E_ECONOMIZER_DUTY | BOILER E ECONOMIZER DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_BFW_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*0.0336523715096497+ECONOMIZER_E_OUTLET_TEMPERATURE*4.52730333899183-53.5667904511771)-(BFW_PRESSURE_TO_BOILER*0.0678913878546345+ECONOMIZER_E_INLET_TEMPERATURE*4.22416911685416-3.01717714574329))*0.239006/1000) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV]; Unknown/no sensor: BOILER_E_CORRECTED_BFW_FLOW | BFW_PRESSURE_TO_BOILER[sensor:UN.UO.71PI1021A.PV] ¦ ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV] ¦ BOILER_E_CORRECTED_BFW_FLOW
BOILER_E_LMTD_ECONOMIZER | BOILER E LMTD ECONOMIZER | DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,((673-ECONOMIZER_E_OUTLET_TEMPERATURE)-(BOILER_E_STACK_TEMPERATURE-ECONOMIZER_E_INLET_TEMPERATURE))/ln((673-ECONOMIZER_E_OUTLET_TEMPERATURE)/(-ECONOMIZER_E_INLET_TEMPERATURE+BOILER_E_STACK_TEMPERATURE))) | NOT COMPUTED |  | PI exists but NOT in hierarchy: ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV] | ECONOMIZER_E_INLET_TEMPERATURE[sensor:UN.UO.71TI1510.PV] ¦ ECONOMIZER_E_OUTLET_TEMPERATURE[sensor:UN.UO.71TI1502.PV]
BOILER_E_UA_ECONOMIZER | BOILER E UA ECONOMIZER | Gcal/h/DEGC | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY/BOILER_E_LMTD_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_LMTD_ECONOMIZER | BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_LMTD_ECONOMIZER
BOILER_E_FOULING_INDEX | BOILER E FOULING INDEX | DEGC h/Gcal | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,1/BOILER_E_UA_ECONOMIZER) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_UA_ECONOMIZER | BOILER_E_UA_ECONOMIZER
BOILER_E_SH_DUTY | BOILER E SH DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW*((BOILER_E_STEAM_DRUM_PRESSURE*-2.64315212289699+DESUPERHEATER_E_OUTLET_TEMPERATURE*3.58096116723573+1939.73413132244)-(BOILER_E_STEAM_DRUM_PRESSURE*-4.27591051303366+BOILER_E_STEAM_DRUM_TEMP*3.45877718874616+2082.10231045632))*0.239006/1000000) | COMPUTED | 0
BOILER_E_SH_SPECIFIC_DUTY | BOILER E SH SPECIFIC DUTY | Gcal/t | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_SH_DUTY/DESUPERHEATER_E_OUTLET_STEAM_FLOW*1000) | COMPUTED | 0
BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER E FUEL GAS CORRECTED TPH | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CORRECTED_FUEL_FLOW/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_CORRECTED_FUEL_FLOW
BOILER_E_TOTAL_FLUE_GAS_CORRECTED | BOILER E TOTAL FLUE GAS CORRECTED | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_FUEL_GAS_CORRECTED_TPH*BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_FLUE_GAS_PER_FUEL_MASS_RATIO ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH
BOILER_E_STACK_LOSS_CORRECTED | BOILER E STACK LOSS CORRECTED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL*BOILER_E_FUEL_GAS_CORRECTED_TPH/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_FUEL_GAS_CORRECTED_TPH ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL | BOILER_E_FUEL_GAS_CORRECTED_TPH ¦ BOILER_E_TOTAL_BOILER_STACK_LOSS_PER_KG_FUEL
BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER E SUPERHEATED STEAM BFW RATIO | - | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(DESUPERHEATER_E_OUTLET_STEAM_FLOW+CBD_BLOW_DOWN_E)/(BOILER_E_CORRECTED_BFW_FLOW*1000)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV]; Unknown/no sensor: BOILER_E_CORRECTED_BFW_FLOW | CBD_BLOW_DOWN_E[sensor:UN.UO.71FC1500.PV] ¦ BOILER_E_CORRECTED_BFW_FLOW
BOILER_E_CO2_EMISSIONS | BOILER E CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CO2_FORMED*BOILER_E_FUEL_GAS_CORRECTED_TPH) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CO2_FORMED ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH | BOILER_E_CO2_FORMED ¦ BOILER_E_FUEL_GAS_CORRECTED_TPH
BOILER_E_CALCULATED_AIRFLOW_NM3H | BOILER E CALCULATED AIRFLOW NM3H | Nm3/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_AIR_FUEL_MASS_RATIO*BOILER_E_CORRECTED_FUEL_FLOW/(28.96/22.414)/1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_AIR_FUEL_MASS_RATIO ¦ BOILER_E_CORRECTED_FUEL_FLOW | BOILER_E_AIR_FUEL_MASS_RATIO ¦ BOILER_E_CORRECTED_FUEL_FLOW
BOILER_E_SH_PERFORMANCE | BOILER E SH PERFORMANCE | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,(BOILER_E_SH_SPECIFIC_DUTY)/0.110075721*100) | COMPUTED | 0
BOILER_E_ENERGY_GAINED | BOILER E ENERGY GAINED | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_TOTAL_STEAM_ENERGY-BOILER_E_BFW_ENERGY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_BFW_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY | BOILER_E_BFW_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_E_CONVECTION_DUTY | BOILER E CONVECTION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_ECONOMIZER_DUTY+BOILER_E_SH_DUTY+BOILER_E_STACK_LOSS_CORRECTED) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_STACK_LOSS_CORRECTED | BOILER_E_ECONOMIZER_DUTY ¦ BOILER_E_STACK_LOSS_CORRECTED
BOILER_E_RADIATION_DUTY | BOILER E RADIATION DUTY | Gcal/h | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_ENERGY_GAINED-BOILER_E_CONVECTION_DUTY) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED
BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION | BOILER E PERC DUTY GAINED IN CONVECTION SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED | BOILER_E_CONVECTION_DUTY ¦ BOILER_E_ENERGY_GAINED
BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER E PER DUTY GAINED IN RADIANT SECTION | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_ENERGY_GAINED*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_ENERGY_GAINED ¦ BOILER_E_RADIATION_DUTY | BOILER_E_ENERGY_GAINED ¦ BOILER_E_RADIATION_DUTY
BOILER_E_RADIATION_DUTY_TO_CONVECTION_DUTY | BOILER E RADIATION DUTY/CONVECTION DUTY | [-] | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION/BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION | BOILER_E_PERC_DUTY_GAINED_IN_CONVECTION_SECTION ¦ BOILER_E_PER_DUTY_GAINED_IN_RADIANT_SECTION
BOILER_E_RADIATION_SECTION_EFFICIENCY | BOILER E RADIATION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_RADIATION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_RADIATION_DUTY | BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_RADIATION_DUTY
BOILER_E_CONVECTION_SECTION_EFFICIENCY | BOILER E CONVECTION SECTION EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | if(BOILER_E_STATUS==0,0,BOILER_E_CONVECTION_DUTY/BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT*100) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_CONVECTION_DUTY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_E_CONVECTION_DUTY ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION | OVER ALL SPECIFIC ENERGY CONSUMPTION | GJ/T | LBM_preprocessing_inferred_tags_main | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_D_TOTAL_STEAM_ENERGY*BOILER_D_STATUS+B | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS (+4 more) | BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_E_TOTAL_STEAM_ENERGY
TOTAL_STEAM_PRODUCTION | TOTAL STEAM PRODUCTION | T/h | LBM_preprocessing_inferred_tags_main | (DESUPERHEATER_OUTLET_STEAM_FLOW*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_STEAM_FLOW*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_STEAM_FLOW*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_STEAM_FLOW*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_STEAM_FLOW*BOILER_E_STATUS)/1000 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
TOTAL_STEAM_ENERGY | TOTAL STEAM ENERGY | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_TOTAL_STEAM_ENERGY+BOILER_B_TOTAL_STEAM_ENERGY+BOILER_C_TOTAL_STEAM_ENERGY+BOILER_D_TOTAL_STEAM_ENERGY+BOILER_E_TOTAL_STEAM_ENERGY | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY | BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_TOTAL_STEAM_ENERGY
BOILER_OVERALL_EFFICIENCY | BOILER OVERALL EFFICIENCY | % | LBM_preprocessing_inferred_tags_main | (BOILER_A_TOTAL_STEAM_ENERGY*BOILER_A_BOILER_INDIRECT_EFFICIENCY*BOILER_A_STATUS+BOILER_B_TOTAL_STEAM_ENERGY*BOILER_B_BOILER_INDIRECT_EFFICIENCY*BOILER_B_STATUS+BOILER_C_TOTAL_STEAM_ENERGY*BOILER_C_BOILER_INDIRECT_EFFICIENCY*BOILER_C_STATUS+BOILER_D_TOTAL_STEAM_ENERGY*BOILER_D_BOILER_INDIRECT_EFFICIENCY*BOILER_D_STATUS+BOILER_E_TOTAL_STEAM_ENERGY*B | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_B_STATUS (+5 more) | BOILER_A_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_A_STATUS ¦ BOILER_A_TOTAL_STEAM_ENERGY ¦ BOILER_B_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_B_STATUS ¦ BOILER_B_TOTAL_STEAM_ENERGY ¦ BOILER_C_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_C_STATUS ¦ BOILER_C_TOTAL_STEAM_ENERGY ¦ BOILER_D_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_D_STATUS ¦ BOILER_D_TOTAL_STEAM_ENERGY ¦ BOILER_E_BOILER_INDIRECT_EFFICIENCY ¦ BOILER_E_TOTAL_STEAM_ENERGY ¦ TOTAL_STEAM_ENERGY
TOTAL_FUEL_CONSUMPTION_GCAL_H | TOTAL FUEL CONSUMPTION GCAL H | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT+BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT | BOILER_A_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_B_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_C_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_D_CORRECTED_FUEL_GAS_ENERGY_INPUT ¦ BOILER_E_CORRECTED_FUEL_GAS_ENERGY_INPUT
TOTAL_STACK_LOSS_GCAL_H | TOTAL STACK LOSS GCAL/H | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_STACK_LOSS_CORRECTED+BOILER_B_STACK_LOSS_CORRECTED+BOILER_C_STACK_LOSS_CORRECTED+BOILER_D_STACK_LOSS_CORRECTED+BOILER_E_STACK_LOSS_CORRECTED | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_E_STACK_LOSS_CORRECTED | BOILER_A_STACK_LOSS_CORRECTED ¦ BOILER_B_STACK_LOSS_CORRECTED ¦ BOILER_C_STACK_LOSS_CORRECTED ¦ BOILER_D_STACK_LOSS_CORRECTED ¦ BOILER_E_STACK_LOSS_CORRECTED
TOTAL_BLOWDOWN_LOSS | TOTAL BLOWDOWN LOSS | Gcal/h | LBM_preprocessing_inferred_tags_main | BOILER_A_BLOWDOWN_LOSS+BOILER_B_BLOWDOWN_LOSS+BOILER_C_BLOWDOWN_LOSS+BOILER_D_BLOWDOWN_LOSS+BOILER_E_BLOWDOWN_LOSS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_BLOWDOWN_LOSS ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_E_BLOWDOWN_LOSS | BOILER_A_BLOWDOWN_LOSS ¦ BOILER_B_BLOWDOWN_LOSS ¦ BOILER_C_BLOWDOWN_LOSS ¦ BOILER_D_BLOWDOWN_LOSS ¦ BOILER_E_BLOWDOWN_LOSS
TOTAL_FUEL_FLOW | TOTAL FUEL FLOW | Ton/h | LBM_preprocessing_inferred_tags_main | (BOILER_A_FUEL_GAS_FLOW+BOILER_B_FUEL_GAS_FLOW+BOILER_C_FUEL_GAS_FLOW+BOILER_D_FUEL_GAS_FLOW+BOILER_E_FUEL_GAS_FLOW/1.295)/1000 | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV] | BOILER_B_FUEL_GAS_FLOW[sensor:UN.UO.71FC1204.PV]
OVERALL_SUPERHEATED_STEAM_BFW_RATIO | OVERALL SUPERHEATED STEAM BFW RATIO | [-] | LBM_preprocessing_inferred_tags_main | (BOILER_A_SUPERHEATED_STEAM_BFW_RATIO+BOILER_B_SUPERHEATED_STEAM_BFW_RATIO+BOILER_C_SUPERHEATED_STEAM_BFW_RATIO+BOILER_D_SUPERHEATED_STEAM_BFW_RATIO+BOILER_E_SUPERHEATED_STEAM_BFW_RATIO)/5 | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_B_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_C_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_D_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_E_SUPERHEATED_STEAM_BFW_RATIO | BOILER_A_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_B_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_C_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_D_SUPERHEATED_STEAM_BFW_RATIO ¦ BOILER_E_SUPERHEATED_STEAM_BFW_RATIO
TOTAL_FUEL_TO_AIR_RATIO | TOTAL FUEL TO AIR RATIO | Kg/ Kg Fuel | LBM_preprocessing_inferred_tags_main | BOILER_A_AIR_FUEL_MASS_RATIO+BOILER_B_AIR_FUEL_MASS_RATIO+BOILER_C_AIR_FUEL_MASS_RATIO+BOILER_D_AIR_FUEL_MASS_RATIO+BOILER_E_AIR_FUEL_MASS_RATIO | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_E_AIR_FUEL_MASS_RATIO | BOILER_A_AIR_FUEL_MASS_RATIO ¦ BOILER_B_AIR_FUEL_MASS_RATIO ¦ BOILER_C_AIR_FUEL_MASS_RATIO ¦ BOILER_D_AIR_FUEL_MASS_RATIO ¦ BOILER_E_AIR_FUEL_MASS_RATIO
TOTAL_CO2_EMISSIONS | TOTAL CO2 EMISSIONS | t/h | LBM_preprocessing_inferred_tags_main | BOILER_A_CO2_EMISSIONS+BOILER_B_CO2_EMISSIONS+BOILER_C_CO2_EMISSIONS+BOILER_D_CO2_EMISSIONS+BOILER_E_CO2_EMISSIONS | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_CO2_EMISSIONS ¦ BOILER_B_CO2_EMISSIONS ¦ BOILER_C_CO2_EMISSIONS ¦ BOILER_D_CO2_EMISSIONS ¦ BOILER_E_CO2_EMISSIONS | BOILER_A_CO2_EMISSIONS ¦ BOILER_B_CO2_EMISSIONS ¦ BOILER_C_CO2_EMISSIONS ¦ BOILER_D_CO2_EMISSIONS ¦ BOILER_E_CO2_EMISSIONS
BOILER_A_STEAM_TO_FIRE_DUTY_RATIO | BOILER A STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_A_STATUS==0,0,DESUPERHEATER_OUTLET_STEAM_FLOW/(BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS
BOILER_B_STEAM_TO_FIRE_DUTY_RATIO | BOILER B STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_B_STATUS==0,0,DESUPERHEATER_B_OUTLET_STEAM_FLOW/(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS
BOILER_C_STEAM_TO_FIRE_DUTY_RATIO | BOILER C STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_C_STATUS==0,0,DESUPERHEATER_C_OUTLET_STEAM_FLOW/(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS | BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS
BOILER_D_STEAM_TO_FIRE_DUTY_RATIO | BOILER D STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main | if(BOILER_D_STATUS==0,0,DESUPERHEATER_D_OUTLET_STEAM_FLOW/(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS | BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS
BOILER_E_STEAM_TO_FIRE_DUTY_RATIO | BOILER E STEAM TO FIRE DUTY RATIO | KG/ KCAL | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(BOILER_E_STATUS==0,0,DESUPERHEATER_E_OUTLET_STEAM_FLOW/(BOILER_E_FG_FLOW_RATE*BOILER_E_MIXED_LHV_PER_KG)*1000) | NOT COMPUTED |  | Unknown/no sensor: BOILER_E_MIXED_LHV_PER_KG | BOILER_E_MIXED_LHV_PER_KG
EXCESS_O2 | EXCESS O2 | % | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FLUE_GAS_OXGYGEN*BOILER_A_STATUS)+(BOILER_B_FLUE_GAS_OXGYGEN*BOILER_B_STATUS)+(BOILER_C_FLUE_GAS_OXGYGEN*BOILER_C_STATUS)+(BOILER_D_FLUE_GAS_OXGYGEN*BOILER_D_STATUS)+(BOILER_E_FLUE_GAS_OXGYGEN_NEW*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV] ¦ BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV] ¦ BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV] ¦ BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV] ¦ BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1104.PV] ¦ BOILER_B_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1204.PV] ¦ BOILER_C_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1304.PV] ¦ BOILER_D_FLUE_GAS_OXGYGEN[sensor:UN.UO.71AC1404.PV] ¦ BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
STACK_TEMP | STACK TEMP | DEG C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_STACK_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_STACK_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_STACK_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_STACK_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_STACK_TEMPERATURE*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
STEAM_TEMP | STEAM TEMP | DEG C | LBM_preprocessing_inferred_tags_main | (DESUPERHEATER_OUTLET_TEMPERATURE*BOILER_A_STATUS+DESUPERHEATER_B_OUTLET_TEMPERATURE*BOILER_B_STATUS+DESUPERHEATER_C_OUTLET_TEMPERATURE*BOILER_C_STATUS+DESUPERHEATER_D_OUTLET_TEMPERATURE*BOILER_D_STATUS+DESUPERHEATER_E_OUTLET_TEMPERATURE*BOILER_E_STATUS)/BOILERS_ONLINE | NOT COMPUTED |  | Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
STEAM_PRESS | STEAM PRESS | BARG | LBM_preprocessing_inferred_tags_main | ((HP_STEAM_PRESSURE_FROM_DS*BOILER_A_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_B*BOILER_B_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_C*BOILER_C_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_D*BOILER_D_STATUS)+(HP_STEAM_PRESSURE_FROM_DS_E*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | PI exists but NOT in hierarchy: HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | HP_STEAM_PRESSURE_FROM_DS[sensor:UN.UO.71PI1113.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_B[sensor:UN.UO.71PI1213.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_C[sensor:UN.UO.71PI1313.PV] ¦ HP_STEAM_PRESSURE_FROM_DS_D[sensor:UN.UO.71PI1413.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
COMBUSTION_AIR_TEMP | COMBUSTION AIR TEMP | DEG C | LBM_preprocessing_inferred_tags_main | ((BOILER_A_COMBUSTION_AIR_TEMPERATURE*BOILER_A_STATUS)+(BOILER_B_COMBUSTION_AIR_TEMPERATURE*BOILER_B_STATUS)+(BOILER_C_COMBUSTION_AIR_TEMPERATURE*BOILER_C_STATUS)+(BOILER_D_COMBUSTION_AIR_TEMPERATURE*BOILER_D_STATUS)+(BOILER_E_COMBUSTION_AIR_TEMP*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] ¦ BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] ¦ BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] ¦ BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] ¦ BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1114B.PV] ¦ BOILER_B_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1214B.PV] ¦ BOILER_C_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1314B.PV] ¦ BOILER_D_COMBUSTION_AIR_TEMPERATURE[sensor:UN.UO.71TI1414B.PV] ¦ BOILER_E_COMBUSTION_AIR_TEMP[sensor:UN.UO.71TI1514.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
BLOWDOWN_CONDUCTIVITY | BLOWDOWN CONDUCTIVITY | US/ CM | LBM_preprocessing_inferred_tags_main | ((BOILER_A_CONDUCTIVITY*BOILER_A_STATUS)+(BOILER_B_CONDUCTIVITY*BOILER_B_STATUS)+(BOILER_C_CONDUCTIVITY*BOILER_C_STATUS)+(BOILER_D_CONDUCTIVITY*BOILER_D_STATUS)+(BOILER_E_CONDUCTIVITY*BOILER_E_STATUS))/BOILERS_ONLINE | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_A_CONDUCTIVITY[sensor:UN.UO.71AC1101.PV] ¦ BOILER_B_CONDUCTIVITY[sensor:UN.UO.71AC1201.PV] ¦ BOILER_C_CONDUCTIVITY[sensor:UN.UO.71AC1301.PV] ¦ BOILER_D_CONDUCTIVITY[sensor:UN.UO.71AC1401.PV] ¦ BOILER_E_CONDUCTIVITY[sensor:UN.UO.71AC1501A.PV]; Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_CONDUCTIVITY[sensor:UN.UO.71AC1101.PV] ¦ BOILER_B_CONDUCTIVITY[sensor:UN.UO.71AC1201.PV] ¦ BOILER_C_CONDUCTIVITY[sensor:UN.UO.71AC1301.PV] ¦ BOILER_D_CONDUCTIVITY[sensor:UN.UO.71AC1401.PV] ¦ BOILER_E_CONDUCTIVITY[sensor:UN.UO.71AC1501A.PV] ¦ BOILERS_ONLINE ¦ BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
SPECIFIC_ENERGY_AVG | SPECIFIC ENERGY AVG | KG/ KCAL | LBM_preprocessing_inferred_tags_main | (BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_A_STATUS+BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_B_STATUS+BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_C_STATUS+BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_D_STATUS+BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ*BOILER_E_STATUS)/BOILERS_ONLINE | NOT COMPUTED |  | Unknown/no sensor: BOILERS_ONLINE ¦ BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS | BOILERS_ONLINE ¦ BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_A_STATUS ¦ BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_B_STATUS ¦ BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_C_STATUS ¦ BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ ¦ BOILER_D_STATUS ¦ BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ
FIRE_DUTY | FIRE DUTY | MMBTU/ DAY | LBM_preprocessing_inferred_tags_main | ((BOILER_A_FG_FLOW_RATE*BOILER_A_MIXED_LHV_PER_KG*1000)*BOILER_A_STATUS+(BOILER_B_FG_FLOW_RATE*BOILER_B_MIXED_LHV_PER_KG*1000)*BOILER_B_STATUS+(BOILER_C_FG_FLOW_RATE*BOILER_C_MIXED_LHV_PER_KG*1000)*BOILER_C_STATUS+(BOILER_D_FG_FLOW_RATE*BOILER_D_MIXED_LHV_PER_KG*1000)*BOILER_D_STATUS+(BOILER_E_FG_FLOW_RATE*BOILER_E_MIXED_LHV_PER_KG*1000)*BOILER_E_S | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS ¦ BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS | BOILER_A_MIXED_LHV_PER_KG ¦ BOILER_A_STATUS ¦ BOILER_B_FG_FLOW_RATE ¦ BOILER_B_MIXED_LHV_PER_KG ¦ BOILER_B_STATUS ¦ BOILER_C_MIXED_LHV_PER_KG ¦ BOILER_C_STATUS ¦ BOILER_D_MIXED_LHV_PER_KG ¦ BOILER_D_STATUS ¦ BOILER_E_MIXED_LHV_PER_KG
VAPOUR_PRESSURE_OF_WATER | VAPOUR PRESSURE OF WATER | mmhg | LBM_preprocessing_inferred_tags_main | 10^(8.07131-(1730.63/(233.426+(AMBIENT_TEMPERATURE)))) | COMPUTED | 4.631
OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA | OVER ALL SPECIFIC ENERGY CONSUMPTION DELTA | nan | TRG_compute_inferred_pre_pta | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark<0,0,(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark)) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
ENERGY_NUMBER | ENERGY NUMBER | MMBTU/ HR | TRG_compute_inferred_pre_pta | ((BOILER_A_FG_FLOW_RATE_actual*BOILER_A_MIXED_LHV_PER_KG_actual*1000)*BOILER_A_STATUS_actual+(BOILER_B_FG_FLOW_RATE_actual*BOILER_B_MIXED_LHV_PER_KG_actual*1000)*BOILER_B_STATUS_actual+(BOILER_C_FG_FLOW_RATE_actual*BOILER_C_MIXED_LHV_PER_KG_actual*1000)*BOILER_C_STATUS_actual+(BOILER_D_FG_FLOW_RATE_actual*BOILER_D_MIXED_LHV_PER_KG_actual*1000)*BOIL | NOT COMPUTED |  | eval_error: name 'BOILER_A_FG_FLOW_RATE_actual' is not defined
ENVIRONMENT_NUMBER | ENVIRONMENT NUMBER | MT/ HR | TRG_compute_inferred_pre_pta | ([ENERGY_NUMBER_actual]/0.0468/1000)*2.75 | NOT COMPUTED |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
opportunity_production | OPPORTUNITY PRODUCTION | MT/ DAY | TRG_compute_inferred_pre_pta | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual])*24/([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark])*0 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
EQUIVALENT_FUEL | EQUIVALENT FUEL | MT/ HR | TRG_compute_inferred_pre_pta | [OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*[TOTAL_STEAM_PRODUCTION_actual]/0.0468/1000 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
opportunity_environment | OPPORTUNITY ENVIRONMENT | MT/ DAY | TRG_compute_inferred_pre_pta | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[EQUIVALENT_FUEL_actual]*2.75*24) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
opportunity_energy | OPPORTUNITY ENERGY | MMBTU/ DAY | TRG_compute_inferred_pre_pta | if(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state==0,0,[OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_state' is not defined
index_process | INDEX PROCESS | % | TRG_compute_inferred_pre_pta | (TOTAL_STEAM_PRODUCTION_actual/(TOTAL_STEAM_PRODUCTION_actual+opportunity_production_actual/24))*100*0+100 | NOT COMPUTED |  | eval_error: name 'TOTAL_STEAM_PRODUCTION_actual' is not defined
index_energy | INDEX ENERGY | % | TRG_compute_inferred_pre_pta | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 | NOT COMPUTED |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
index_environment | INDEX ENVIRONMENT | % | TRG_compute_inferred_pre_pta | ((([ENERGY_NUMBER_actual])-[opportunity_energy_actual]/24)/([ENERGY_NUMBER_actual]))*100 | NOT COMPUTED |  | eval_error: name 'ENERGY_NUMBER_actual' is not defined
BOILER_A_ACTUAL_SP_ENERGY_DELTA | BOILER A ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_A_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_B_ACTUAL_SP_ENERGY_DELTA | BOILER B ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_B_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_C_ACTUAL_SP_ENERGY_DELTA | BOILER C ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_C_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_D_ACTUAL_SP_ENERGY_DELTA | BOILER D ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_D_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_E_ACTUAL_SP_ENERGY_DELTA | BOILER E ACTUAL SP ENERGY DELTA | GJ/ T | TRG_compute_inferred_pre_pta | if((BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)<0,0,(BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual-BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_benchmark)) | NOT COMPUTED |  | eval_error: name 'BOILER_E_SPECIFIC_ENERGY_CONSUMPTION_IN_GJ_actual' is not defined
BOILER_A_FUEL_GAIN_LOSS | BOILER A FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_A_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_B_FUEL_GAIN_LOSS | BOILER B FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_B_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_B_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_C_FUEL_GAIN_LOSS | BOILER C FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_C_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_C_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_D_FUEL_GAIN_LOSS | BOILER D FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_D_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_D_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
BOILER_E_FUEL_GAIN_LOSS | BOILER E FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | ([BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual]*[DESUPERHEATER_E_OUTLET_STEAM_FLOW_actual])/0.0468/10^6*24 | NOT COMPUTED |  | eval_error: name 'BOILER_E_ACTUAL_SP_ENERGY_DELTA_actual' is not defined
TOTAL_FUEL_GAIN_LOSS | TOTAL FUEL GAIN LOSS | MT/ DAY | TRG_compute_inferred_pre_pta | BOILER_A_FUEL_GAIN_LOSS_actual+BOILER_B_FUEL_GAIN_LOSS_actual+BOILER_C_FUEL_GAIN_LOSS_actual+BOILER_D_FUEL_GAIN_LOSS_actual+BOILER_E_FUEL_GAIN_LOSS_actual | NOT COMPUTED |  | eval_error: name 'BOILER_A_FUEL_GAIN_LOSS_actual' is not defined
FLAG_QUALITY_RATE | FLAG QUALITY RATE | % | LBM_preprocessing_inferred_tags_main | if(([STEAM_TEMP]>390&&[STEAM_PRESS]>40),1,0) | NOT COMPUTED |  | Unknown/no sensor: STEAM_PRESS ¦ STEAM_TEMP | STEAM_PRESS ¦ STEAM_TEMP
FLAG_QUALITY_RATE_PTA | FLAG QUALITY RATE PTA | % | TRG_compute_pta |  | NOT COMPUTED |  | No formula defined and no PI value
QUALITY_RATE | QUALITY RATE | % | TRG_compute_inferred_post_pta | FLAG_QUALITY_RATE_PTA_actual*100/24 | NOT COMPUTED |  | eval_error: name 'FLAG_QUALITY_RATE_PTA_actual' is not defined
Calc_capacity | CALC CAPACITY | MT/ HR | LBM_preprocessing_inferred_tags_main,LBM_postprocessing_capacity_utilization_inferred,LBM_optimum_inferred_tags_main | (DESUPERHEATER_OUTLET_STEAM_FLOW+DESUPERHEATER_B_OUTLET_STEAM_FLOW+DESUPERHEATER_C_OUTLET_STEAM_FLOW+DESUPERHEATER_D_OUTLET_STEAM_FLOW+DESUPERHEATER_E_OUTLET_STEAM_FLOW) | COMPUTED | 13739.292
Capacity_Utilization | CAPACITY UTILIZATION | % | LBM_ |  | NOT COMPUTED |  | No formula defined and no PI value
CAPACITY_UTILIZATION_1 | CAPACITY UTILIZATION 1 | % | LBM_preprocessing_inferred_tags_main | [TOTAL_STEAM_PRODUCTION]/750000*100 | NOT COMPUTED |  | Unknown/no sensor: TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
OVERALL_ENERGY_CONSUMPTION_DAY | OVERALL ENERGY CONSUMPTION DAY | GJ/ DAY | TRG_compute_inferred_pre_pta | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_benchmark | OVERALL ENERGY CONSUMPTION DAY BENCHMARK | GJ/ DAY | TRG_compute_inferred_pre_pta | OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24 | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark' is not defined
OVERALL_ENERGY_CONSUMPTION_DAY_DELTA | OVERALL ENERGY CONSUMPTION DAY DELTA | GJ/ DAY | TRG_compute_inferred_pre_pta | abs(OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual*24-OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_benchmark*24)*TOTAL_STEAM_PRODUCTION_MT_DAY_actual | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_actual' is not defined
EQUIVALENT_FUEL_DAY | EQUIVALENT FUEL DAY | MT/ DAY | TRG_compute_inferred_pre_pta | [EQUIVALENT_FUEL_actual]*24 | NOT COMPUTED |  | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
TOTAL_ENERGY_GAP | TOTAL ENERGY GAP | MT/ DAY | TRG_compute_inferred_pre_pta | ([OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual]*0.947*[TOTAL_STEAM_PRODUCTION_actual]*24) | NOT COMPUTED |  | eval_error: name 'OVER_ALL_SPECIFIC_ENERGY_CONSUMPTION_DELTA_actual' is not defined
TOTAL_CO2_GAP | TOTAL CO2 GAP | MMBTU/ DAY | TRG_compute_inferred_pre_pta | [EQUIVALENT_FUEL_actual]*2.75*24 | NOT COMPUTED |  | eval_error: name 'EQUIVALENT_FUEL_actual' is not defined
Boiler_E_Nox_Emission | Boiler E Nox Emission | ng/J | LBM_preprocessing_inferred_tags_main,362_DM_data_ingestion_inferred_tags | if(BOILER_E_STATUS==0,0,BOILER_E_NOX*46/24.45*1000000*2.07/10000000*20.9/(20.9-BOILER_E_FLUE_GAS_OXGYGEN_NEW)) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILER_E_NOX[sensor:UN.UO.71AI1505A1.PV] | BOILER_E_FLUE_GAS_OXGYGEN_NEW[sensor:UN.UO.71AC1504AA.PV] ¦ BOILER_E_NOX[sensor:UN.UO.71AI1505A1.PV]
Boiler_E_Nox_Emission_Forecast | Boiler E Nox Emission Forecast | ng/J | 362_DM_ |  | NOT COMPUTED |  | No formula defined and no PI value
Boiler_E_Nox_Emission_Max_Forecast | Boiler E Nox Emission Max Forecast | ng/J | 362_DM_ |  | NOT COMPUTED |  | No formula defined and no PI value
Boiler_E_Nox_Emission_Timestamp_Max_Forecast | Boiler E Nox Emission Timestamp Max Forecast | nan | 362_DM_ |  | NOT COMPUTED |  | No formula defined and no PI value
TOTAL_STEAM_PRODUCTION_MT_DAY | TOTAL STEAM PRODUCTION IN MT PER DAY | MT/ DAY | LBM_preprocessing_inferred_tags_main | [TOTAL_STEAM_PRODUCTION]*24 | NOT COMPUTED |  | Unknown/no sensor: TOTAL_STEAM_PRODUCTION | TOTAL_STEAM_PRODUCTION
Boiler_E_Nox_Emission_Actual_Value | Boiler E Nox Emission Actual Value | nan | 362_DM_ |  | NOT COMPUTED |  | No formula defined and no PI value
STEAM_MARGIN_TPH | Steam margin available in running boilers in TPH | TPH | LBM_preprocessing_inferred_tags_main | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS])*150-[TOTAL_STEAM_PRODUCTION] | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS ¦ TOTAL_STEAM_PRODUCTION | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS ¦ TOTAL_STEAM_PRODUCTION
STEAM_MARGIN_NUMBER | Available steam margin divided by 150 | nan | LBM_preprocessing_inferred_tags_main | [STEAM_MARGIN_TPH]/150 | NOT COMPUTED |  | Unknown/no sensor: STEAM_MARGIN_TPH | STEAM_MARGIN_TPH
NUMBER_OF_BOILERS_ONLINE | Number of boilers running | nan | LBM_preprocessing_inferred_tags_main | ([BOILER_A_STATUS]+[BOILER_B_STATUS]+[BOILER_C_STATUS]+[BOILER_D_STATUS]+[BOILER_E_STATUS]) | NOT COMPUTED |  | Unknown/no sensor: BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS | BOILER_A_STATUS ¦ BOILER_B_STATUS ¦ BOILER_C_STATUS ¦ BOILER_D_STATUS
NUMBER_OF_BOILERS_OPTIMUM | Optimum number of boilers that can be run considering steam margin. | nan | LBM_preprocessing_inferred_tags_main | if([STEAM_MARGIN_NUMBER]>2.0,([NUMBER_OF_BOILERS_ONLINE]-1),[NUMBER_OF_BOILERS_ONLINE]) | NOT COMPUTED |  | Unknown/no sensor: NUMBER_OF_BOILERS_ONLINE ¦ STEAM_MARGIN_NUMBER | NUMBER_OF_BOILERS_ONLINE ¦ STEAM_MARGIN_NUMBER
FLAG_BFW_QUALITY | FLAG BFW QUALITY | % | LBM_preprocessing_inferred_tags_main | if([BFW_OXYGEN]>7ll[BFW_SILICA]>20ll[BFW_SODIUM]>20[BFW_PH]>9.6ll[BFW_PH]<9.2ll[BFW_CONDUCTIVITY]>10,0,1) | NOT COMPUTED |  | PI exists but NOT in hierarchy: BFW_CONDUCTIVITY[sensor:UN.UO.71AI1005B.PV] ¦ BFW_OXYGEN[sensor:UN.UO.71AI1001.PV] ¦ BFW_PH[sensor:UN.UO.71AI1005A.PV] ¦ BFW_SILICA[sensor:UN.UO.71AI1002.PV] ¦ BFW_SODIUM[sensor:UN.UO.71AI1004.PV] | BFW_CONDUCTIVITY[sensor:UN.UO.71AI1005B.PV] ¦ BFW_OXYGEN[sensor:UN.UO.71AI1001.PV] ¦ BFW_PH[sensor:UN.UO.71AI1005A.PV] ¦ BFW_SILICA[sensor:UN.UO.71AI1002.PV] ¦ BFW_SODIUM[sensor:UN.UO.71AI1004.PV]
FLAG_BFW_QUALITY_PTA | FLAG BFW QUALITY PTA | % | TRG_compute_pta |  | NOT COMPUTED |  | No formula defined and no PI value
BFW_QUALITY_RATE | BFW QUALITY RATE | % | TRG_compute_inferred_post_pta | FLAG_BFW_QUALITY_PTA_actual*100/24 | NOT COMPUTED |  | eval_error: name 'FLAG_BFW_QUALITY_PTA_actual' is not defined

## PI_Seeds_35
tag_name | sensor_id | value | description | uom
DESUPERHEATER_OUTLET_STEAM_FLOW | UN.UO.71FI1101.PV | 2696.23 | DESUPERHEATER OUTLET STEAM FLOW | KG/HR
DESUPERHEATER_OUTLET_TEMPERATURE | UN.UO.71TC1111.PV | 16.593 | DESUPERHEATER OUTLET TEMPERATURE | C
BOILER_A_FUEL_GAS_FLOW | UN.UO.71FC1104.PV | 175.484 | BOILER A FUEL GAS FLOW | KG/HR
BOILER_A_STACK_TEMPERATURE | UN.UO.71TI1107.PV | 5.907 | BOILER A STACK TEMPERATURE | C
AMBIENT_TEMPERATURE | UN.UO.86XI6024.PV | 0.265 | AMBIENT TEMPERATURE | DEGC
RELATIVE_HUMIDITY | UN.UO.86XI6025.PV | -0.17 | RELATIVE HUMIDITY | %
DESUPERHEATER_B_OUTLET_STEAM_FLOW | UN.UO.71FI1201.PV | 2760.21 | DESUPERHEATER B OUTLET STEAM FLOW | KG/HR
DESUPERHEATER_B_OUTLET_TEMPERATURE | UN.UO.71TC1211.PV | 16.304 | DESUPERHEATER B OUTLET TEMPERATURE | C
BOILER_B_STACK_TEMPERATURE | UN.UO.71TI1207.PV | 5.891 | BOILER B STACK TEMPERATURE | C
DESUPERHEATER_C_OUTLET_STEAM_FLOW | UN.UO.71FI1301.PV | 2699.001 | DESUPERHEATER C OUTLET STEAM FLOW | KG/HR
DESUPERHEATER_C_OUTLET_TEMPERATURE | UN.UO.71TC1311.PV | 16.618 | DESUPERHEATER C OUTLET TEMPERATURE | C
BOILER_C_FUEL_GAS_FLOW | UN.UO.71FC1304.PV | 175.495 | BOILER C FUEL GAS FLOW | KG/HR
BOILER_C_STACK_TEMPERATURE | UN.UO.71TI1307.PV | 5.934 | BOILER C STACK TEMPERATURE | C
DESUPERHEATER_D_OUTLET_STEAM_FLOW | UN.UO.71FI1401.PV | 2780.088 | DESUPERHEATER D OUTLET STEAM FLOW | KG/HR
DESUPERHEATER_D_OUTLET_TEMPERATURE | UN.UO.71TC1411.PV | 16.38 | DESUPERHEATER D OUTLET TEMPERATURE | C
BOILER_D_FUEL_GAS_FLOW | UN.UO.71FC1404.PV | 175.493 | BOILER D FUEL GAS FLOW | KG/HR
BOILER_D_STACK_TEMPERATURE | UN.UO.71TI1407.PV | 5.755 | BOILER D STACK TEMPERATURE | C
DESUPERHEATER_E_OUTLET_STEAM_FLOW | UN.UO.71FI1501A.PV | 2803.763 | DESUPERHEATER E OUTLET STEAM FLOW | KG/HR
DESUPERHEATER_E_OUTLET_TEMPERATURE | UN.UO.71TC1511.PV | 16.573 | DESUPERHEATER E OUTLET TEMPERATURE | C
HP_STEAM_PRESSURE_FROM_DS_E | UN.UO.71PC1513.PV | 1.884 | HP STEAM PRESSURE FROM DS E | BARG
BOILER_E_FUEL_GAS_FLOW | UN.UO.71FC1504.PV | 233.005 | BOILER E FUEL GAS FLOW | KG/HR
BOILER_E_STACK_TEMPERATURE | UN.UO.71TI1507.PV | 6.509 | BOILER E STACK TEMPERATURE | C
BOILER_FG_N2_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51219.PV | 0.289 | BOILER FG N2 CONCENTRATION ARRAZI | %
BOILER_FG_CH4_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51211.PV | 3.788 | BOILER FG CH4 CONCENTRATION ARRAZI | %
BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51212.PV | 0.062 | BOILER FG ETHANE CONCENTRATION ARRAZI | %
BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51213.PV | 0.011 | BOILER FG PROPANE CONCENTRATION ARRAZI | %
BOILER_FG_NC4_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51214.PV | 0.003 | BOILER FG NC4 CONCENTRATION ARRAZI | %
BOILER_FG_IC4_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51215.PV | 0.002 | BOILER FG IC4 CONCENTRATION ARRAZI | %
BOILER_FG_CO2_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI51217.PV | 0.01 | BOILER FG CO2 CONCENTRATION ARRAZI | %
BOILER_FG_NC5_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI512110.PV | 0.001 | BOILER FG NC5 CONCENTRATION ARRAZI | %
BOILER_FG_IC5_CONCENTRATION_ARRAZI | AR.AR5.DCS.Process.AI512111.PV | 0.001 | BOILER FG IC5 CONCENTRATION ARRAZI | %
HP_STEAM_VENT_CONTROLLER_OPENING | UN.UO.70PC0012A.MV | 0 | HP STEAM VENT CONTROLLER OPENING | BARG
HP_STEAM_HDR_PRESSURE_A | UN.UO.70PI0012A.PV | 1.865 | HP STEAM HDR PRESSURE A | BARG
CONDENSATE_TO_DEARATOR_A | UN.UO.71FI1096.PV | 19050.913 | CONDENSATE TO DEARATOR A
CONDENSATE_FLOW_TO_DEAERTOR_B | UN.UO.71FI1097.PV | 14918.798 | FEED WATER FLOW TO DEAERTOR B | KG/HR