## Mapping
Element Path | Element Type | Attribute Name | UOM | PI Sensor | Logical Column (tag.csv) | Master PI Column | Value | Match Type
United | System | Ambient Temperature | degC | UN.UO.86XI6024.PV | Ambient_Temperature_1 | Ambient_Temperature_1 | 6.6314 | DIRECT
United | System | Ambient Pressure | bar | UN.UO.86XI6025.PV | Relative_Humidity | Relative_Humidity | -4.2572 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Steam Header (100-110 KG/CM2A)A-steam header a | UB VHP Steam Header (100-110 KG/CM2A) | Header Pressure | KG/CM2A | UN.ETH.17PC7032.PV | VHP_Steam_Pressure | VHP_Steam_Pressure | 103.9342 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Steam Header (100-110 KG/CM2A)A-steam header a | UB VHP Steam Header (100-110 KG/CM2A) | Header Temperature | degC | UN.ETH.12TI2107.PV | VHP_Steam_Temperature | VHP_Steam_Temperature | 499.2784 | DIRECT
Steam Distribution (Headers/PRDS)A > UB HP-2 Steam Header (40-45 KG/CM2A)A-steam header a | UB HP-2 Steam Header (40-45 KG/CM2A) | Header Pressure | KG/CM2A | UN.UO.71PC1113.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Distribution (Headers/PRDS)A > UB HP-2 Steam Header (40-45 KG/CM2A)A-steam header a | UB HP-2 Steam Header (40-45 KG/CM2A) | Header Temperature | degC | UN.UO.71TC1111.PV | Boiler_A_DSP_outlet_Temp | Boiler_A_DSP_outlet_Temp | 398.2 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Steam Header (20-25 KG/CM2A)A-steam header a | UB MP-2 Steam Header (20-25 KG/CM2A) | Header Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Steam Header (20-25 KG/CM2A)A-steam header a | UB MP-2 Steam Header (20-25 KG/CM2A) | Header Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam Distribution (Headers/PRDS)A > UB LP-1 Steam Header (5-7 KG/CM2A)A-steam header a | UB LP-1 Steam Header (5-7 KG/CM2A) | Header Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Distribution (Headers/PRDS)A > UB LP-1 Steam Header (5-7 KG/CM2A)A-steam header a | UB LP-1 Steam Header (5-7 KG/CM2A) | Header Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Steam Output | metric_ton/h | UN.UO.71FI1101.PV | BLR_1_HPS_Gen_raw | BLR_1_HPS_Gen_raw | 60756.0312 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Steam Pressure | bar | UN.UO.71PC1113.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Steam Temperature | degC | UN.UO.71TC1111.PV | Boiler_A_DSP_outlet_Temp | Boiler_A_DSP_outlet_Temp | 398.2 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Flue Gas O2 | mol% | UN.UO.71AC1104.PV | BOILER_A_FLUE_GAS_OXGYGEN | BOILER_A_FLUE_GAS_OXGYGEN | 3.6288 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas C1 | mol% | AR.AR5.DCS.Process.AI51211.PV | BOILER_FG_CH4_CONCENTRATION_ARRAZI | BOILER_FG_CH4_CONCENTRATION_ARRAZI | 90.9146 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas C2 | mol% | AR.AR5.DCS.Process.AI51212.PV | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | 1.4986 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas C3 | mol% | AR.AR5.DCS.Process.AI51213.PV | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | 0.2733 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas CO2 | mol% | AR.AR5.DCS.Process.AI51217.PV | BOILER_FG_CO2_CONCENTRATION_ARRAZI | BOILER_FG_CO2_CONCENTRATION_ARRAZI | 0.2467 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas Flow | metric_ton/h | UN.UO.71FC1104.PV | Boielr_A_Fuel_Gas_Flow | Boielr_A_Fuel_Gas_Flow | 4549.573 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas iC4 | mol% | AR.AR5.DCS.Process.AI51215.PV | BOILER_FG_IC4_CONCENTRATION_ARRAZI | BOILER_FG_IC4_CONCENTRATION_ARRAZI | 0.0386 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas iC5 | mol% | AR.AR5.DCS.Process.AI512111.PV | BOILER_FG_IC5_CONCENTRATION_ARRAZI | BOILER_FG_IC5_CONCENTRATION_ARRAZI | 0.0179 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas N2 | mol% | AR.AR5.DCS.Process.AI51219.PV | BOILER_FG_N2_CONCENTRATION_ARRAZI | BOILER_FG_N2_CONCENTRATION_ARRAZI | 6.933 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas nC4 | mol% | AR.AR5.DCS.Process.AI51214.PV | BOILER_FG_NC4_CONCENTRATION_ARRAZI | BOILER_FG_NC4_CONCENTRATION_ARRAZI | 0.0644 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Fuel Gas nC5 | mol% | AR.AR5.DCS.Process.AI512110.PV | BOILER_FG_NC5_CONCENTRATION_ARRAZI | BOILER_FG_NC5_CONCENTRATION_ARRAZI | 0.013 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerA-fuel fired boiler a | UB HP-2 Fuel Fired Boiler | Excess O2 | percent | UN.UO.71AC1104.PV | BOILER_A_FLUE_GAS_OXGYGEN | BOILER_A_FLUE_GAS_OXGYGEN | 3.6288 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler Air PreheaterA | UB HP-2 Fuel Fired Boiler Air Preheater | Air Inlet Temperature | degC | UN.UO.71TI1114B.PV | Boiler_A_Combustion_Air_Temperature | Boiler_A_Combustion_Air_Temperature | 27.7676 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Pressure | bar | UN.UO.71PI1021A.PV | BFW_Pressure | BFW_Pressure | 79.3 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Temperature | degC | UN.UO.71TI1079.PV | BFW_Temperature | BFW_Temperature | 109.9 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Inlet Flow | metric_ton/h | UN.UO.71FC1103.PV | BFW_TO_BOILER_A | BFW_TO_BOILER_A | 63951.5 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Quality (Conductivity) | uS/cm | UN.UO.71AI1005B.PV | BFW_Conductivity | BFW_Conductivity | 4.1147 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Bearing Temperature | degC | UN.UO.71TI1016A.PV | BFW_A_Bearing_temp | BFW_A_Bearing_temp | 34.9864 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Discharge Pressure | bar | UN.UO.71PI1021A.PV | BFW_Pressure | BFW_Pressure | 79.3 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Motor Current | A | UN.UO.71II1001.PV | BFW_A_AMPS | BFW_A_AMPS | -0.3919 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Vibration | mm/s | UN.UO.71VI1002A.PV | BFW_A_Vibrations | BFW_A_Vibrations | 0.5934 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Blowdown Conductivity | uS/cm | UN.UO.71AC1101.PV | BOILER_A_CONDUCTIVITY | BOILER_A_CONDUCTIVITY | 50.8059 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Continuous Blowdown Flow | metric_ton/h | UN.UO.71FC1100.PV | BOILER_A_CBD | BOILER_A_CBD | 901.4901 | DIRECT
UB HP-2 Fuel Fired Boiler Combustion SystemA > UB HP-2 Fuel Fired Boiler BurnerA | UB HP-2 Fuel Fired Boiler Burner | Burner Backpressure | bar | UN.UO.71PI1122A.PV |  |  |  | TAG_MISSING
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Inlet Steam Temperature | degC | UN.UO.71TI1106.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Outlet Steam Temperature | degC | UN.UO.71TC1111.PV | Boiler_A_DSP_outlet_Temp | Boiler_A_DSP_outlet_Temp | 398.2 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Spray Water Flow | metric_ton/h | UN.UO.71FI1102.PV | DSP_BFW_TO_BOILER_A | DSP_BFW_TO_BOILER_A | 988.6 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Inlet Temperature | degC | UN.UO.71TI1110.PV | BFW_temp_A | BFW_temp_A | 109.8918 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Outlet Temperature | degC | UN.UO.71TI1102.PV | BLR_A_Eco_BFW_Out_Temp | Process_flow_of_E_1102_1 | 142.1 | SEMANTIC
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | O2 in Flue Gas | vol% | UN.UO.71AC1104.PV | BOILER_A_FLUE_GAS_OXGYGEN | BOILER_A_FLUE_GAS_OXGYGEN | 3.6288 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | Stack Temperature | degC | UN.UO.71TI1107.PV | BOILER_A_STACK_TEMPERATURE | BOILER_A_STACK_TEMPERATURE | 140.1031 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Level | percent | UN.UO.71LC1102A.PV |  | Process_flow_of_E_1102_1 | 142.1 | SEMANTIC
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Pressure | bar | UN.UO.71PC1103.PV |  | Eth_HP_to_E_1103_flow_Energy | 18.8424 | SEMANTIC
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Attemperator Spray Flow | metric_ton/h | UN.UO.71FI1101.PV | BLR_1_HPS_Gen_raw | BLR_1_HPS_Gen_raw | 60756.0312 | DIRECT
UB HP-2 Fuel Fired BoilerA-fuel fired boiler a > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Steam Inlet Temperature | degC | UN.UO.71TI1119.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Steam Output | metric_ton/h | UN.UO.71FI1201.PV | BLR_2_HPS_Gen_raw | BLR_2_HPS_Gen_raw | 62755.2422 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Steam Pressure | bar | UN.UO.71PC1213.PV |  | Boiler_1_Fuel_Cost | 338.5 | SEMANTIC
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Steam Temperature | degC | UN.UO.71TC1211.PV | Boiler_B_DSP_outlet_Temp | Boiler_B_DSP_outlet_Temp | 390.6 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Flue Gas O2 | mol% | UN.UO.71AC1204.PV | BOILER_B_FLUE_GAS_OXGYGEN | BOILER_B_FLUE_GAS_OXGYGEN | 3.6674 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas C1 | mol% | AR.AR5.DCS.Process.AI51211.PV | BOILER_FG_CH4_CONCENTRATION_ARRAZI | BOILER_FG_CH4_CONCENTRATION_ARRAZI | 90.9146 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas C2 | mol% | AR.AR5.DCS.Process.AI51212.PV | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | 1.4986 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas C3 | mol% | AR.AR5.DCS.Process.AI51213.PV | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | 0.2733 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas CO2 | mol% | AR.AR5.DCS.Process.AI51217.PV | BOILER_FG_CO2_CONCENTRATION_ARRAZI | BOILER_FG_CO2_CONCENTRATION_ARRAZI | 0.2467 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas Flow | metric_ton/h | UN.UO.71FC1204.PV | Boielr_B_Fuel_Gas_Flow | Boielr_B_Fuel_Gas_Flow | 4549.675 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas iC4 | mol% | AR.AR5.DCS.Process.AI51215.PV | BOILER_FG_IC4_CONCENTRATION_ARRAZI | BOILER_FG_IC4_CONCENTRATION_ARRAZI | 0.0386 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas iC5 | mol% | AR.AR5.DCS.Process.AI512111.PV | BOILER_FG_IC5_CONCENTRATION_ARRAZI | BOILER_FG_IC5_CONCENTRATION_ARRAZI | 0.0179 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas N2 | mol% | AR.AR5.DCS.Process.AI51219.PV | BOILER_FG_N2_CONCENTRATION_ARRAZI | BOILER_FG_N2_CONCENTRATION_ARRAZI | 6.933 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas nC4 | mol% | AR.AR5.DCS.Process.AI51214.PV | BOILER_FG_NC4_CONCENTRATION_ARRAZI | BOILER_FG_NC4_CONCENTRATION_ARRAZI | 0.0644 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Fuel Gas nC5 | mol% | AR.AR5.DCS.Process.AI512110.PV | BOILER_FG_NC5_CONCENTRATION_ARRAZI | BOILER_FG_NC5_CONCENTRATION_ARRAZI | 0.013 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerB-fuel fired boiler b | UB HP-2 Fuel Fired Boiler | Excess O2 | percent | UN.UO.71AC1204.PV | BOILER_B_FLUE_GAS_OXGYGEN | BOILER_B_FLUE_GAS_OXGYGEN | 3.6674 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler Air PreheaterA | UB HP-2 Fuel Fired Boiler Air Preheater | Air Inlet Temperature | degC | UN.UO.71TI1214B.PV | Boiler_B_Combustion_Air_Temperature | Boiler_B_Combustion_Air_Temperature | 28.41 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Pressure | bar | UN.UO.71PI1021A.PV | BFW_Pressure | BFW_Pressure | 79.3 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Temperature | degC | UN.UO.71TI1079.PV | BFW_Temperature | BFW_Temperature | 109.9 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Inlet Flow | metric_ton/h | UN.UO.71FC1203.PV | BFW_TO_BOILER_B | BFW_TO_BOILER_B | 65566.1 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Quality (Conductivity) | uS/cm | UN.UO.71AI1005B.PV | BFW_Conductivity | BFW_Conductivity | 4.1147 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Bearing Temperature | degC | UN.UO.71TI1020A.PV | BFW_D_Bearing_temp | BFW_D_Bearing_temp | 37.9519 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Discharge Pressure | bar | UN.UO.71PI1021A.PV | BFW_Pressure | BFW_Pressure | 79.3 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Motor Current | A | UN.UO.71II1002.PV | BFW_D_AMPS | BFW_D_AMPS | -0.5679 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Vibration | mm/s | UN.UO.71VI1006A.PV | BFW_D_Vibrations | BFW_D_Vibrations | 0.7947 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Blowdown Conductivity | uS/cm | UN.UO.71AC1201.PV | BOILER_B_CONDUCTIVITY | BOILER_B_CONDUCTIVITY | 20.4163 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Continuous Blowdown Flow | metric_ton/h | UN.UO.71FC1200.PV | BOILER_B_CBD | BOILER_B_CBD | 902.3948 | DIRECT
UB HP-2 Fuel Fired Boiler Combustion SystemA > UB HP-2 Fuel Fired Boiler BurnerA | UB HP-2 Fuel Fired Boiler Burner | Burner Backpressure | bar | UN.UO.71PI1222A.PV |  |  |  | TAG_MISSING
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Inlet Steam Temperature | degC | UN.UO.71TI1206.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Outlet Steam Temperature | degC | UN.UO.71TC1211.PV | Boiler_B_DSP_outlet_Temp | Boiler_B_DSP_outlet_Temp | 390.6 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Spray Water Flow | metric_ton/h | UN.UO.71FI1202.PV | DSP_BFW_TO_BOILER_B | DSP_BFW_TO_BOILER_B | 1175.8 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Inlet Temperature | degC | UN.UO.71TI1210.PV | BFW_temp_A | BFW_temp_A | 109.8918 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Outlet Temperature | degC | UN.UO.71TI1202.PV | BLR_B_Eco_BFW_Out_Temp | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | O2 in Flue Gas | vol% | UN.UO.71AC1204.PV | BOILER_B_FLUE_GAS_OXGYGEN | BOILER_B_FLUE_GAS_OXGYGEN | 3.6674 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | Stack Temperature | degC | UN.UO.71TI1207.PV | BOILER_B_STACK_TEMPERATURE | BOILER_B_STACK_TEMPERATURE | 139.598 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Level | percent | UN.UO.71LC1202A.PV |  | EG1_BFW_to_Steam_drum_1 | 0.0572 | SEMANTIC
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Pressure | bar | UN.UO.71PC1203.PV |  | Fuel_gas_drum_pressure | 4.2 | SEMANTIC
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Attemperator Spray Flow | metric_ton/h | UN.UO.71FI1201.PV | BLR_2_HPS_Gen_raw | BLR_2_HPS_Gen_raw | 62755.2422 | DIRECT
UB HP-2 Fuel Fired BoilerB-fuel fired boiler b > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Steam Inlet Temperature | degC | UN.UO.71TI1219.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Steam Output | metric_ton/h | UN.UO.71FI1301.PV | BLR_3_HPS_Gen_raw | BLR_3_HPS_Gen_raw | 61148.6641 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Steam Pressure | bar | UN.UO.71PC1113.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Steam Temperature | degC | UN.UO.71TC1111.PV | Boiler_A_DSP_outlet_Temp | Boiler_A_DSP_outlet_Temp | 398.2 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Flue Gas O2 | mol% | UN.UO.71AC1304.PV | BOILER_C_FLUE_GAS_OXGYGEN | BOILER_C_FLUE_GAS_OXGYGEN | 3.4841 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas C1 | mol% | AR.AR5.DCS.Process.AI51211.PV | BOILER_FG_CH4_CONCENTRATION_ARRAZI | BOILER_FG_CH4_CONCENTRATION_ARRAZI | 90.9146 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas C2 | mol% | AR.AR5.DCS.Process.AI51212.PV | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | 1.4986 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas C3 | mol% | AR.AR5.DCS.Process.AI51213.PV | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | 0.2733 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas CO2 | mol% | AR.AR5.DCS.Process.AI51217.PV | BOILER_FG_CO2_CONCENTRATION_ARRAZI | BOILER_FG_CO2_CONCENTRATION_ARRAZI | 0.2467 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas Flow | metric_ton/h | UN.UO.71FC1304.PV | Boielr_C_Fuel_Gas_Flow | Boielr_C_Fuel_Gas_Flow | 4549.645 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas iC4 | mol% | AR.AR5.DCS.Process.AI51215.PV | BOILER_FG_IC4_CONCENTRATION_ARRAZI | BOILER_FG_IC4_CONCENTRATION_ARRAZI | 0.0386 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas iC5 | mol% | AR.AR5.DCS.Process.AI512111.PV | BOILER_FG_IC5_CONCENTRATION_ARRAZI | BOILER_FG_IC5_CONCENTRATION_ARRAZI | 0.0179 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas N2 | mol% | AR.AR5.DCS.Process.AI51219.PV | BOILER_FG_N2_CONCENTRATION_ARRAZI | BOILER_FG_N2_CONCENTRATION_ARRAZI | 6.933 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas nC4 | mol% | AR.AR5.DCS.Process.AI51214.PV | BOILER_FG_NC4_CONCENTRATION_ARRAZI | BOILER_FG_NC4_CONCENTRATION_ARRAZI | 0.0644 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Fuel Gas nC5 | mol% | AR.AR5.DCS.Process.AI512110.PV | BOILER_FG_NC5_CONCENTRATION_ARRAZI | BOILER_FG_NC5_CONCENTRATION_ARRAZI | 0.013 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerC-fuel fired boiler c | UB HP-2 Fuel Fired Boiler | Excess O2 | percent | UN.UO.71AC1304.PV | BOILER_C_FLUE_GAS_OXGYGEN | BOILER_C_FLUE_GAS_OXGYGEN | 3.4841 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler Air PreheaterA | UB HP-2 Fuel Fired Boiler Air Preheater | Air Inlet Temperature | degC | UN.UO.71TI1314B.PV | Boiler_C_Combustion_Air_Temperature | Boiler_C_Combustion_Air_Temperature | 28.2626 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Pressure | bar | UN.UO.71PI1021A.PV | BFW_Pressure | BFW_Pressure | 79.3 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Temperature | degC | UN.UO.71TI1079.PV | BFW_Temperature | BFW_Temperature | 109.9 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Inlet Flow | metric_ton/h | UN.UO.71FC1303.PV | BFW_TO_BOILER_C | BFW_TO_BOILER_C | 61405.8 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Quality (Conductivity) | uS/cm | UN.UO.71AI1005B.PV | BFW_Conductivity | BFW_Conductivity | 4.1147 | DIRECT
UB HP-2 Fuel Fired Boiler BFW SystemA > UB HP-2 Fuel Fired Boiler BFW PumpA | UB HP-2 Fuel Fired Boiler BFW Pump | Vibration | mm/s | UN.UO.71VI1872.PV | BFW_F_Vibration | BFW_F_Vibration | 0 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Blowdown Conductivity | uS/cm | UN.UO.71AC1301.PV | BOILER_C_CONDUCTIVITY | BOILER_C_CONDUCTIVITY | 50.005 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Continuous Blowdown Flow | metric_ton/h | UN.UO.71FC1300.PV | BOILER_C_CBD | BOILER_C_CBD | 901.0344 | DIRECT
UB HP-2 Fuel Fired Boiler Combustion SystemA > UB HP-2 Fuel Fired Boiler BurnerA | UB HP-2 Fuel Fired Boiler Burner | Burner Backpressure | bar | UN.UO.71PI1322A.PV |  |  |  | TAG_MISSING
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Inlet Steam Temperature | degC | UN.UO.71TI1306.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Outlet Steam Temperature | degC | UN.UO.71TC1311.PV | Boiler_C_DSP_outlet_Temp | Boiler_C_DSP_outlet_Temp | 398.7 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Spray Water Flow | metric_ton/h | UN.UO.71FI1302.PV | DSP_BFW_TO_BOILER_C | DSP_BFW_TO_BOILER_C | 1650.5 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Inlet Temperature | degC | UN.UO.71TI1310.PV | BFW_temp_A | BFW_temp_A | 109.8918 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Outlet Temperature | degC | UN.UO.71TI1302.PV | BLR_C_Eco_BFW_Out_Temp | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | O2 in Flue Gas | vol% | UN.UO.71AC1304.PV | BOILER_C_FLUE_GAS_OXGYGEN | BOILER_C_FLUE_GAS_OXGYGEN | 3.4841 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | Stack Temperature | degC | UN.UO.71TI1307.PV | BOILER_C_STACK_TEMPERATURE | BOILER_C_STACK_TEMPERATURE | 140.9907 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Level | percent | UN.UO.71LC1302A.PV |  | EG1_BFW_to_Steam_drum_1 | 0.0572 | SEMANTIC
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Pressure | bar | UN.UO.71PC1303.PV |  | Fuel_gas_drum_pressure | 4.2 | SEMANTIC
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Attemperator Spray Flow | metric_ton/h | UN.UO.71FI1301.PV | BLR_3_HPS_Gen_raw | BLR_3_HPS_Gen_raw | 61148.6641 | DIRECT
UB HP-2 Fuel Fired BoilerC-fuel fired boiler c > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Steam Inlet Temperature | degC | UN.UO.71TI1319.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Steam Output | metric_ton/h | UN.UO.71FI1401.PV | BLR_4_HPS_Gen_raw | BLR_4_HPS_Gen_raw | 62796.7891 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Steam Pressure | bar | UN.UO.71PC1113.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Steam Temperature | degC | UN.UO.71TC1111.PV | Boiler_A_DSP_outlet_Temp | Boiler_A_DSP_outlet_Temp | 398.2 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Flue Gas O2 | mol% | UN.UO.71AC1404.PV | BOILER_D_FLUE_GAS_OXGYGEN | BOILER_D_FLUE_GAS_OXGYGEN | 3.611 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas C1 | mol% | AR.AR5.DCS.Process.AI51211.PV | BOILER_FG_CH4_CONCENTRATION_ARRAZI | BOILER_FG_CH4_CONCENTRATION_ARRAZI | 90.9146 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas C2 | mol% | AR.AR5.DCS.Process.AI51212.PV | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | 1.4986 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas C3 | mol% | AR.AR5.DCS.Process.AI51213.PV | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | 0.2733 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas CO2 | mol% | AR.AR5.DCS.Process.AI51217.PV | BOILER_FG_CO2_CONCENTRATION_ARRAZI | BOILER_FG_CO2_CONCENTRATION_ARRAZI | 0.2467 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas Flow | metric_ton/h | UN.UO.71FC1404.PV | Boielr_D_Fuel_Gas_Flow | Boielr_D_Fuel_Gas_Flow | 4549.444 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas iC4 | mol% | AR.AR5.DCS.Process.AI51215.PV | BOILER_FG_IC4_CONCENTRATION_ARRAZI | BOILER_FG_IC4_CONCENTRATION_ARRAZI | 0.0386 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas iC5 | mol% | AR.AR5.DCS.Process.AI512111.PV | BOILER_FG_IC5_CONCENTRATION_ARRAZI | BOILER_FG_IC5_CONCENTRATION_ARRAZI | 0.0179 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas N2 | mol% | AR.AR5.DCS.Process.AI51219.PV | BOILER_FG_N2_CONCENTRATION_ARRAZI | BOILER_FG_N2_CONCENTRATION_ARRAZI | 6.933 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas nC4 | mol% | AR.AR5.DCS.Process.AI51214.PV | BOILER_FG_NC4_CONCENTRATION_ARRAZI | BOILER_FG_NC4_CONCENTRATION_ARRAZI | 0.0644 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Fuel Gas nC5 | mol% | AR.AR5.DCS.Process.AI512110.PV | BOILER_FG_NC5_CONCENTRATION_ARRAZI | BOILER_FG_NC5_CONCENTRATION_ARRAZI | 0.013 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerD-fuel fired boiler d | UB HP-2 Fuel Fired Boiler | Excess O2 | percent | UN.UO.71AC1404.PV | BOILER_D_FLUE_GAS_OXGYGEN | BOILER_D_FLUE_GAS_OXGYGEN | 3.611 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler Air PreheaterA | UB HP-2 Fuel Fired Boiler Air Preheater | Air Inlet Temperature | degC | UN.UO.71TI1414B.PV | Boiler_D_Combustion_Air_Temperature | Boiler_D_Combustion_Air_Temperature | 22.9298 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Pressure | bar | UN.UO.71PI1021A.PV | BFW_Pressure | BFW_Pressure | 79.3 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Temperature | degC | UN.UO.71TI1079.PV | BFW_Temperature | BFW_Temperature | 109.9 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Inlet Flow | metric_ton/h | UN.UO.71FC1403.PV | BFW_TO_BOILER_D | BFW_TO_BOILER_D | 63955.4 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Quality (Conductivity) | uS/cm | UN.UO.71AI1005B.PV | BFW_Conductivity | BFW_Conductivity | 4.1147 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Blowdown Conductivity | uS/cm | UN.UO.71AC1401.PV | BOILER_D_CONDUCTIVITY | BOILER_D_CONDUCTIVITY | 98.5394 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Continuous Blowdown Flow | metric_ton/h | UN.UO.71FC1400.PV | BOILER_D_CBD | BOILER_D_CBD | 899.8964 | DIRECT
UB HP-2 Fuel Fired Boiler Combustion SystemA > UB HP-2 Fuel Fired Boiler BurnerA | UB HP-2 Fuel Fired Boiler Burner | Burner Backpressure | bar | UN.UO.71PI1422A.PV |  |  |  | TAG_MISSING
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Inlet Steam Temperature | degC | UN.UO.71TI1406.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Outlet Steam Temperature | degC | UN.UO.71TC1411.PV | Boiler_D_DSP_outlet_Temp | Boiler_D_DSP_outlet_Temp | 392.4 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Spray Water Flow | metric_ton/h | UN.UO.71FI1402.PV | DSP_BFW_TO_BOILER_D | DSP_BFW_TO_BOILER_D | 954.2 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Inlet Temperature | degC | UN.UO.71TI1410.PV | BFW_temp_A | BFW_temp_A | 109.8918 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Outlet Temperature | degC | UN.UO.71TI1402.PV | BLR_D_Eco_BFW_Out_Temp | E_1402_level | 50.5 | SEMANTIC
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | O2 in Flue Gas | vol% | UN.UO.71AC1404.PV | BOILER_D_FLUE_GAS_OXGYGEN | BOILER_D_FLUE_GAS_OXGYGEN | 3.611 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | Stack Temperature | degC | UN.UO.71TI1407.PV | BOILER_D_STACK_TEMPERATURE | BOILER_D_STACK_TEMPERATURE | 136.6631 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Level | percent | UN.UO.71LC1402A.PV |  | E_1402_level | 50.5 | SEMANTIC
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Pressure | bar | UN.UO.71PC1403.PV |  | Fuel_gas_drum_pressure | 4.2 | SEMANTIC
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Attemperator Spray Flow | metric_ton/h | UN.UO.71FI1401.PV | BLR_4_HPS_Gen_raw | BLR_4_HPS_Gen_raw | 62796.7891 | DIRECT
UB HP-2 Fuel Fired BoilerD-fuel fired boiler d > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Steam Inlet Temperature | degC | UN.UO.71TI1419.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Steam Output | metric_ton/h | UN.UO.71FI1501.PV | BLR_5_HPS_Gen_raw | BLR_5_HPS_Gen_raw | 65744.0703 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Steam Pressure | bar | UN.UO.71PC1113.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Steam Temperature | degC | UN.UO.71TC1111.PV | Boiler_A_DSP_outlet_Temp | Boiler_A_DSP_outlet_Temp | 398.2 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Flue Gas O2 | mol% | UN.UO.71AC1504.PV | BOILER_E_FLUE_GAS_OXGYGEN | BOILER_E_FLUE_GAS_OXGYGEN | 2.0622 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas C1 | mol% | AR.AR5.DCS.Process.AI51211.PV | BOILER_FG_CH4_CONCENTRATION_ARRAZI | BOILER_FG_CH4_CONCENTRATION_ARRAZI | 90.9146 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas C2 | mol% | AR.AR5.DCS.Process.AI51212.PV | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | BOILER_FG_ETHANE_CONCENTRATION_ARRAZI | 1.4986 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas C3 | mol% | AR.AR5.DCS.Process.AI51213.PV | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | BOILER_FG_PROPANE_CONCENTRATION_ARRAZI | 0.2733 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas CO2 | mol% | AR.AR5.DCS.Process.AI51217.PV | BOILER_FG_CO2_CONCENTRATION_ARRAZI | BOILER_FG_CO2_CONCENTRATION_ARRAZI | 0.2467 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas Flow | metric_ton/h | UN.UO.71FC1504.PV | Boielr_E_Fuel_Gas_Flow | Boielr_E_Fuel_Gas_Flow | 6041.557 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas iC4 | mol% | AR.AR5.DCS.Process.AI51215.PV | BOILER_FG_IC4_CONCENTRATION_ARRAZI | BOILER_FG_IC4_CONCENTRATION_ARRAZI | 0.0386 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas iC5 | mol% | AR.AR5.DCS.Process.AI512111.PV | BOILER_FG_IC5_CONCENTRATION_ARRAZI | BOILER_FG_IC5_CONCENTRATION_ARRAZI | 0.0179 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas N2 | mol% | AR.AR5.DCS.Process.AI51219.PV | BOILER_FG_N2_CONCENTRATION_ARRAZI | BOILER_FG_N2_CONCENTRATION_ARRAZI | 6.933 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas nC4 | mol% | AR.AR5.DCS.Process.AI51214.PV | BOILER_FG_NC4_CONCENTRATION_ARRAZI | BOILER_FG_NC4_CONCENTRATION_ARRAZI | 0.0644 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Fuel Gas nC5 | mol% | AR.AR5.DCS.Process.AI512110.PV | BOILER_FG_NC5_CONCENTRATION_ARRAZI | BOILER_FG_NC5_CONCENTRATION_ARRAZI | 0.013 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Fuel Fired BoilerE-fuel fired boiler e | UB HP-2 Fuel Fired Boiler | Excess O2 | percent | UN.UO.71AC1504.PV | BOILER_E_FLUE_GAS_OXGYGEN | BOILER_E_FLUE_GAS_OXGYGEN | 2.0622 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler Air PreheaterA | UB HP-2 Fuel Fired Boiler Air Preheater | Air Inlet Temperature | degC | UN.UO.71TI1514B.PV | Boiler_E_Combustion_Air_Temp | Boiler_E_Combustion_Air_Temp | 45.8146 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Pressure | bar | UN.UO.71PI1021A.PV | BFW_Pressure | BFW_Pressure | 79.3 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Header Temperature | degC | UN.UO.71TI1079.PV | BFW_Temperature | BFW_Temperature | 109.9 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Inlet Flow | metric_ton/h | UN.UO.71FC1503.PV | BFW_TO_BOILER_E | BFW_TO_BOILER_E | 60906.1 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler BFW SystemA | UB HP-2 Fuel Fired Boiler BFW System | BFW Quality (Conductivity) | uS/cm | UN.UO.71AI1005B.PV | BFW_Conductivity | BFW_Conductivity | 4.1147 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Blowdown Conductivity | uS/cm | UN.UO.71AC1501.PV | BOILER_E_CONDUCTIVITY | BOILER_E_CONDUCTIVITY | 65.2588 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler Blowdown SystemA | UB HP-2 Fuel Fired Boiler Blowdown System | Continuous Blowdown Flow | metric_ton/h | UN.UO.71FC1500.PV | BOILER_E_CBD | BOILER_E_CBD | 988.0331 | DIRECT
UB HP-2 Fuel Fired Boiler Combustion SystemA > UB HP-2 Fuel Fired Boiler BurnerA | UB HP-2 Fuel Fired Boiler Burner | Burner Backpressure | bar | UN.UO.71PI1522A.PV |  |  |  | TAG_MISSING
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Inlet Steam Temperature | degC | UN.UO.71TI1506.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Outlet Steam Temperature | degC | UN.UO.71TC1511.PV | Boiler_E_DSP_outlet_Temp | Boiler_E_DSP_outlet_Temp | 397.7 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler DesuperheaterA | UB HP-2 Fuel Fired Boiler Desuperheater | Spray Water Flow | metric_ton/h | UN.UO.71FI1502.PV | DSP_BFW_TO_BOILER_E | DSP_BFW_TO_BOILER_E | 3587.2 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Inlet Temperature | degC | UN.UO.71TI1510.PV | BFW_temp_A | BFW_temp_A | 109.8918 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler EconomizerA | UB HP-2 Fuel Fired Boiler Economizer | BFW Outlet Temperature | degC | UN.UO.71TI1502.PV | BLR_E_Eco_BFW_Out_Temp | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | O2 in Flue Gas | vol% | UN.UO.71AC1504.PV | BOILER_E_FLUE_GAS_OXGYGEN | BOILER_E_FLUE_GAS_OXGYGEN | 2.0622 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler StackA | UB HP-2 Fuel Fired Boiler Stack | Stack Temperature | degC | UN.UO.71TI1507.PV | BOILER_E_STACK_TEMPERATURE | BOILER_E_STACK_TEMPERATURE | 154.7974 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Level | percent | UN.UO.71LC1502A.PV |  | EG1_BFW_to_Steam_drum_1 | 0.0572 | SEMANTIC
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler Steam DrumA | UB HP-2 Fuel Fired Boiler Steam Drum | Drum Pressure | bar | UN.UO.71PC1503.PV |  | Fuel_gas_drum_pressure | 4.2 | SEMANTIC
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Attemperator Spray Flow | metric_ton/h | UN.UO.71FI1501.PV | BLR_5_HPS_Gen_raw | BLR_5_HPS_Gen_raw | 65744.0703 | DIRECT
UB HP-2 Fuel Fired BoilerE-fuel fired boiler e > UB HP-2 Fuel Fired Boiler SuperheaterA | UB HP-2 Fuel Fired Boiler Superheater | Steam Inlet Temperature | degC | UN.UO.71TI1519.PV |  | Boiler_A_Main_Fuel_Gas_Temperature | 24.6415 | SEMANTIC
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerA-waste heat boiler a | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031A.PV | Furnace_A_steam_outlet_flow | Furnace_A_steam_outlet_flow | -4.4115 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerA-waste heat boiler a | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688A.PV | Furnace_A_steam_outlet_pressure | Furnace_A_steam_outlet_pressure | 2.4 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerA-waste heat boiler a | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017A.PV | Furnace_A_steam_outlet_temp | Furnace_A_steam_outlet_temp | 46 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerB-waste heat boiler b | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031B.PV | Furnace_B_steam_outlet_flow | Furnace_B_steam_outlet_flow | 56.054 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerB-waste heat boiler b | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688B.PV | Furnace_B_steam_outlet_pressure | Furnace_B_steam_outlet_pressure | 104.3 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerB-waste heat boiler b | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017B.PV | Furnace_B_steam_outlet_temp | Furnace_B_steam_outlet_temp | 500.3 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerC-waste heat boiler c | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031C.PV | Furnace_C_steam_outlet_flow | Furnace_C_steam_outlet_flow | 60.404 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerC-waste heat boiler c | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688C.PV | Furnace_C_steam_outlet_pressure | Furnace_C_steam_outlet_pressure | 104.2 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerC-waste heat boiler c | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017D.PV | Furnace_D_steam_outlet_temp | Furnace_D_steam_outlet_temp | 500 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerD-waste heat boiler d | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031D.PV | Furnace_D_steam_outlet_flow | Furnace_D_steam_outlet_flow | 59.1488 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerD-waste heat boiler d | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688D.PV | Furnace_D_steam_outlet_pressure | Furnace_D_steam_outlet_pressure | 104.1 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerD-waste heat boiler d | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017D.PV | Furnace_D_steam_outlet_temp | Furnace_D_steam_outlet_temp | 500 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerE-waste heat boiler e | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031E.PV | Furnace_E_steam_outlet_flow | Furnace_E_steam_outlet_flow | 57.8751 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerE-waste heat boiler e | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688E.PV | Furnace_E_steam_outlet_pressure | Furnace_E_steam_outlet_pressure | 104.3 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerE-waste heat boiler e | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017E.PV | Furnace_E_steam_outlet_temp | Furnace_E_steam_outlet_temp | 500 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerF-waste heat boiler f | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031F.PV | Furnace_F_steam_outlet_flow | Furnace_F_steam_outlet_flow | 50.1101 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerF-waste heat boiler f | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688F.PV | Furnace_F_steam_outlet_pressure | Furnace_F_steam_outlet_pressure | 104.3 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerF-waste heat boiler f | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017F.PV | Furnace_F_steam_outlet_temp | Furnace_F_steam_outlet_temp | 500 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerG-waste heat boiler g | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031G.PV | Furnace_G_steam_outlet_flow | Furnace_G_steam_outlet_flow | 57.5746 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerG-waste heat boiler g | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688G.PV | Furnace_G_steam_outlet_pressure | Furnace_G_steam_outlet_pressure | 104.4 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerG-waste heat boiler g | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017G.PV | Furnace_G_steam_outlet_temp | Furnace_G_steam_outlet_temp | 500 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerH-waste heat boiler h | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031H.PV | Furnace_H_steam_outlet_flow | Furnace_H_steam_outlet_flow | 59.5274 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerH-waste heat boiler h | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688H.PV | Furnace_H_steam_outlet_pressure | Furnace_H_steam_outlet_pressure | 104.1 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerH-waste heat boiler h | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017H.PV | Furnace_H_steam_outlet_temp | Furnace_H_steam_outlet_temp | 500 | DIRECT
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerI-waste heat boiler i | UB VHP Waste Heat Boiler | Steam Output | metric_ton/h | UN.ETH.11FI1031I.PV | WHB_VHP_Steam_raw |  |  | COL_MISSING
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerI-waste heat boiler i | UB VHP Waste Heat Boiler | Steam Pressure | bar | UN.ETH.11PI1688I.PV |  | VHP_Steam_Pressure | 103.9342 | SEMANTIC
Steam Generators & TurbinesA > UB VHP Waste Heat BoilerI-waste heat boiler i | UB VHP Waste Heat Boiler | Steam Temperature | degC | UN.ETH.11TC1017I.PV |  | VHP_Steam_Temperature | 499.2784 | SEMANTIC
Steam ConsumersA > UB HP-2 Steam ExportA-steam export a | UB HP-2 Steam Export | Export Flow | metric_ton/h | UN.EG1.29FI9201.PV | EOEG_1_HPS_Demand_raw | EOEG_1_HPS_Demand_raw | 4.4127 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportA-steam export a | UB HP-2 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportA-steam export a | UB HP-2 Steam Export | Export Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportB-steam export b | UB HP-2 Steam Export | Export Flow | metric_ton/h | UN.EG2.49FI9201.PV | EOEG_2_HPS_Demand_raw | EOEG_2_HPS_Demand_raw | 0 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportB-steam export b | UB HP-2 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportB-steam export b | UB HP-2 Steam Export | Export Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportC-steam export c | UB HP-2 Steam Export | Export Flow | metric_ton/h | UN.EG3.69FI9201.PV | EOEG_3_HPS_Demand_raw | EOEG_3_HPS_Demand_raw | -0.0084 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportC-steam export c | UB HP-2 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportC-steam export c | UB HP-2 Steam Export | Export Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportD-steam export d | UB HP-2 Steam Export | Export Flow | metric_ton/h | UN.ETH.17FC7064.PV | ETH_HPS_Demand_old | ETH_HPS_Demand_old | 0 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportD-steam export d | UB HP-2 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam ConsumersA > UB HP-2 Steam ExportD-steam export d | UB HP-2 Steam Export | Export Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportE-steam export a | UB MP-2 Steam Export | Export Flow | metric_ton/h | UN.EG1.29FI9202.PV | EOEG_1_MPS_Demand_raw | EOEG_1_MPS_Demand_raw | 19.6369 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportE-steam export a | UB MP-2 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportE-steam export a | UB MP-2 Steam Export | Export Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportF-steam export b | UB MP-2 Steam Export | Export Flow | metric_ton/h | UN.EG2.49FI9202.PV | EOEG_2_MPS_Demand_raw | EOEG_2_MPS_Demand_raw | 0 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportF-steam export b | UB MP-2 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportF-steam export b | UB MP-2 Steam Export | Export Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportG-steam export c | UB MP-2 Steam Export | Export Flow | metric_ton/h | UN.EG3.69FI9208.PV | EOEG_3_MPS_Demand_raw | EOEG_3_MPS_Demand_raw | 65.0297 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportG-steam export c | UB MP-2 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam ConsumersA > UB MP-2 Steam ExportG-steam export c | UB MP-2 Steam Export | Export Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportH-steam export a | UB LP-1 Steam Export | Export Flow | metric_ton/h | UN.EG1.29FI9203.PV | EOEG_1_LPS_Demand_raw | EOEG_1_LPS_Demand_raw | -0.0272 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportH-steam export a | UB LP-1 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportH-steam export a | UB LP-1 Steam Export | Export Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportI-steam export b | UB LP-1 Steam Export | Export Flow | metric_ton/h | UN.EG2.49FI9203.PV | EOEG_2_LPS_Demand_raw | EOEG_2_LPS_Demand_raw | 0.8332 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportI-steam export b | UB LP-1 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportI-steam export b | UB LP-1 Steam Export | Export Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportJ-steam export c | UB LP-1 Steam Export | Export Flow | metric_ton/h | UN.EG3.69FI9209.PV | EOEG_3_LPS_Demand_raw | EOEG_3_LPS_Demand_raw | 37.092 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportJ-steam export c | UB LP-1 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportJ-steam export c | UB LP-1 Steam Export | Export Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportK-steam export d | UB LP-1 Steam Export | Export Flow | metric_ton/h | UN.UO.17FI7065 | ETH_LPS_Demand_raw | ETH_LPS_Demand_raw | 68.9853 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportK-steam export d | UB LP-1 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportK-steam export d | UB LP-1 Steam Export | Export Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportL-steam export e | UB LP-1 Steam Export | Export Flow | metric_ton/h | UN.LAO.39FI9004.PV | LAO_LP_Steam_Demand_raw | LAO_LP_Steam_Demand_raw | 930.5038 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportL-steam export e | UB LP-1 Steam Export | Export Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam ConsumersA > UB LP-1 Steam ExportL-steam export e | UB LP-1 Steam Export | Export Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam ConsumersA > UB VHP Steam VentA-steam vent a | UB VHP Steam Vent | Vent Valve Opening | percent | UN.ETH.17PC7032.MV | HP_Steam_Vent_Valve_PC7032_Opening_ETH | HP_Steam_Vent_Valve_PC7032_Opening_ETH | 0 | DIRECT
Steam ConsumersA > UB VHP Steam VentA-steam vent a | UB VHP Steam Vent | Vent Pressure | KG/CM2A | UN.ETH.17PC7032.PV | VHP_Steam_Pressure | VHP_Steam_Pressure | 103.9342 | DIRECT
Steam ConsumersA > UB HP-2 Steam VentB-steam vent a | UB HP-2 Steam Vent | Vent Valve Opening | metric_ton/h | UN.UO.70PC0012A.MV | HP_Steam_Vent_valve_PV0012_Opening_UO | HP_Steam_Vent_valve_PV0012_Opening_UO | 0 | DIRECT
Steam ConsumersA > UB HP-2 Steam VentB-steam vent a | UB HP-2 Steam Vent | Vent Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam ConsumersA > UB LP-1 Steam VentC-steam vent a | UB LP-1 Steam Vent | Vent Valve Opening | metric_ton/h | UN.UO.70PC0024B.MV | LP_Steam_Vent_valve_PV0024B_Opening_UO | LP_Steam_Vent_valve_PV0024B_Opening_UO | 2.1434 | DIRECT
Steam ConsumersA > UB LP-1 Steam VentC-steam vent a | UB LP-1 Steam Vent | Vent Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam ConsumersA > UB LP-1 DeaeratorA-deaerator a | UB LP-1 Deaerator | LP Steam Flow | metric_ton/h | UN.UO.71FI1002.PV | Deaerator_A_LPS_raw | Deaerator_A_LPS_raw | 39457.05 | DIRECT
Steam ConsumersA > UB LP-1 DeaeratorB-deaerator b | UB LP-1 Deaerator | LP Steam Flow | metric_ton/h | UN.UO.71FI1004.PV | Deaerator_B_LPS_raw | Deaerator_B_LPS_raw | 45145.76 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineA-bfw turbine a | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1812.PV | BFW_B_Turb_Steam_raw | BFW_B_Turb_Steam_raw | 12603.1582 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineA-bfw turbine a | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineA-bfw turbine a | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineA-bfw turbine a | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineA-bfw turbine a | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineA-bfw turbine a | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1812.PV | BFW_B_Turb_Steam_raw | BFW_B_Turb_Steam_raw | 12603.1582 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineB-bfw turbine b | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1813.PV | BFW_C_Turb_Steam_raw | BFW_C_Turb_Steam_raw | 16227.8135 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineB-bfw turbine b | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineB-bfw turbine b | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineB-bfw turbine b | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineB-bfw turbine b | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineB-bfw turbine b | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1813.PV | BFW_C_Turb_Steam_raw | BFW_C_Turb_Steam_raw | 16227.8135 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineC-bfw turbine c | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1604.PV | BFW_E_Turb_Steam_raw | BFW_E_Turb_Steam_raw | 13629.6621 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineC-bfw turbine c | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineC-bfw turbine c | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineC-bfw turbine c | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineC-bfw turbine c | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineC-bfw turbine c | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1604.PV | BFW_E_Turb_Steam_raw | BFW_E_Turb_Steam_raw | 13629.6621 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineD-fd turbine a | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1814.PV | VHP_BFW_B_Turb_Steam_raw | VHP_BFW_B_Turb_Steam_raw | 31960.7324 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineD-fd turbine a | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineD-fd turbine a | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineD-fd turbine a | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineD-fd turbine a | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineD-fd turbine a | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1814.PV | VHP_BFW_B_Turb_Steam_raw | VHP_BFW_B_Turb_Steam_raw | 31960.7324 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineE-fd turbine b | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1815.PV | VHP_BFW_C_Turb_Steam_raw | VHP_BFW_C_Turb_Steam_raw | 30662.7383 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineE-fd turbine b | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineE-fd turbine b | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineE-fd turbine b | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineE-fd turbine b | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineE-fd turbine b | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1815.PV | VHP_BFW_C_Turb_Steam_raw | VHP_BFW_C_Turb_Steam_raw | 30662.7383 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineF-fd turbine c | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.72FI2007.PV | Air_Compressor_Turbine_A_Steam_raw | Air_Compressor_Turbine_A_Steam_raw | 21.9727 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineF-fd turbine c | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineF-fd turbine c | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineF-fd turbine c | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineF-fd turbine c | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineF-fd turbine c | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.72FI2007.PV | Air_Compressor_Turbine_A_Steam_raw | Air_Compressor_Turbine_A_Steam_raw | 21.9727 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineG-fd turbine d | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.72FI2008.PV | Air_Compressor_Turbine_D_Steam_raw | Air_Compressor_Turbine_D_Steam_raw | 25690.4551 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineG-fd turbine d | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineG-fd turbine d | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineG-fd turbine d | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineG-fd turbine d | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineG-fd turbine d | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.72FI2008.PV | Air_Compressor_Turbine_D_Steam_raw | Air_Compressor_Turbine_D_Steam_raw | 25690.4551 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineH-fd turbine e | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1108.PV | FD_Fan_BLR_1_Steam_raw | FD_Fan_BLR_1_Steam_raw | 4037.3484 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineH-fd turbine e | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineH-fd turbine e | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineH-fd turbine e | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineH-fd turbine e | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineH-fd turbine e | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1108.PV | FD_Fan_BLR_1_Steam_raw | FD_Fan_BLR_1_Steam_raw | 4037.3484 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineI-air compressor turbine a | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineI-air compressor turbine a | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineI-air compressor turbine a | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.71FI1208.PV | FD_Fan_BLR_2_Steam_raw | FD_Fan_BLR_2_Steam_raw | 4077.0686 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineI-air compressor turbine a | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineI-air compressor turbine a | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineI-air compressor turbine a | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1208.PV | FD_Fan_BLR_2_Steam_raw | FD_Fan_BLR_2_Steam_raw | 4077.0686 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineJ-air compressor turbine b | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1308.PV | FD_Fan_BLR_3_Steam_raw | FD_Fan_BLR_3_Steam_raw | 4280.561 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineJ-air compressor turbine b | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineJ-air compressor turbine b | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineJ-air compressor turbine b | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineJ-air compressor turbine b | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineJ-air compressor turbine b | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1308.PV | FD_Fan_BLR_3_Steam_raw | FD_Fan_BLR_3_Steam_raw | 4280.561 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineK-cw turbine a | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1408.PV | FD_Fan_BLR_4_Steam_raw | FD_Fan_BLR_4_Steam_raw | 4454.9297 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineK-cw turbine a | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineK-cw turbine a | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineK-cw turbine a | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineK-cw turbine a | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineK-cw turbine a | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1408.PV | FD_Fan_BLR_4_Steam_raw | FD_Fan_BLR_4_Steam_raw | 4454.9297 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineL-cw turbine b | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.71FI1508.PV | FD_Fan_BLR_5_Steam_raw | FD_Fan_BLR_5_Steam_raw | 5814.8696 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineL-cw turbine b | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineL-cw turbine b | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineL-cw turbine b | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineL-cw turbine b | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineL-cw turbine b | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.71FI1508.PV | FD_Fan_BLR_5_Steam_raw | FD_Fan_BLR_5_Steam_raw | 5814.8696 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-cw turbine c | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.78FI8085.PV | CW_Turbine_A_Steam | CW_Turbine_A_Steam | 33.6697 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-cw turbine c | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-cw turbine c | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-cw turbine c | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-cw turbine c | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-cw turbine c | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.78FI8085.PV | CW_Turbine_A_Steam | CW_Turbine_A_Steam | 33.6697 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw a | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.78FI8086.PV | CW_Turbine_B_Steam | CW_Turbine_B_Steam | 5.2893 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw a | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw a | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw a | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw a | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw a | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.78FI8086.PV | CW_Turbine_B_Steam | CW_Turbine_B_Steam | 5.2893 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw b | UB HP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.78FI8623.PV | CW_Turbine_G_Steam | CW_Turbine_G_Steam | 36.0046 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw b | UB HP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw b | UB HP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw b | UB HP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw b | UB HP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB HP-2 Backpressure TurbineM-vhp bfw b | UB HP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.78FI8623.PV | CW_Turbine_G_Steam | CW_Turbine_G_Steam | 36.0046 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineN-dmw a | UB MP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.73FI3025.PV | DMW_Turbine_A_Steam_raw | DMW_Turbine_A_Steam_raw | 6265.1685 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineN-dmw a | UB MP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineN-dmw a | UB MP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineN-dmw a | UB MP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineN-dmw a | UB MP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineN-dmw a | UB MP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.73FI3025.PV | DMW_Turbine_A_Steam_raw | DMW_Turbine_A_Steam_raw | 6265.1685 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineO-dmw b | UB MP-2 Backpressure Turbine | Inlet Steam Flow | metric_ton/h | UN.UO.73FI3026.PV | DMW_Turbine_C_Steam_raw | DMW_Turbine_C_Steam_raw | 6.5032 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineO-dmw b | UB MP-2 Backpressure Turbine | Inlet Pressure | bar | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineO-dmw b | UB MP-2 Backpressure Turbine | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineO-dmw b | UB MP-2 Backpressure Turbine | Exhaust Pressure | bar | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineO-dmw b | UB MP-2 Backpressure Turbine | Exhaust Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Generators & TurbinesA > UB MP-2 Backpressure TurbineO-dmw b | UB MP-2 Backpressure Turbine | Exhaust Flow | metric_ton/h | UN.UO.73FI3026.PV | DMW_Turbine_C_Steam_raw | DMW_Turbine_C_Steam_raw | 6.5032 | DIRECT
Steam Generators & TurbinesA > UB VHP Extraction-Condensing TurbineA-cgc a | UB VHP Extraction-Condensing Turbine | Inlet Steam Flow | metric_ton/h | UN.ETH.12FI2157.PV | CGC_turbine_Inlet_steam_flow | CGC_turbine_Inlet_steam_flow | 491.1052 | DIRECT
Steam Generators & TurbinesA > UB VHP Extraction-Condensing TurbineA-cgc a | UB VHP Extraction-Condensing Turbine | Inlet Pressure | bar | UN.ETH.12PI2125.PV | CGC_turbine_Inlet_steam_pressure | CGC_turbine_Inlet_steam_pressure | 103.3 | DIRECT
Steam Generators & TurbinesA > UB VHP Extraction-Condensing TurbineA-cgc a | UB VHP Extraction-Condensing Turbine | Inlet Temperature | degC | UN.ETH.12TI2107.PV | VHP_Steam_Temperature | VHP_Steam_Temperature | 499.2784 | DIRECT
Steam Generators & TurbinesA > UB VHP Extraction-Condensing TurbineA-cgc a | UB VHP Extraction-Condensing Turbine | Extraction Pressure | bar | UN.ETH.12PI2130.PV | CGC_turbine_extraction_steam_pressure | CGC_turbine_extraction_steam_pressure | 45.3 | DIRECT
Steam Generators & TurbinesA > UB VHP Extraction-Condensing TurbineA-cgc a | UB VHP Extraction-Condensing Turbine | Extraction Flow | metric_ton/h | UN.ETH.12FI2158.PV | HP_Steam_from_CGC_Extraction | HP_Steam_from_CGC_Extraction | 292.7732 | DIRECT
Steam Generators & TurbinesA > UB VHP Extraction-Condensing TurbineA-cgc a | UB VHP Extraction-Condensing Turbine | Condenser Pressure | mbar | 1 |  | CGC_turbine_extraction_steam_pressure | 45.3 | SEMANTIC
Steam ConsumersA > UB LP-1 Steam ExchangerA-steam exchanger a | UB LP-1 Steam Exchanger | Steam Flow Control valve opening | metric_ton/h | UN.UO.70PC0024A.MV | LP_Steam_Dumping_Valve_PC0024A_Opening_UO | LP_Steam_Dumping_Valve_PC0024A_Opening_UO | 42.5806 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)A-letdown station (prds) a | UB VHP Letdown Station (PRDS) | Inlet Pressure | KG/CM2A | UN.ETH.17PC7032.PV | VHP_Steam_Pressure | VHP_Steam_Pressure | 103.9342 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)A-letdown station (prds) a | UB VHP Letdown Station (PRDS) | Outlet Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)A-letdown station (prds) a | UB VHP Letdown Station (PRDS) | Inlet Temperature | degC | UN.ETH.12TI2107.PV | VHP_Steam_Temperature | VHP_Steam_Temperature | 499.2784 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)A-letdown station (prds) a | UB VHP Letdown Station (PRDS) | Outlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)A-letdown station (prds) a | UB VHP Letdown Station (PRDS) | Pressure Valve Opening | percent | UN.ETH.17TC7006.PV | ETH_VHP_HP_Desuperheater1_outlet_temp | ETH_VHP_HP_Desuperheater1_outlet_temp | 262.1 | DIRECT
| UB VHP Letdown Station (PRDS) | Temperature Valve Opening | percent | UN.ETH.17TC7006.MV | ETH_VHP_HP_Desuperheater1_water_opening | ETH_VHP_HP_Desuperheater1_water_opening | 2 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)B-letdown station (prds) b | UB VHP Letdown Station (PRDS) | Inlet Pressure | KG/CM2A | UN.ETH.17PC7032.PV | VHP_Steam_Pressure | VHP_Steam_Pressure | 103.9342 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)B-letdown station (prds) b | UB VHP Letdown Station (PRDS) | Outlet Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)B-letdown station (prds) b | UB VHP Letdown Station (PRDS) | Inlet Temperature | degC | UN.ETH.12TI2107.PV | VHP_Steam_Temperature | VHP_Steam_Temperature | 499.2784 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)B-letdown station (prds) b | UB VHP Letdown Station (PRDS) | Outlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
| UB VHP Letdown Station (PRDS) | Pressure Valve Opening | percent | UN.ETH.17PC7024.MV | ETH_VHP_HP_Desuperheater2_opening | ETH_VHP_HP_Desuperheater2_opening | 7.2 | DIRECT
Steam Distribution (Headers/PRDS)A > UB VHP Letdown Station (PRDS)B-letdown station (prds) b | UB VHP Letdown Station (PRDS) | Temperature Valve Opening | percent | UN.ETH.17TC7012.MV | ETH_VHP_HP_Desuperheater2_water_opening | ETH_VHP_HP_Desuperheater2_water_opening | 2.6 | DIRECT
Steam Distribution (Headers/PRDS)A > UB HP-2 Letdown Station (PRDS)C-letdown station (prds) a | UB HP-2 Letdown Station (PRDS) | Inlet Pressure | KG/CM2A | UN.UO.70PI0012A.PV | HP_Steam_Pressure | HP_Steam_Pressure | 44.7938 | DIRECT
Steam Distribution (Headers/PRDS)A > UB HP-2 Letdown Station (PRDS)C-letdown station (prds) a | UB HP-2 Letdown Station (PRDS) | Outlet Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam Distribution (Headers/PRDS)A > UB HP-2 Letdown Station (PRDS)C-letdown station (prds) a | UB HP-2 Letdown Station (PRDS) | Inlet Temperature | degC | UN.UO.70TI0007.PV | HP_Steam_Temperature | HP_Steam_Temperature | 395.6656 | DIRECT
Steam Distribution (Headers/PRDS)A > UB HP-2 Letdown Station (PRDS)C-letdown station (prds) a | UB HP-2 Letdown Station (PRDS) | Outlet Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam Distribution (Headers/PRDS)A > UB HP-2 Letdown Station (PRDS)C-letdown station (prds) a | UB HP-2 Letdown Station (PRDS) | Valve Opening | percent | UN.UO.70PC0007A.MV | UO_HP_MP_Desuperheater1_opening | UO_HP_MP_Desuperheater1_opening | 46.6267 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)D-letdown station (prds) a | UB MP-2 Letdown Station (PRDS) | Inlet Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)D-letdown station (prds) a | UB MP-2 Letdown Station (PRDS) | Outlet Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)D-letdown station (prds) a | UB MP-2 Letdown Station (PRDS) | Inlet Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)D-letdown station (prds) a | UB MP-2 Letdown Station (PRDS) | Outlet Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)D-letdown station (prds) a | UB MP-2 Letdown Station (PRDS) | Valve Opening | percent | UN.UO.70PC0013A.MV | MP_to_LP_Letdown_Valve_Opening_PV013A_UO | MP_to_LP_Letdown_Valve_Opening_PV013A_UO | 0 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)E-letdown station (prds) b | UB MP-2 Letdown Station (PRDS) | Inlet Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)E-letdown station (prds) b | UB MP-2 Letdown Station (PRDS) | Outlet Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)E-letdown station (prds) b | UB MP-2 Letdown Station (PRDS) | Inlet Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)E-letdown station (prds) b | UB MP-2 Letdown Station (PRDS) | Outlet Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)E-letdown station (prds) b | UB MP-2 Letdown Station (PRDS) | Valve Opening | percent | UN.UO.70PC0013B.MV | MP_to_LP_Letdown_Valve_Opening_PV013B_UO | MP_to_LP_Letdown_Valve_Opening_PV013B_UO | 0 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)F-letdown station (prds) c | UB MP-2 Letdown Station (PRDS) | Inlet Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)F-letdown station (prds) c | UB MP-2 Letdown Station (PRDS) | Outlet Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)F-letdown station (prds) c | UB MP-2 Letdown Station (PRDS) | Inlet Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)F-letdown station (prds) c | UB MP-2 Letdown Station (PRDS) | Outlet Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)F-letdown station (prds) c | UB MP-2 Letdown Station (PRDS) | Valve Opening | percent | UN.UO.70PY0031.MV | MP_to_LP_Letdown_Valve_Opening_PV31_UO | MP_to_LP_Letdown_Valve_Opening_PV31_UO | 0 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)G-letdown station (prds) d | UB MP-2 Letdown Station (PRDS) | Inlet Pressure | KG/CM2A | UN.UO.70PC0007A.PV | MP_Steam_Pressure | MP_Steam_Pressure | 21.0088 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)G-letdown station (prds) d | UB MP-2 Letdown Station (PRDS) | Outlet Pressure | KG/CM2A | UN.UO.70PI0024A.PV | LP_Steam_Pressure | LP_Steam_Pressure | 5.1001 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)G-letdown station (prds) d | UB MP-2 Letdown Station (PRDS) | Inlet Temperature | degC | UN.UO.70TC0005.PV | MP_Steam_Temperature | MP_Steam_Temperature | 277.1837 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)G-letdown station (prds) d | UB MP-2 Letdown Station (PRDS) | Outlet Temperature | degC | UN.UO.70TI0006.PV | LP_Steam_Temperature | LP_Steam_Temperature | 229.8323 | DIRECT
Steam Distribution (Headers/PRDS)A > UB MP-2 Letdown Station (PRDS)G-letdown station (prds) d | UB MP-2 Letdown Station (PRDS) | Valve Opening | percent | UN.UO.70PY0032.MV | MP_to_LP_Letdown_Valve_Opening_PV32_UO | MP_to_LP_Letdown_Valve_Opening_PV32_UO | 0 | DIRECT
SUMMARY | Match Type | Count
| DIRECT | 371
| SEMANTIC | 29
| TAG_MISSING | 5
| COL_MISSING | 1
| NO_VALUE | 0
| TOTAL | 406